## Inverter-Full Data
Utility Interactive Inverter List (Full Data)
Data has not changed since July 15, 2019
Inverter List Notes
Archive of the "Prior List of Eligible Inverters" Expired March 31, 2005. (Adobe PDF, 6 pages, 120 kilobytes).
* Equipment is in the process of being removed from the list of eligible equipment pursuant to Appendix A, Section B, of the Guidelines for California's Solar Electric Incentive Programs (Senate Bill 1) at:
Guidelines for California's Solar Electric Incentive Programs (Senate Bill 1)
Starting January 1, 2020, the Energy Commission will stop accepting requests to list inverters that do not incorporate advanced functions.
(1) Any text in brackets at the end of the Model Number is not part of the Manufacturer's Model Number. Part of the text in brackets indicates the specified voltage option for that model number, if provided; models with multiple voltage options will have multiple row entries, with one for each eligible option.
Blue colored text indicates that the model number occurs multiple times on the list under different manufacturer names.
Manufacturer Name | Model Number1 | Description | Maximum Continuous Output Power at Unity Power Factor | Nominal Voltage | Weighted Efficiency | Built-In Meter | Microinverter | Notes | Night Tare Loss | Power Rating, Continuous, 40 deg C | Night Tare Loss, 40 deg C | Voltage Minimum | Voltage Nominal | Voltage Maximum | Power Level | Power Level | Power Level | Power Level | Power Level | Power Level | Efficiency @Vmin, | Efficiency @Vmin, | Efficiency @Vmin, | Efficiency @Vmin, | Efficiency @Vmin, | Efficiency @Vmin, | Efficiency @Vmin, | Efficiency @Vnom | Efficiency @Vnom | Efficiency @Vnom | Efficiency @Vnom | Efficiency @Vnom | Efficiency @Vnom | Efficiency @Vnom | Efficiency @Vmax | Efficiency @Vmax | Efficiency @Vmax | Efficiency @Vmax | Efficiency @Vmax | Efficiency @Vmax | Efficiency @Vmax | CEC Listing Date | Last Update
|  |  | (kW) | (Vac) | (%) |  |  |  | (W) | (kW) | (W) | (Vdc) | (Vdc) | (Vdc) | 10% (kW) | 20% (kW) | 30% (kW) | 50% (kW) | 75% (kW) | 100% (kW) | 10% Pwr Lvl (%) | 20% Pwr Lvl (%) | 30% Pwr Lvl (%) | 50% Pwr Lvl (%) | 75% Pwr Lvl (%) | 100% Pwr Lvl (%) | Wtd (%) | 10% Pwr Lvl (%) | 20% Pwr Lvl (%) | 30% Pwr Lvl (%) | 50% Pwr Lvl (%) | 75% Pwr Lvl (%) | 100% Pwr Lvl (%) | Wtd (%) | 10% Pwr Lvl (%) | 20% Pwr Lvl (%) | 30% Pwr Lvl (%) | 50% Pwr Lvl (%) | 75% Pwr Lvl (%) | 100% Pwr Lvl (%) | Wtd (%)
ABB | MICRO-0.25-I-OUTD-US-208 [208V] | 250 W Utility Interactive Microinverter | 0.25 | 208 | 96 | N | Y | Multiple Listing of Power-One | 0.02 |  |  | 30 | 40 | 50 | 0.03 | 0.05 | 0.08 | 0.13 | 0.19 | 0.25 | 91.2 | 94.5 | 95.4 | 96 | 96.2 | 96.2 | 95.8 | 91.5 | 94.4 | 95.5 | 96.2 | 96.3 | 96.4 | 95.9 | 91.2 | 94.3 | 95.3 | 96.2 | 96.2 | 96.4 | 95.8
ABB | MICRO-0.25-I-OUTD-US-240 [240V] | 250 W Utility Interactive Microinverter | 0.25 | 240 | 96 | N | Y | Multiple Listing of Power-One | 0.05 |  |  | 30 | 40 | 50 | 0.03 | 0.05 | 0.08 | 0.13 | 0.19 | 0.25 | 90.8 | 94.2 | 95.4 | 96 | 96.1 | 96.2 | 95.7 | 91.2 | 94.2 | 95.3 | 96.3 | 96.2 | 96.5 | 95.8 | 90.5 | 94 | 95.3 | 96.3 | 96.1 | 96.5 | 95.8
ABB | MICRO-0.3HV-I-OUTD-US-208 [208V] | 300 W Utility Interactive Microinverter | 0.3 | 208 | 96 | N | Y | Multiple Listing of Power-One | 0.06 |  |  | 30 | 45 | 60 | 0.03 | 0.06 | 0.09 | 0.15 | 0.225 | 0.3 | 92.8 | 95.2 | 95.8 | 96.1 | 96 | 95.6 | 95.8 | 92.3 | 95 | 95.8 | 96.2 | 96.3 | 96.3 | 96 | 91.9 | 94.9 | 95.7 | 96.2 | 96.2 | 96.2 | 95.9
ABB | MICRO-0.3HV-I-OUTD-US-240 [240V] | 300 W Utility Interactive Microinverter | 0.3 | 240 | 96 | N | Y | Multiple Listing of Power-One | 0.06 |  |  | 30 | 45 | 60 | 0.03 | 0.06 | 0.09 | 0.15 | 0.225 | 0.3 | 92.4 | 95 | 95.7 | 96 | 96 | 95.7 | 95.8 | 91.8 | 94.7 | 95.8 | 96.2 | 96.4 | 96.4 | 96 | 91.7 | 94.6 | 95.6 | 96.1 | 96.2 | 96.4 | 95.8
ABB | MICRO-0.3-I-OUTD-US-208 [208V] | 300 W Utility Interactive Microinverter | 0.3 | 208 | 96 | N | Y | Multiple Listing of Power-One | 0.02 |  |  | 30 | 40 | 50 | 0.03 | 0.06 | 0.09 | 0.15 | 0.23 | 0.3 | 92 | 95 | 95.8 | 96 | 96.2 | 96 | 95.9 | 92.2 | 94.9 | 95.8 | 96.3 | 96.4 | 96.4 | 96 | 91.7 | 94.8 | 95.6 | 96.2 | 96.3 | 96.4 | 96
ABB | MICRO-0.3-I-OUTD-US-240 [240V] | 300 W Utility Interactive Microinverter | 0.3 | 240 | 96 | N | Y | Multiple Listing of Power-One | 0.05 |  |  | 30 | 40 | 50 | 0.03 | 0.06 | 0.09 | 0.15 | 0.23 | 0.3 | 91.7 | 94.8 | 95.8 | 96 | 96.1 | 96 | 95.8 | 92 | 94.8 | 95.7 | 96.3 | 96.4 | 96.4 | 96 | 91.6 | 94.7 | 95.6 | 96.3 | 96.4 | 96.5 | 96
ABB | UNO-2.0-I-OUTD-S-US [208V] | 2 kW, 208 Vac Utility Interactive Inverter. Model number may include -W | 2 | 208 | 95.5 | Y | N | Multiple Listing of Power-One | 0.4 | 2 | 0.4 | 100 | 330 | 416 | 0.2 | 0.4 | 0.6 | 1 | 1.5 | 2 | 90.4 | 94.2 | 95.5 | 95.9 | 95.6 | 95 | 95.4 | 88.3 | 94.1 | 95.3 | 96.1 | 96.1 | 96 | 95.6 | 85.6 | 92.5 | 94.3 | 95.6 | 95.8 | 95.8 | 95
ABB | UNO-2.0-I-OUTD-S-US [240V] | 2 kW, 240 Vac Utility Interactive Inverter. Model number may include -W | 2 | 240 | 95.5 | Y | N | Multiple Listing of Power-One | 0.4 | 2 | 0.4 | 100 | 340 | 416 | 0.2 | 0.4 | 0.6 | 1 | 1.5 | 2 | 89.2 | 94.5 | 95.4 | 96 | 96 | 95.5 | 95.5 | 88.3 | 94.1 | 95.5 | 96.4 | 96.5 | 96.5 | 95.9 | 85.5 | 92.8 | 94.6 | 95.9 | 96.2 | 96.3 | 95.4
ABB | UNO-2.0-I-OUTD-S-US [277V] | 2 kW, 277 Vac Utility Interactive Inverter. Model number may include -W | 2 | 277 | 95.5 | Y | N | Multiple Listing of Power-One | 0.5 | 2 | 0.5 | 100 | 360 | 416 | 0.2 | 0.4 | 0.6 | 1 | 1.5 | 2 | 87.6 | 94.2 | 95.1 | 95.9 | 96 | 95.7 | 95.4 | 87.8 | 93.7 | 95.1 | 96.2 | 96.6 | 96.6 | 95.8 | 85.8 | 93 | 94.7 | 96.1 | 96.4 | 96.6 | 95.6
ABB | UNO-2.0-TL-OUTD-S-US [208V] | 2.0 kW, 208 Vac Utility Interactive Inverter | 2 | 208 | 96.5 | Y | N |  | 0.11 | 2 | 0.11 | 180 | 400 | 480 | 0.2 | 0.4 | 0.6 | 1 | 1.5 | 2 | 91.7068 | 94.899 | 95.5602 | 95.9572 | 95.9308 | 95.8079 | 95.6652 | 92.3515 | 95.6294 | 96.4468 | 96.9728 | 97.0562 | 97.0233 | 96.7044 | 91.0019 | 95.1782 | 96.0695 | 96.7303 | 96.8835 | 96.8764 | 96.4327
ABB | UNO-2.0-TL-OUTD-S-US [240V] | 2.0 kW, 240 Vac Utility Interactive Inverter | 2 | 240 | 96.5 | Y | N |  | 0.15 | 2 | 0.15 | 180 | 400 | 480 | 0.2 | 0.4 | 0.6 | 1 | 1.5 | 2 | 91.2 | 94.5 | 95.4 | 95.8 | 96 | 95.9 | 95.6 | 92.7 | 95.8 | 96.6 | 97.2 | 97.3 | 97.3 | 96.9 | 91.3 | 95.3 | 96.2 | 96.9 | 97.2 | 97.2 | 96.7
ABB | UNO-2.0-TL-OUTD-S-US [277V] | 2.0 kW, 277 Vac Utility Interactive Inverter | 2 | 277 | 96.5 | Y | N |  | 0.15 | 2 | 0.15 | 180 | 400 | 480 | 0.2 | 0.4 | 0.6 | 1 | 1.5 | 2 | 90.2646 | 94.0996 | 95.0474 | 95.7968 | 95.97 | 95.9471 | 95.5 | 91.4691 | 95.1802 | 96.172 | 96.9329 | 97.1504 | 97.2299 | 96.6655 | 91.5415 | 95.4443 | 96.413 | 97.1915 | 97.4681 | 97.5166 | 96.9476
ABB | UNO-2.0-TL-OUTD-S-US-A [208V] | 2.0 kW, 208 Vac Utility Interactive Inverter with arc detector | 2 | 208 | 96.5 | Y | N |  | 0.11 | 2 | 0.11 | 180 | 400 | 480 | 0.2 | 0.4 | 0.6 | 1 | 1.5 | 2 | 91.7068 | 94.899 | 95.5602 | 95.9572 | 95.9308 | 95.8079 | 95.6652 | 92.3515 | 95.6294 | 96.4468 | 96.9728 | 97.0562 | 97.0233 | 96.7044 | 91.0019 | 95.1782 | 96.0695 | 96.7303 | 96.8835 | 96.8764 | 96.4327
ABB | UNO-2.0-TL-OUTD-S-US-A [240V] | 2.0 kW, 240 Vac Utility Interactive Inverter with arc detector | 2 | 240 | 96.5 | Y | N |  | 0.15 | 2 | 0.15 | 180 | 400 | 480 | 0.2 | 0.4 | 0.6 | 1 | 1.5 | 2 | 91.1975 | 94.5303 | 95.4161 | 95.8429 | 95.9573 | 95.8859 | 95.603 | 92.6562 | 95.7866 | 96.5911 | 97.1714 | 97.3297 | 97.3297 | 96.9437 | 91.299 | 95.2613 | 96.1981 | 96.9232 | 97.1551 | 97.1651 | 96.6631
ABB | UNO-2.0-TL-OUTD-S-US-A [277V] | 2.0 kW, 277 Vac Utility Interactive Inverter with arc detector | 2 | 277 | 96.5 | Y | N |  | 0.15 | 2 | 0.15 | 180 | 400 | 480 | 0.2 | 0.4 | 0.6 | 1 | 1.5 | 2 | 90.2646 | 94.0996 | 95.0474 | 95.7968 | 95.97 | 95.9471 | 95.5 | 91.4691 | 95.1802 | 96.172 | 96.9329 | 97.1504 | 97.2299 | 96.6655 | 91.5415 | 95.4443 | 96.413 | 97.1915 | 97.4681 | 97.5166 | 96.9476
ABB | UNO-2.0-TL-OUTD-S-US-B-C-M [208V] | 2.0 kW, 208 Vac Utility Interactive Inverter with revenue grade meter | 2 | 208 | 96.5 | Y | N |  | 0.11 | 2 | 0.11 | 180 | 400 | 480 | 0.2 | 0.4 | 0.6 | 1 | 1.5 | 2 | 91.7068 | 94.899 | 95.5602 | 95.9572 | 95.9308 | 95.8079 | 95.6652 | 92.3515 | 95.6294 | 96.4468 | 96.9728 | 97.0562 | 97.0233 | 96.7044 | 91.0019 | 95.1782 | 96.0695 | 96.7303 | 96.8835 | 96.8764 | 96.4327
ABB | UNO-2.0-TL-OUTD-S-US-B-C-M [240V] | 2.0 kW, 240 Vac Utility Interactive Inverter with revenue grade meter | 2 | 240 | 96.5 | Y | N |  | 0.15 | 2 | 0.15 | 180 | 400 | 480 | 0.2 | 0.4 | 0.6 | 1 | 1.5 | 2 | 91.1975 | 94.5303 | 95.4161 | 95.8429 | 95.9573 | 95.8859 | 95.603 | 92.6562 | 95.7866 | 96.5911 | 97.1714 | 97.3297 | 97.3297 | 96.9437 | 91.299 | 95.2613 | 96.1981 | 96.9232 | 97.1551 | 97.1651 | 96.6631
ABB | UNO-2.0-TL-OUTD-S-US-B-C-M [277V] | 2.0 kW, 277 Vac Utility Interactive Inverter with revenue grade meter | 2 | 277 | 96.5 | Y | N |  | 0.15 | 2 | 0.15 | 180 | 400 | 480 | 0.2 | 0.4 | 0.6 | 1 | 1.5 | 2 | 90.2646 | 94.0996 | 95.0474 | 95.7968 | 95.97 | 95.9471 | 95.5 | 91.4691 | 95.1802 | 96.172 | 96.9329 | 97.1504 | 97.2299 | 96.6655 | 91.5415 | 95.4443 | 96.413 | 97.1915 | 97.4681 | 97.5166 | 96.9476
ABB | UNO-2.0-TL-OUTD-S-US-B-C-M-A [208V] | 2.0 kW, 208 Vac Utility Interactive Inverter with arc detector, with revenue grade meter | 2 | 208 | 96.5 | Y | N |  | 0.11 | 2 | 0.11 | 180 | 400 | 480 | 0.2 | 0.4 | 0.6 | 1 | 1.5 | 2 | 91.7068 | 94.899 | 95.5602 | 95.9572 | 95.9308 | 95.8079 | 95.6652 | 92.3515 | 95.6294 | 96.4468 | 96.9728 | 97.0562 | 97.0233 | 96.7044 | 91.0019 | 95.1782 | 96.0695 | 96.7303 | 96.8835 | 96.8764 | 96.4327
ABB | UNO-2.0-TL-OUTD-S-US-B-C-M-A [240V] | 2.0 kW, 240 Vac Utility Interactive Inverter with arc detector, with revenue grade meter | 2 | 240 | 96.5 | Y | N |  | 0.15 | 2 | 0.15 | 180 | 400 | 480 | 0.2 | 0.4 | 0.6 | 1 | 1.5 | 2 | 91.1975 | 94.5303 | 95.4161 | 95.8429 | 95.9573 | 95.8859 | 95.603 | 92.6562 | 95.7866 | 96.5911 | 97.1714 | 97.3297 | 97.3297 | 96.9437 | 91.299 | 95.2613 | 96.1981 | 96.9232 | 97.1551 | 97.1651 | 96.6631
ABB | UNO-2.0-TL-OUTD-S-US-B-C-M-A [277V] | 2.0 kW, 277 Vac Utility Interactive Inverter with arc detector, with revenue grade meter | 2 | 277 | 96.5 | Y | N |  | 0.15 | 2 | 0.15 | 180 | 400 | 480 | 0.2 | 0.4 | 0.6 | 1 | 1.5 | 2 | 90.2646 | 94.0996 | 95.0474 | 95.7968 | 95.97 | 95.9471 | 95.5 | 91.4691 | 95.1802 | 96.172 | 96.9329 | 97.1504 | 97.2299 | 96.6655 | 91.5415 | 95.4443 | 96.413 | 97.1915 | 97.4681 | 97.5166 | 96.9476
ABB | UNO-2.0-TL-OUTD-S-US-B-M [208V] | 2.0 kW, 208 Vac Utility Interactive Inverter with revenue grade meter | 2 | 208 | 96.5 | Y | N |  | 0.11 | 2 | 0.11 | 180 | 400 | 480 | 0.2 | 0.4 | 0.6 | 1 | 1.5 | 2 | 91.7068 | 94.899 | 95.5602 | 95.9572 | 95.9308 | 95.8079 | 95.6652 | 92.3515 | 95.6294 | 96.4468 | 96.9728 | 97.0562 | 97.0233 | 96.7044 | 91.0019 | 95.1782 | 96.0695 | 96.7303 | 96.8835 | 96.8764 | 96.4327
ABB | UNO-2.0-TL-OUTD-S-US-B-M [240V] | 2.0 kW, 240 Vac Utility Interactive Inverter with revenue grade meter | 2 | 240 | 96.5 | Y | N |  | 0.15 | 2 | 0.15 | 180 | 400 | 480 | 0.2 | 0.4 | 0.6 | 1 | 1.5 | 2 | 91.1975 | 94.5303 | 95.4161 | 95.8429 | 95.9573 | 95.8859 | 95.603 | 92.6562 | 95.7866 | 96.5911 | 97.1714 | 97.3297 | 97.3297 | 96.9437 | 91.299 | 95.2613 | 96.1981 | 96.9232 | 97.1551 | 97.1651 | 96.6631
ABB | UNO-2.0-TL-OUTD-S-US-B-M [277V] | 2.0 kW, 277 Vac Utility Interactive Inverter with revenue grade meter | 2 | 277 | 96.5 | Y | N |  | 0.15 | 2 | 0.15 | 180 | 400 | 480 | 0.2 | 0.4 | 0.6 | 1 | 1.5 | 2 | 90.2646 | 94.0996 | 95.0474 | 95.7968 | 95.97 | 95.9471 | 95.5 | 91.4691 | 95.1802 | 96.172 | 96.9329 | 97.1504 | 97.2299 | 96.6655 | 91.5415 | 95.4443 | 96.413 | 97.1915 | 97.4681 | 97.5166 | 96.9476
ABB | UNO-2.0-TL-OUTD-S-US-B-M-A [208V] | 2.0 kW, 208 Vac Utility Interactive Inverter with arc detector and revenue grade meter | 2 | 208 | 96.5 | Y | N |  | 0.11 | 2 | 0.11 | 180 | 400 | 480 | 0.2 | 0.4 | 0.6 | 1 | 1.5 | 2 | 91.7068 | 94.899 | 95.5602 | 95.9572 | 95.9308 | 95.8079 | 95.6652 | 92.3515 | 95.6294 | 96.4468 | 96.9728 | 97.0562 | 97.0233 | 96.7044 | 91.0019 | 95.1782 | 96.0695 | 96.7303 | 96.8835 | 96.8764 | 96.4327
ABB | UNO-2.0-TL-OUTD-S-US-B-M-A [240V] | 2.0 kW, 240 Vac Utility Interactive Inverter with arc detector and revenue grade meter | 2 | 240 | 96.5 | Y | N |  | 0.15 | 2 | 0.15 | 180 | 400 | 480 | 0.2 | 0.4 | 0.6 | 1 | 1.5 | 2 | 91.1975 | 94.5303 | 95.4161 | 95.8429 | 95.9573 | 95.8859 | 95.603 | 92.6562 | 95.7866 | 96.5911 | 97.1714 | 97.3297 | 97.3297 | 96.9437 | 91.299 | 95.2613 | 96.1981 | 96.9232 | 97.1551 | 97.1651 | 96.6631
ABB | UNO-2.0-TL-OUTD-S-US-B-M-A [277V] | 2.0 kW, 277 Vac Utility Interactive Inverter with arc detector and revenue grade meter | 2 | 277 | 96.5 | Y | N |  | 0.15 | 2 | 0.15 | 180 | 400 | 480 | 0.2 | 0.4 | 0.6 | 1 | 1.5 | 2 | 90.2646 | 94.0996 | 95.0474 | 95.7968 | 95.97 | 95.9471 | 95.5 | 91.4691 | 95.1802 | 96.172 | 96.9329 | 97.1504 | 97.2299 | 96.6655 | 91.5415 | 95.4443 | 96.413 | 97.1915 | 97.4681 | 97.5166 | 96.9476
ABB | UNO-2.0-TL-OUTD-S-US-C-M [208V] | 2.0 kW, 208 Vac Utility Interactive Inverter with revenue grade meter | 2 | 208 | 96.5 | Y | N |  | 0.11 | 2 | 0.11 | 180 | 400 | 480 | 0.2 | 0.4 | 0.6 | 1 | 1.5 | 2 | 91.7068 | 94.899 | 95.5602 | 95.9572 | 95.9308 | 95.8079 | 95.6652 | 92.3515 | 95.6294 | 96.4468 | 96.9728 | 97.0562 | 97.0233 | 96.7044 | 91.0019 | 95.1782 | 96.0695 | 96.7303 | 96.8835 | 96.8764 | 96.4327
ABB | UNO-2.0-TL-OUTD-S-US-C-M [240V] | 2.0 kW, 240 Vac Utility Interactive Inverter with revenue grade meter | 2 | 240 | 96.5 | Y | N |  | 0.15 | 2 | 0.15 | 180 | 400 | 480 | 0.2 | 0.4 | 0.6 | 1 | 1.5 | 2 | 91.1975 | 94.5303 | 95.4161 | 95.8429 | 95.9573 | 95.8859 | 95.603 | 92.6562 | 95.7866 | 96.5911 | 97.1714 | 97.3297 | 97.3297 | 96.9437 | 91.299 | 95.2613 | 96.1981 | 96.9232 | 97.1551 | 97.1651 | 96.6631
ABB | UNO-2.0-TL-OUTD-S-US-C-M [277V] | 2.0 kW, 277 Vac Utility Interactive Inverter with revenue grade meter | 2 | 277 | 96.5 | Y | N |  | 0.15 | 2 | 0.15 | 180 | 400 | 480 | 0.2 | 0.4 | 0.6 | 1 | 1.5 | 2 | 90.2646 | 94.0996 | 95.0474 | 95.7968 | 95.97 | 95.9471 | 95.5 | 91.4691 | 95.1802 | 96.172 | 96.9329 | 97.1504 | 97.2299 | 96.6655 | 91.5415 | 95.4443 | 96.413 | 97.1915 | 97.4681 | 97.5166 | 96.9476
ABB | UNO-2.0-TL-OUTD-S-US-C-M-A [208V] | 2.0 kW, 208 Vac Utility Interactive Inverter with revenue grade meter | 2 | 208 | 96.5 | Y | N |  | 0.11 | 2 | 0.11 | 180 | 400 | 480 | 0.2 | 0.4 | 0.6 | 1 | 1.5 | 2 | 91.7068 | 94.899 | 95.5602 | 95.9572 | 95.9308 | 95.8079 | 95.6652 | 92.3515 | 95.6294 | 96.4468 | 96.9728 | 97.0562 | 97.0233 | 96.7044 | 91.0019 | 95.1782 | 96.0695 | 96.7303 | 96.8835 | 96.8764 | 96.4327
ABB | UNO-2.0-TL-OUTD-S-US-C-M-A [240V] | 2.0 kW, 240 Vac Utility Interactive Inverter with revenue grade meter | 2 | 240 | 96.5 | Y | N |  | 0.15 | 2 | 0.15 | 180 | 400 | 480 | 0.2 | 0.4 | 0.6 | 1 | 1.5 | 2 | 91.1975 | 94.5303 | 95.4161 | 95.8429 | 95.9573 | 95.8859 | 95.603 | 92.6562 | 95.7866 | 96.5911 | 97.1714 | 97.3297 | 97.3297 | 96.9437 | 91.299 | 95.2613 | 96.1981 | 96.9232 | 97.1551 | 97.1651 | 96.6631
ABB | UNO-2.0-TL-OUTD-S-US-C-M-A [277V] | 2.0 kW, 277 Vac Utility Interactive Inverter with revenue grade meter | 2 | 277 | 96.5 | Y | N |  | 0.15 | 2 | 0.15 | 180 | 400 | 480 | 0.2 | 0.4 | 0.6 | 1 | 1.5 | 2 | 90.2646 | 94.0996 | 95.0474 | 95.7968 | 95.97 | 95.9471 | 95.5 | 91.4691 | 95.1802 | 96.172 | 96.9329 | 97.1504 | 97.2299 | 96.6655 | 91.5415 | 95.4443 | 96.413 | 97.1915 | 97.4681 | 97.5166 | 96.9476
ABB | UNO-2.0-TL-OUTD-S-US-Z-A [208V] | 2.0 kW, 208 Vac Utility Interactive Inverter with arc detector | 2 | 208 | 96.5 | Y | N |  | 0.11 | 2 | 0.11 | 180 | 400 | 480 | 0.2 | 0.4 | 0.6 | 1 | 1.5 | 2 | 91.7068 | 94.899 | 95.5602 | 95.9572 | 95.9308 | 95.8079 | 95.6652 | 92.3515 | 95.6294 | 96.4468 | 96.9728 | 97.0562 | 97.0233 | 96.7044 | 91.0019 | 95.1782 | 96.0695 | 96.7303 | 96.8835 | 96.8764 | 96.4327
ABB | UNO-2.0-TL-OUTD-S-US-Z-A [240V] | 2.0 kW, 240 Vac Utility Interactive Inverter with arc detector | 2 | 240 | 96.5 | Y | N |  | 0.15 | 2 | 0.15 | 180 | 400 | 480 | 0.2 | 0.4 | 0.6 | 1 | 1.5 | 2 | 91.1975 | 94.5303 | 95.4161 | 95.8429 | 95.9573 | 95.8859 | 95.603 | 92.6562 | 95.7866 | 96.5911 | 97.1714 | 97.3297 | 97.3297 | 96.9437 | 91.299 | 95.2613 | 96.1981 | 96.9232 | 97.1551 | 97.1651 | 96.6631
ABB | UNO-2.0-TL-OUTD-S-US-Z-A [277V] | 2.0 kW, 277 Vac Utility Interactive Inverter with arc detector | 2 | 277 | 96.5 | Y | N |  | 0.15 | 2 | 0.15 | 180 | 400 | 480 | 0.2 | 0.4 | 0.6 | 1 | 1.5 | 2 | 90.2646 | 94.0996 | 95.0474 | 95.7968 | 95.97 | 95.9471 | 95.5 | 91.4691 | 95.1802 | 96.172 | 96.9329 | 97.1504 | 97.2299 | 96.6655 | 91.5415 | 95.4443 | 96.413 | 97.1915 | 97.4681 | 97.5166 | 96.9476
ABB | UNO-2.0-TL-OUTD-S-US-Z-M-A [208V] | 2.0 kW, 208 Vac Utility Interactive Inverter with arc detector and revenue grade meter | 2 | 208 | 96.5 | Y | N |  | 0.11 | 2 | 0.11 | 180 | 400 | 480 | 0.2 | 0.4 | 0.6 | 1 | 1.5 | 2 | 91.7068 | 94.899 | 95.5602 | 95.9572 | 95.9308 | 95.8079 | 95.6652 | 92.3515 | 95.6294 | 96.4468 | 96.9728 | 97.0562 | 97.0233 | 96.7044 | 91.0019 | 95.1782 | 96.0695 | 96.7303 | 96.8835 | 96.8764 | 96.4327
ABB | UNO-2.0-TL-OUTD-S-US-Z-M-A [240V] | 2.0 kW, 240 Vac Utility Interactive Inverter with arc detector and revenue grade meter | 2 | 240 | 96.5 | Y | N |  | 0.15 | 2 | 0.15 | 180 | 400 | 480 | 0.2 | 0.4 | 0.6 | 1 | 1.5 | 2 | 91.1975 | 94.5303 | 95.4161 | 95.8429 | 95.9573 | 95.8859 | 95.603 | 92.6562 | 95.7866 | 96.5911 | 97.1714 | 97.3297 | 97.3297 | 96.9437 | 91.299 | 95.2613 | 96.1981 | 96.9232 | 97.1551 | 97.1651 | 96.6631
ABB | UNO-2.0-TL-OUTD-S-US-Z-M-A [277V] | 2.0 kW, 277 Vac Utility Interactive Inverter with arc detector and revenue grade meter | 2 | 277 | 96.5 | Y | N |  | 0.15 | 2 | 0.15 | 180 | 400 | 480 | 0.2 | 0.4 | 0.6 | 1 | 1.5 | 2 | 90.2646 | 94.0996 | 95.0474 | 95.7968 | 95.97 | 95.9471 | 95.5 | 91.4691 | 95.1802 | 96.172 | 96.9329 | 97.1504 | 97.2299 | 96.6655 | 91.5415 | 95.4443 | 96.413 | 97.1915 | 97.4681 | 97.5166 | 96.9476
ABB | UNO-2.5-I-OUTD-S-US [208V] | 2.5 kW, 208 Vac Utility Interactive Inverter. Model number may include -W | 2.5 | 208 | 95.5 | Y | N | Multiple Listing of Power-One | 0.4 | 2.5 | 0.4 | 100 | 330 | 416 | 0.25 | 0.5 | 0.75 | 1.25 | 1.88 | 2.5 | 91.9 | 95.2 | 95.8 | 95.8 | 95.2 | 94.2 | 95.2 | 89.6 | 94.9 | 95.8 | 96.1 | 96 | 95.7 | 95.7 | 87.5 | 93.6 | 94.9 | 95.8 | 95.8 | 95.6 | 95.2
ABB | UNO-2.5-I-OUTD-S-US [240V] | 2.5 kW, 240 Vac Utility Interactive Inverter. Model number may include -W | 2.5 | 240 | 96 | Y | N | Multiple Listing of Power-One | 0.4 | 2.5 | 0.4 | 100 | 340 | 416 | 0.25 | 0.5 | 0.75 | 1.25 | 1.88 | 2.5 | 91 | 95.1 | 95.8 | 96.1 | 95.7 | 95 | 95.5 | 89.8 | 95 | 96 | 96.5 | 96.5 | 96.3 | 96.1 | 87.8 | 94 | 95.3 | 96.3 | 96.3 | 96.3 | 95.7
ABB | UNO-2.5-I-OUTD-S-US [277V] | 2.5 kW, 277 Vac Utility Interactive Inverter. Model number may include -W | 2.5 | 277 | 96 | Y | N | Multiple Listing of Power-One | 0.5 | 2.5 | 0.5 | 100 | 360 | 416 | 0.25 | 0.5 | 0.75 | 1.25 | 1.88 | 2.5 | 89.7 | 94.7 | 95.6 | 96 | 95.9 | 95.3 | 95.5 | 89 | 94.6 | 95.7 | 96.4 | 96.6 | 96.6 | 96.1 | 87.9 | 94.1 | 95.4 | 96.4 | 96.6 | 96.6 | 95.9
ABB | PVI-3.0-OUTD-S-US [208V] | 3 kW, 208 Vac Utility Interactive Inverter | 3 | 208 | 96 | Y | N | Multiple Listing of Power-One | 0.1 | 3 | 0.1 | 100 | 310 | 480 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 93.1 | 95.5 | 96 | 95.9 | 95.7 | 95.1 | 95.6 | 93.3 | 95.9 | 96.4 | 96.4 | 96.2 | 95.8 | 96.1 | 91 | 94.9 | 95.7 | 96 | 95.8 | 95.5 | 95.6
ABB | PVI-3.0-OUTD-S-US [240V] | 3 kW, 240 Vac Utility Interactive Inverter | 3 | 240 | 96 | Y | N | Multiple Listing of Power-One | 0.1 | 3 | 0.1 | 100 | 340 | 480 | 0.25 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 92.5 | 95.2 | 95.9 | 96.1 | 95.9 | 95.5 | 95.7 | 93.1 | 95.9 | 96.5 | 96.7 | 96.7 | 96.4 | 96.5 | 91.1 | 95.1 | 96 | 96.4 | 96.4 | 96.2 | 96.1
ABB | PVI-3.0-OUTD-S-US [277V] | 3 kW, 277 Vac Utility Interactive Inverter | 3 | 277 | 96 | Y | N | Multiple Listing of Power-One | 0.2 | 3 | 0.2 | 100 | 390 | 480 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 91.4 | 94.7 | 95.5 | 96.1 | 95.9 | 95.6 | 95.7 | 92.5 | 95.8 | 96.5 | 96.9 | 96.9 | 96.8 | 96.6 | 91.1 | 95.2 | 96.2 | 96.7 | 96.8 | 96.7 | 96.4
ABB | PVI-3.0-OUTD-S-US-A [208V] | 3 kW, 208 Vac Utility Interactive Inverter with arc detector | 3 | 208 | 96 | Y | N | Multiple Listing of Power-One | 0.1 | 3 | 0.1 | 100 | 310 | 480 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 93.1 | 95.5 | 96 | 95.9 | 95.7 | 95.1 | 95.6 | 93.3 | 95.9 | 96.4 | 96.4 | 96.2 | 95.8 | 96.1 | 91 | 94.9 | 95.7 | 96 | 95.8 | 95.5 | 95.6 | 2017-07-01 | 2018-10-15
ABB | PVI-3.0-OUTD-S-US-A [240V] | 3 kW, 240 Vac Utility Interactive Inverter with arc detector | 3 | 240 | 96 | Y | N | Multiple Listing of Power-One | 0.1 | 3 | 0.1 | 100 | 340 | 480 | 0.25 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 92.5 | 95.2 | 95.9 | 96.1 | 95.9 | 95.5 | 95.7 | 93.1 | 95.9 | 96.5 | 96.7 | 96.7 | 96.4 | 96.5 | 91.1 | 95.1 | 96 | 96.4 | 96.4 | 96.2 | 96.1 | 2017-07-01 | 2018-10-15
ABB | PVI-3.0-OUTD-S-US-A [277V] | 3 kW, 277 Vac Utility Interactive Inverter with arc detector | 3 | 277 | 96 | Y | N | Multiple Listing of Power-One | 0.2 | 3 | 0.2 | 100 | 390 | 480 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 91.4 | 94.7 | 95.5 | 96.1 | 95.9 | 95.6 | 95.7 | 92.5 | 95.8 | 96.5 | 96.9 | 96.9 | 96.8 | 96.6 | 91.1 | 95.2 | 96.2 | 96.7 | 96.8 | 96.7 | 96.4 | 2017-07-01 | 2018-10-15
ABB | PVI-3.0-OUTD-S-US-Z [208V] | 3 kW, 208 Vac Utility Interactive Inverter | 3 | 208 | 96 | Y | N |  | 0.1 | 3 | 0.1 | 100 | 310 | 480 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 93.1 | 95.5 | 96 | 95.9 | 95.7 | 95.1 | 95.6 | 93.3 | 95.9 | 96.4 | 96.4 | 96.2 | 95.8 | 96.1 | 91 | 94.9 | 95.7 | 96 | 95.8 | 95.5 | 95.6
ABB | PVI-3.0-OUTD-S-US-Z [240V] | 3 kW, 240 Vac Utility Interactive Inverter | 3 | 240 | 96 | Y | N |  | 0.1 | 3 | 0.1 | 100 | 340 | 480 | 0.25 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 92.5 | 95.2 | 95.9 | 96.1 | 95.9 | 95.5 | 95.7 | 93.1 | 95.9 | 96.5 | 96.7 | 96.7 | 96.4 | 96.5 | 91.1 | 95.1 | 96 | 96.4 | 96.4 | 96.2 | 96.1
ABB | PVI-3.0-OUTD-S-US-Z [277V] | 3 kW, 277 Vac Utility Interactive Inverter | 3 | 277 | 96 | Y | N |  | 0.2 | 3 | 0.2 | 100 | 390 | 480 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 91.4 | 94.7 | 95.5 | 96.1 | 95.9 | 95.6 | 95.7 | 92.5 | 95.8 | 96.5 | 96.9 | 96.9 | 96.8 | 96.6 | 91.1 | 95.2 | 96.2 | 96.7 | 96.8 | 96.7 | 96.4
ABB | PVI-3.0-OUTD-S-US-Z-A [208V] | 3 kW, 208 Vac Utility Interactive Inverter with arc detector | 3 | 208 | 96 | Y | N | Multiple Listing of Power-One | 0.1 | 3 | 0.1 | 100 | 310 | 480 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 93.1 | 95.5 | 96 | 95.9 | 95.7 | 95.1 | 95.6 | 93.3 | 95.9 | 96.4 | 96.4 | 96.2 | 95.8 | 96.1 | 91 | 94.9 | 95.7 | 96 | 95.8 | 95.5 | 95.6 | 2017-07-01 | 2018-10-15
ABB | PVI-3.0-OUTD-S-US-Z-A [240V] | 3 kW, 240 Vac Utility Interactive Inverter with arc detector | 3 | 240 | 96 | Y | N | Multiple Listing of Power-One | 0.1 | 3 | 0.1 | 100 | 340 | 480 | 0.25 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 92.5 | 95.2 | 95.9 | 96.1 | 95.9 | 95.5 | 95.7 | 93.1 | 95.9 | 96.5 | 96.7 | 96.7 | 96.4 | 96.5 | 91.1 | 95.1 | 96 | 96.4 | 96.4 | 96.2 | 96.1 | 2017-07-01 | 2018-10-15
ABB | PVI-3.0-OUTD-S-US-Z-A [277V] | 3 kW, 277 Vac Utility Interactive Inverter with arc detector | 3 | 277 | 96 | Y | N | Multiple Listing of Power-One | 0.2 | 3 | 0.2 | 100 | 390 | 480 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 91.4 | 94.7 | 95.5 | 96.1 | 95.9 | 95.6 | 95.7 | 92.5 | 95.8 | 96.5 | 96.9 | 96.9 | 96.8 | 96.6 | 91.1 | 95.2 | 96.2 | 96.7 | 96.8 | 96.7 | 96.4 | 2017-07-01 | 2018-10-15
ABB | PVI-3.0-OUTD-S-US-Z-M-A [208V] | 3 kW, 208 Vac Utility Interactive Inverter with arc-fault detection and meter | 3 | 208 | 96 | Y | N | Multiple Listing of Power-One | 0.1 |  |  | 100 | 310 | 480 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 93.1 | 95.5 | 96 | 95.9 | 95.7 | 95.1 | 95.6 | 93.3 | 95.9 | 96.4 | 96.4 | 96.2 | 95.8 | 96.1 | 91 | 94.9 | 95.7 | 96 | 95.8 | 95.5 | 95.6 | 2017-07-01 | 2018-10-15
ABB | PVI-3.0-OUTD-S-US-Z-M-A [240V] | 3 kW, 240 Vac Utility Interactive Inverter with arc-fault detection and meter | 3 | 240 | 96 | Y | N | Multiple Listing of Power-One | 0.1 |  |  | 100 | 340 | 480 | 0.25 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 92.5 | 95.2 | 95.9 | 96.1 | 95.9 | 95.5 | 95.7 | 93.1 | 95.9 | 96.5 | 96.7 | 96.7 | 96.4 | 96.5 | 91.1 | 95.1 | 96 | 96.4 | 96.4 | 96.2 | 96.1 | 2017-07-01 | 2018-10-15
ABB | PVI-3.0-OUTD-S-US-Z-M-A [277V] | 3 kW, 277 Vac Utility Interactive Inverter with arc-fault detection and meter | 3 | 277 | 96 | Y | N | Multiple Listing of Power-One | 0.2 |  |  | 100 | 390 | 480 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 91.4 | 94.7 | 95.5 | 96.1 | 95.9 | 95.6 | 95.7 | 92.5 | 95.8 | 96.5 | 96.9 | 96.9 | 96.8 | 96.6 | 91.1 | 95.2 | 96.2 | 96.7 | 96.8 | 96.7 | 96.4 | 2017-07-01 | 2018-10-15
ABB | PVI-3.0-OUTD-US [208V] | 3 kW, 208 Vac Utility Interactive Inverter | 3 | 208 | 96 | Y | N | Multiple Listing of Power-One | 0.1 | 3 | 0.1 | 100 | 310 | 480 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 93.1 | 95.5 | 96 | 95.9 | 95.7 | 95.1 | 95.6 | 93.3 | 95.9 | 96.4 | 96.4 | 96.2 | 95.8 | 96.1 | 91 | 94.9 | 95.7 | 96 | 95.8 | 95.5 | 95.6
ABB | PVI-3.0-OUTD-US [240V] | 3 kW, 240 Vac Utility Interactive Inverter, model # may include -S- or -W | 3 | 240 | 96 | Y | N | Multiple Listing of Power-One | 0.1 | 3 | 0.1 | 100 | 340 | 480 | 0.25 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 92.5 | 95.2 | 95.9 | 96.1 | 95.9 | 95.5 | 95.7 | 93.1 | 95.9 | 96.5 | 96.7 | 96.7 | 96.4 | 96.5 | 91.1 | 95.1 | 96 | 96.4 | 96.4 | 96.2 | 96.1
ABB | PVI-3.0-OUTD-US [277V] | 3 kW, 277 Vac Utility Interactive Inverter, model # may include -S- or -W | 3 | 277 | 96 | Y | N | Multiple Listing of Power-One | 0.2 | 3 | 0.2 | 100 | 390 | 480 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 91.4 | 94.7 | 95.5 | 96.1 | 95.9 | 95.6 | 95.7 | 92.5 | 95.8 | 96.5 | 96.9 | 96.9 | 96.8 | 96.6 | 91.1 | 95.2 | 96.2 | 96.7 | 96.8 | 96.7 | 96.4
ABB | UNO-3.0-TL-OUTD-S-US [208V] | 3.0 kW, 208 Vac Utility Interactive Inverter | 3 | 208 | 96.5 | Y | N |  | 0.11 | 3 | 0.11 | 180 | 400 | 480 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 93.5877 | 95.5788 | 95.9532 | 95.9149 | 95.7186 | 95.1981 | 95.6697 | 94.4062 | 96.4712 | 96.8978 | 97.0529 | 97.019 | 96.7605 | 96.8667 | 93.6377 | 96.0982 | 96.6144 | 96.8857 | 96.8551 | 96.6678 | 96.6567
ABB | UNO-3.0-TL-OUTD-S-US [240V] | 3.0 kW, 240 Vac Utility Interactive Inverter | 3 | 240 | 96.5 | Y | N |  | 0.15 | 3 | 0.15 | 180 | 400 | 480 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 93.094 | 95.4386 | 95.8649 | 95.9573 | 95.8111 | 95.4222 | 95.7015 | 94.5916 | 96.6224 | 97.087 | 97.3297 | 97.3224 | 97.1876 | 97.1447 | 93.754 | 96.232 | 96.804 | 97.1551 | 97.1447 | 97.1026 | 96.9226
ABB | UNO-3.0-TL-OUTD-S-US [277V] | 3.0 kW, 277 Vac Utility Interactive Inverter | 3 | 277 | 96.5 | Y | N |  | 0.2 | 3 | 0.2 | 180 | 400 | 480 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 92.4542 | 95.1981 | 95.7797 | 95.9716 | 95.9228 | 95.6371 | 95.7266 | 93.7103 | 96.2189 | 96.8155 | 97.1633 | 97.2311 | 97.1831 | 96.9732 | 93.9658 | 96.4497 | 97.0595 | 97.4757 | 97.5241 | 97.5271 | 97.2623
ABB | UNO-3.0-TL-OUTD-S-US-A [208V] | 3.0 kW, 208 Vac Utility Interactive Inverter with arc detector | 3 | 208 | 96.5 | Y | N |  | 0.11 | 3 | 0.11 | 180 | 400 | 480 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 93.5877 | 95.5788 | 95.9532 | 95.9149 | 95.7186 | 95.1981 | 95.6697 | 94.4062 | 96.4712 | 96.8978 | 97.0529 | 97.019 | 96.7605 | 96.8667 | 93.6377 | 96.0982 | 96.6144 | 96.8857 | 96.8551 | 96.6678 | 96.6567
ABB | UNO-3.0-TL-OUTD-S-US-A [240V] | 3.0 kW, 240 Vac Utility Interactive Inverter with arc detector | 3 | 240 | 96.5 | Y | N |  | 0.15 | 3 | 0.15 | 180 | 400 | 480 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 93.094 | 95.4386 | 95.8649 | 95.9573 | 95.8111 | 95.4222 | 95.7015 | 94.5916 | 96.6224 | 97.087 | 97.3297 | 97.3224 | 97.1876 | 97.1447 | 93.754 | 96.232 | 96.804 | 97.1551 | 97.1447 | 97.1026 | 96.9226
ABB | UNO-3.0-TL-OUTD-S-US-A [277V] | 3.0 kW, 277 Vac Utility Interactive Inverter with arc detector | 3 | 277 | 96.5 | Y | N |  | 0.2 | 3 | 0.2 | 180 | 400 | 480 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 92.4542 | 95.1981 | 95.7797 | 95.9716 | 95.9228 | 95.6371 | 95.7266 | 93.7103 | 96.2189 | 96.8155 | 97.1633 | 97.2311 | 97.1831 | 96.9732 | 93.9658 | 96.4497 | 97.0595 | 97.4757 | 97.5241 | 97.5271 | 97.2623
ABB | UNO-3.0-TL-OUTD-S-US-B-C-M [208V] | 3.0 kW, 208 Vac Utility Interactive Inverter with revenue grade meter | 3 | 208 | 96.5 | Y | N |  | 0.11 | 3 | 0.11 | 180 | 400 | 480 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 93.5877 | 95.5788 | 95.9532 | 95.9149 | 95.7186 | 95.1981 | 95.6697 | 94.4062 | 96.4712 | 96.8978 | 97.0529 | 97.019 | 96.7605 | 96.8667 | 93.6377 | 96.0982 | 96.6144 | 96.8857 | 96.8551 | 96.6678 | 96.6567
ABB | UNO-3.0-TL-OUTD-S-US-B-C-M [240V] | 3.0 kW, 240 Vac Utility Interactive Inverter with revenue grade meter | 3 | 240 | 96.5 | Y | N |  | 0.15 | 3 | 0.15 | 180 | 400 | 480 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 93.094 | 95.4386 | 95.8649 | 95.9573 | 95.8111 | 95.4222 | 95.7015 | 94.5916 | 96.6224 | 97.087 | 97.3297 | 97.3224 | 97.1876 | 97.1447 | 93.754 | 96.232 | 96.804 | 97.1551 | 97.1447 | 97.1026 | 96.9226
ABB | UNO-3.0-TL-OUTD-S-US-B-C-M [277V] | 3.0 kW, 277 Vac Utility Interactive Inverter with revenue grade meter | 3 | 277 | 96.5 | Y | N |  | 0.2 | 3 | 0.2 | 180 | 400 | 480 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 92.4542 | 95.1981 | 95.7797 | 95.9716 | 95.9228 | 95.6371 | 95.7266 | 93.7103 | 96.2189 | 96.8155 | 97.1633 | 97.2311 | 97.1831 | 96.9732 | 93.9658 | 96.4497 | 97.0595 | 97.4757 | 97.5241 | 97.5271 | 97.2623
ABB | UNO-3.0-TL-OUTD-S-US-B-C-M-A [208V] | 3.0 kW, 208 Vac Utility Interactive Inverter with arc detector and revenue grade meter | 3 | 208 | 96.5 | Y | N |  | 0.11 | 3 | 0.11 | 180 | 400 | 480 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 93.5877 | 95.5788 | 95.9532 | 95.9149 | 95.7186 | 95.1981 | 95.6697 | 94.4062 | 96.4712 | 96.8978 | 97.0529 | 97.019 | 96.7605 | 96.8667 | 93.6377 | 96.0982 | 96.6144 | 96.8857 | 96.8551 | 96.6678 | 96.6567
ABB | UNO-3.0-TL-OUTD-S-US-B-C-M-A [240V] | 3.0 kW, 240 Vac Utility Interactive Inverter with arc detector and revenue grade meter | 3 | 240 | 96.5 | Y | N |  | 0.15 | 3 | 0.15 | 180 | 400 | 480 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 93.094 | 95.4386 | 95.8649 | 95.9573 | 95.8111 | 95.4222 | 95.7015 | 94.5916 | 96.6224 | 97.087 | 97.3297 | 97.3224 | 97.1876 | 97.1447 | 93.754 | 96.232 | 96.804 | 97.1551 | 97.1447 | 97.1026 | 96.9226
ABB | UNO-3.0-TL-OUTD-S-US-B-C-M-A [277V] | 3.0 kW, 277 Vac Utility Interactive Inverter with arc detector and revenue grade meter | 3 | 277 | 96.5 | Y | N |  | 0.2 | 3 | 0.2 | 180 | 400 | 480 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 92.4542 | 95.1981 | 95.7797 | 95.9716 | 95.9228 | 95.6371 | 95.7266 | 93.7103 | 96.2189 | 96.8155 | 97.1633 | 97.2311 | 97.1831 | 96.9732 | 93.9658 | 96.4497 | 97.0595 | 97.4757 | 97.5241 | 97.5271 | 97.2623
ABB | UNO-3.0-TL-OUTD-S-US-B-M [208V] | 3.0 kW, 208 Vac Utility Interactive Inverter with revenue grade meter | 3 | 208 | 96.5 | Y | N |  | 0.11 | 3 | 0.11 | 180 | 400 | 480 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 93.5877 | 95.5788 | 95.9532 | 95.9149 | 95.7186 | 95.1981 | 95.6697 | 94.4062 | 96.4712 | 96.8978 | 97.0529 | 97.019 | 96.7605 | 96.8667 | 93.6377 | 96.0982 | 96.6144 | 96.8857 | 96.8551 | 96.6678 | 96.6567
ABB | UNO-3.0-TL-OUTD-S-US-B-M [240V] | 3.0 kW, 240 Vac Utility Interactive Inverter with revenue grade meter | 3 | 240 | 96.5 | Y | N |  | 0.15 | 3 | 0.15 | 180 | 400 | 480 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 93.094 | 95.4386 | 95.8649 | 95.9573 | 95.8111 | 95.4222 | 95.7015 | 94.5916 | 96.6224 | 97.087 | 97.3297 | 97.3224 | 97.1876 | 97.1447 | 93.754 | 96.232 | 96.804 | 97.1551 | 97.1447 | 97.1026 | 96.9226
ABB | UNO-3.0-TL-OUTD-S-US-B-M [277V] | 3.0 kW, 277 Vac Utility Interactive Inverter with revenue grade meter | 3 | 277 | 96.5 | Y | N |  | 0.2 | 3 | 0.2 | 180 | 400 | 480 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 92.4542 | 95.1981 | 95.7797 | 95.9716 | 95.9228 | 95.6371 | 95.7266 | 93.7103 | 96.2189 | 96.8155 | 97.1633 | 97.2311 | 97.1831 | 96.9732 | 93.9658 | 96.4497 | 97.0595 | 97.4757 | 97.5241 | 97.5271 | 97.2623
ABB | UNO-3.0-TL-OUTD-S-US-B-M-A [208V] | 3.0 kW, 208 Vac Utility Interactive Inverter with arc detector and revenue grade meter | 3 | 208 | 96.5 | Y | N |  | 0.11 | 3 | 0.11 | 180 | 400 | 480 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 93.5877 | 95.5788 | 95.9532 | 95.9149 | 95.7186 | 95.1981 | 95.6697 | 94.4062 | 96.4712 | 96.8978 | 97.0529 | 97.019 | 96.7605 | 96.8667 | 93.6377 | 96.0982 | 96.6144 | 96.8857 | 96.8551 | 96.6678 | 96.6567
ABB | UNO-3.0-TL-OUTD-S-US-B-M-A [240V] | 3.0 kW, 240 Vac Utility Interactive Inverter with arc detector and revenue grade meter | 3 | 240 | 96.5 | Y | N |  | 0.15 | 3 | 0.15 | 180 | 400 | 480 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 93.094 | 95.4386 | 95.8649 | 95.9573 | 95.8111 | 95.4222 | 95.7015 | 94.5916 | 96.6224 | 97.087 | 97.3297 | 97.3224 | 97.1876 | 97.1447 | 93.754 | 96.232 | 96.804 | 97.1551 | 97.1447 | 97.1026 | 96.9226
ABB | UNO-3.0-TL-OUTD-S-US-B-M-A [277V] | 3.0 kW, 277 Vac Utility Interactive Inverter with arc detector and revenue grade meter | 3 | 277 | 96.5 | Y | N |  | 0.2 | 3 | 0.2 | 180 | 400 | 480 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 92.4542 | 95.1981 | 95.7797 | 95.9716 | 95.9228 | 95.6371 | 95.7266 | 93.7103 | 96.2189 | 96.8155 | 97.1633 | 97.2311 | 97.1831 | 96.9732 | 93.9658 | 96.4497 | 97.0595 | 97.4757 | 97.5241 | 97.5271 | 97.2623
ABB | UNO-3.0-TL-OUTD-S-US-C-M [208V] | 3.0 kW, 208 Vac Utility Interactive Inverter with revenue grade meter | 3 | 208 | 96.5 | Y | N |  | 0.11 | 3 | 0.11 | 180 | 400 | 480 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 93.5877 | 95.5788 | 95.9532 | 95.9149 | 95.7186 | 95.1981 | 95.6697 | 94.4062 | 96.4712 | 96.8978 | 97.0529 | 97.019 | 96.7605 | 96.8667 | 93.6377 | 96.0982 | 96.6144 | 96.8857 | 96.8551 | 96.6678 | 96.6567
ABB | UNO-3.0-TL-OUTD-S-US-C-M [240V] | 3.0 kW 240 Vac Utility Interactive Inverter, with revenue grade meter | 3 | 240 | 96.5 | Y | N |  | 0.15 | 3 | 0.15 | 180 | 400 | 480 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 93.094 | 95.4386 | 95.8649 | 95.9573 | 95.8111 | 95.4222 | 95.7015 | 94.5916 | 96.6224 | 97.087 | 97.3297 | 97.3224 | 97.1876 | 97.1447 | 93.754 | 96.232 | 96.804 | 97.1551 | 97.1447 | 97.1026 | 96.9226
ABB | UNO-3.0-TL-OUTD-S-US-C-M [277V] | 3.0 kW, 277 Vac Utility Interactive Inverter with revenue grade meter | 3 | 277 | 96.5 | Y | N |  | 0.2 | 3 | 0.2 | 180 | 400 | 480 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 92.4542 | 95.1981 | 95.7797 | 95.9716 | 95.9228 | 95.6371 | 95.7266 | 93.7103 | 96.2189 | 96.8155 | 97.1633 | 97.2311 | 97.1831 | 96.9732 | 93.9658 | 96.4497 | 97.0595 | 97.4757 | 97.5241 | 97.5271 | 97.2623
ABB | UNO-3.0-TL-OUTD-S-US-C-M-A [208V] | 3.0 kW, 208 Vac Utility Interactive Inverter with arc detector and revenue grade meter | 3 | 208 | 96.5 | Y | N |  | 0.11 | 3 | 0.11 | 180 | 400 | 480 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 93.5877 | 95.5788 | 95.9532 | 95.9149 | 95.7186 | 95.1981 | 95.6697 | 94.4062 | 96.4712 | 96.8978 | 97.0529 | 97.019 | 96.7605 | 96.8667 | 93.6377 | 96.0982 | 96.6144 | 96.8857 | 96.8551 | 96.6678 | 96.6567
ABB | UNO-3.0-TL-OUTD-S-US-C-M-A [240V] | 3.0 kW, 240 Vac Utility Interactive Inverter with arc detector and revenue grade meter | 3 | 240 | 96.5 | Y | N |  | 0.15 | 3 | 0.15 | 180 | 400 | 480 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 93.094 | 95.4386 | 95.8649 | 95.9573 | 95.8111 | 95.4222 | 95.7015 | 94.5916 | 96.6224 | 97.087 | 97.3297 | 97.3224 | 97.1876 | 97.1447 | 93.754 | 96.232 | 96.804 | 97.1551 | 97.1447 | 97.1026 | 96.9226
ABB | UNO-3.0-TL-OUTD-S-US-C-M-A [277V] | 3.0 kW, 277 Vac Utility Interactive Inverter with arc detector and revenue grade meter | 3 | 277 | 96.5 | Y | N |  | 0.2 | 3 | 0.2 | 180 | 400 | 480 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 92.4542 | 95.1981 | 95.7797 | 95.9716 | 95.9228 | 95.6371 | 95.7266 | 93.7103 | 96.2189 | 96.8155 | 97.1633 | 97.2311 | 97.1831 | 96.9732 | 93.9658 | 96.4497 | 97.0595 | 97.4757 | 97.5241 | 97.5271 | 97.2623
ABB | UNO-3.0-TL-OUTD-S-US-Z-A [208V] | 3.0 kW, 208 Vac Utility Interactive Inverter with arc detector | 3 | 208 | 96.5 | Y | N |  | 0.11 | 3 | 0.11 | 180 | 400 | 480 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 93.5877 | 95.5788 | 95.9532 | 95.9149 | 95.7186 | 95.1981 | 95.6697 | 94.4062 | 96.4712 | 96.8978 | 97.0529 | 97.019 | 96.7605 | 96.8667 | 93.6377 | 96.0982 | 96.6144 | 96.8857 | 96.8551 | 96.6678 | 96.6567
ABB | UNO-3.0-TL-OUTD-S-US-Z-A [240V] | 3.0 kW, 240 Vac Utility Interactive Inverter with arc detector | 3 | 240 | 96.5 | Y | N |  | 0.15 | 3 | 0.15 | 180 | 400 | 480 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 93.094 | 95.4386 | 95.8649 | 95.9573 | 95.8111 | 95.4222 | 95.7015 | 94.5916 | 96.6224 | 97.087 | 97.3297 | 97.3224 | 97.1876 | 97.1447 | 93.754 | 96.232 | 96.804 | 97.1551 | 97.1447 | 97.1026 | 96.9226
ABB | UNO-3.0-TL-OUTD-S-US-Z-A [277V] | 3.0 kW, 277 Vac Utility Interactive Inverter with arc detector | 3 | 277 | 96.5 | Y | N |  | 0.2 | 3 | 0.2 | 180 | 400 | 480 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 92.4542 | 95.1981 | 95.7797 | 95.9716 | 95.9228 | 95.6371 | 95.7266 | 93.7103 | 96.2189 | 96.8155 | 97.1633 | 97.2311 | 97.1831 | 96.9732 | 93.9658 | 96.4497 | 97.0595 | 97.4757 | 97.5241 | 97.5271 | 97.2623
ABB | UNO-3.0-TL-OUTD-S-US-Z-M-A [208V] | 3.0 kW, 208 Vac Utility Interactive Inverter with arc detector and revenue grade meter | 3 | 208 | 96.5 | Y | N |  | 0.11 | 3 | 0.11 | 180 | 400 | 480 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 93.5877 | 95.5788 | 95.9532 | 95.9149 | 95.7186 | 95.1981 | 95.6697 | 94.4062 | 96.4712 | 96.8978 | 97.0529 | 97.019 | 96.7605 | 96.8667 | 93.6377 | 96.0982 | 96.6144 | 96.8857 | 96.8551 | 96.6678 | 96.6567
ABB | UNO-3.0-TL-OUTD-S-US-Z-M-A [240V] | 3.0 kW, 240 Vac Utility Interactive Inverter with arc detector and revenue grade meter | 3 | 240 | 96.5 | Y | N |  | 0.15 | 3 | 0.15 | 180 | 400 | 480 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 93.094 | 95.4386 | 95.8649 | 95.9573 | 95.8111 | 95.4222 | 95.7015 | 94.5916 | 96.6224 | 97.087 | 97.3297 | 97.3224 | 97.1876 | 97.1447 | 93.754 | 96.232 | 96.804 | 97.1551 | 97.1447 | 97.1026 | 96.9226
ABB | UNO-3.0-TL-OUTD-S-US-Z-M-A [277V] | 3.0 kW, 277 Vac Utility Interactive Inverter with arc detector and revenue grade meter | 3 | 277 | 96.5 | Y | N |  | 0.2 | 3 | 0.2 | 180 | 400 | 480 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 92.4542 | 95.1981 | 95.7797 | 95.9716 | 95.9228 | 95.6371 | 95.7266 | 93.7103 | 96.2189 | 96.8155 | 97.1633 | 97.2311 | 97.1831 | 96.9732 | 93.9658 | 96.4497 | 97.0595 | 97.4757 | 97.5241 | 97.5271 | 97.2623
ABB | PVI-3.8-I-OUTD-x-US-y-Z [208V] | 3.8 kW, 208 Vac Inverter, where x may include S and y = PG or NG | 3.3 | 208 | 96 | Y | N |  | 0.1 | 3.3 | 0.1 | 100 | 310 | 416 | 0.33 | 0.66 | 0.99 | 1.65 | 2.475 | 3.3 | 93.6 | 95.7 | 96.2 | 96.4 | 96.3 | 96 | 96.2 | 92.5 | 95.6 | 96.3 | 96.6 | 96.7 | 96.5 | 96.4 | 89.5 | 94 | 95.3 | 96.1 | 96.3 | 96.1 | 95.7
ABB | PVI-3.6-OUTD-S-US [208V] | 3.6 kW, 208 Vac Utility Interactive Inverter | 3.6 | 208 | 96 | Y | N | Multiple Listing of Power-One | 0.1 | 3.6 | 0.1 | 100 | 310 | 480 | 0.36 | 0.72 | 1.08 | 1.8 | 2.7 | 3.6 | 92.2 | 94.7 | 95.4 | 95.9 | 95.9 | 95.6 | 95.6 | 92.7 | 95.5 | 96.1 | 96.4 | 96.4 | 96.1 | 96.1 | 90.3 | 94.5 | 95.3 | 95.9 | 96 | 95.7 | 95.6
ABB | PVI-3.6-OUTD-S-US [240V] | 3.6 kW, 240 Vac Utility Interactive Inverter | 3.6 | 240 | 96 | Y | N | Multiple Listing of Power-One | 0.2 | 3.6 | 0.2 | 100 | 340 | 480 | 0.3 | 0.72 | 1.08 | 1.8 | 2.7 | 3.6 | 91.1 | 94.1 | 94.9 | 95.6 | 95.8 | 95.7 | 95.4 | 92.4 | 95.5 | 96.3 | 96.7 | 96.7 | 96.6 | 96.5 | 90.2 | 94.6 | 95.6 | 96.2 | 96.4 | 96.3 | 95.9
ABB | PVI-3.6-OUTD-S-US [277V] | 3.6 kW, 277 Vac Utility Interactive Inverter | 3.6 | 277 | 96 | Y | N | Multiple Listing of Power-One | 0.2 | 3.6 | 0.2 | 100 | 395 | 480 | 0.36 | 0.72 | 1.08 | 1.8 | 2.7 | 3.6 | 90 | 93.4 | 94.4 | 95.4 | 95.7 | 95.6 | 95.1 | 91.9 | 95.4 | 96.3 | 96.9 | 97 | 96.9 | 96.6 | 90.4 | 94.9 | 95.9 | 96.6 | 96.8 | 96.8 | 96.3
ABB | PVI-3.6-OUTD-S-US-A [208V] | 3.6 kW, 208 Vac Utility Interactive Inverter with arc detector | 3.6 | 208 | 96 | Y | N | Multiple Listing of Power-One | 0.1 | 3.6 | 0.1 | 100 | 310 | 480 | 0.36 | 0.72 | 1.08 | 1.8 | 2.7 | 3.6 | 92.2 | 94.7 | 95.4 | 95.9 | 95.9 | 95.6 | 95.6 | 92.7 | 95.5 | 96.1 | 96.4 | 96.4 | 96.1 | 96.1 | 90.3 | 94.5 | 95.3 | 95.9 | 96 | 95.7 | 95.6 | 2017-07-01 | 2018-10-15
ABB | PVI-3.6-OUTD-S-US-A [240V] | 3.6 kW, 240 Vac Utility Interactive Inverter with arc detector | 3.6 | 240 | 96 | Y | N | Multiple Listing of Power-One | 0.2 | 3.6 | 0.2 | 100 | 340 | 480 | 0.3 | 0.72 | 1.08 | 1.8 | 2.7 | 3.6 | 91.1 | 94.1 | 94.9 | 95.6 | 95.8 | 95.7 | 95.4 | 92.4 | 95.5 | 96.3 | 96.7 | 96.7 | 96.6 | 96.5 | 90.2 | 94.6 | 95.6 | 96.2 | 96.4 | 96.3 | 95.9 | 2017-07-01 | 2018-10-15
ABB | PVI-3.6-OUTD-S-US-A [277V] | 3.6 kW, 277 Vac Utility Interactive Inverter with arc detector | 3.6 | 277 | 96 | Y | N | Multiple Listing of Power-One | 0.2 | 3.6 | 0.2 | 100 | 395 | 480 | 0.36 | 0.72 | 1.08 | 1.8 | 2.7 | 3.6 | 90 | 93.4 | 94.4 | 95.4 | 95.7 | 95.6 | 95.1 | 91.9 | 95.4 | 96.3 | 96.9 | 97 | 96.9 | 96.6 | 90.4 | 94.9 | 95.9 | 96.6 | 96.8 | 96.8 | 96.3 | 2017-07-01 | 2018-10-15
ABB | PVI-3.6-OUTD-S-US-Z [208V] | 3.6 kW, 208 Vac Utility Interactive Inverter | 3.6 | 208 | 96 | Y | N |  | 0.1 | 3.6 | 0.1 | 100 | 310 | 480 | 0.36 | 0.72 | 1.08 | 1.8 | 2.7 | 3.6 | 92.2 | 94.7 | 95.4 | 95.9 | 95.9 | 95.6 | 95.6 | 92.7 | 95.5 | 96.1 | 96.4 | 96.4 | 96.1 | 96.1 | 90.3 | 94.5 | 95.3 | 95.9 | 96 | 95.7 | 95.6
ABB | PVI-3.6-OUTD-S-US-Z [240V] | 3.6 kW, 240 Vac Utility Interactive Inverter | 3.6 | 240 | 96 | Y | N |  | 0.2 | 3.6 | 0.2 | 100 | 340 | 480 | 0.3 | 0.72 | 1.08 | 1.8 | 2.7 | 3.6 | 91.1 | 94.1 | 94.9 | 95.6 | 95.8 | 95.7 | 95.4 | 92.4 | 95.5 | 96.3 | 96.7 | 96.7 | 96.6 | 96.5 | 90.2 | 94.6 | 95.6 | 96.2 | 96.4 | 96.3 | 95.9
ABB | PVI-3.6-OUTD-S-US-Z [277V] | 3.6 kW, 277 Vac Utility Interactive Inverter | 3.6 | 277 | 96 | Y | N |  | 0.2 | 3.6 | 0.2 | 100 | 395 | 480 | 0.36 | 0.72 | 1.08 | 1.8 | 2.7 | 3.6 | 90 | 93.4 | 94.4 | 95.4 | 95.7 | 95.6 | 95.1 | 91.9 | 95.4 | 96.3 | 96.9 | 97 | 96.9 | 96.6 | 90.4 | 94.9 | 95.9 | 96.6 | 96.8 | 96.8 | 96.3
ABB | PVI-3.6-OUTD-S-US-Z-A [208V] | 3.6 kW, 208 Vac Utility Interactive Inverter with arc detector | 3.6 | 208 | 96 | Y | N | Multiple Listing of Power-One | 0.1 | 3.6 | 0.1 | 100 | 310 | 480 | 0.36 | 0.72 | 1.08 | 1.8 | 2.7 | 3.6 | 92.2 | 94.7 | 95.4 | 95.9 | 95.9 | 95.6 | 95.6 | 92.7 | 95.5 | 96.1 | 96.4 | 96.4 | 96.1 | 96.1 | 90.3 | 94.5 | 95.3 | 95.9 | 96 | 95.7 | 95.6 | 2017-07-01 | 2018-10-15
ABB | PVI-3.6-OUTD-S-US-Z-A [240V] | 3.6 kW, 240 Vac Utility Interactive Inverter with arc detector | 3.6 | 240 | 96 | Y | N | Multiple Listing of Power-One | 0.2 | 3.6 | 0.2 | 100 | 340 | 480 | 0.3 | 0.72 | 1.08 | 1.8 | 2.7 | 3.6 | 91.1 | 94.1 | 94.9 | 95.6 | 95.8 | 95.7 | 95.4 | 92.4 | 95.5 | 96.3 | 96.7 | 96.7 | 96.6 | 96.5 | 90.2 | 94.6 | 95.6 | 96.2 | 96.4 | 96.3 | 95.9 | 2017-07-01 | 2018-10-15
ABB | PVI-3.6-OUTD-S-US-Z-A [277V] | 3.6 kW, 277 Vac Utility Interactive Inverter with arc detector | 3.6 | 277 | 96 | Y | N | Multiple Listing of Power-One | 0.2 | 3.6 | 0.2 | 100 | 395 | 480 | 0.36 | 0.72 | 1.08 | 1.8 | 2.7 | 3.6 | 90 | 93.4 | 94.4 | 95.4 | 95.7 | 95.6 | 95.1 | 91.9 | 95.4 | 96.3 | 96.9 | 97 | 96.9 | 96.6 | 90.4 | 94.9 | 95.9 | 96.6 | 96.8 | 96.8 | 96.3 | 2017-07-01 | 2018-10-15
ABB | PVI-3.6-OUTD-S-US-Z-M-A [208V] | 3.6 kW, 208 Vac Utility Interactive Inverter with arc-fault detection and meter | 3.6 | 208 | 96 | Y | N | Multiple Listing of Power-One | 0.1 |  |  | 100 | 310 | 480 | 0.36 | 0.72 | 1.08 | 1.8 | 2.7 | 3.6 | 92.2 | 94.7 | 95.4 | 95.9 | 95.9 | 95.6 | 95.6 | 92.7 | 95.5 | 96.1 | 96.4 | 96.4 | 96.1 | 96.1 | 90.3 | 94.5 | 95.3 | 95.9 | 96 | 95.7 | 95.6 | 2017-07-01 | 2018-10-15
ABB | PVI-3.6-OUTD-S-US-Z-M-A [240V] | 3.6 kW, 240 Vac Utility Interactive Inverter with arc-fault detection and meter | 3.6 | 240 | 96 | Y | N | Multiple Listing of Power-One | 0.2 |  |  | 100 | 340 | 480 | 0.3 | 0.72 | 1.08 | 1.8 | 2.7 | 3.6 | 91.1 | 94.1 | 94.9 | 95.6 | 95.8 | 95.7 | 95.4 | 92.4 | 95.5 | 96.3 | 96.7 | 96.7 | 96.6 | 96.5 | 90.2 | 94.6 | 95.6 | 96.2 | 96.4 | 96.3 | 95.9 | 2017-07-01 | 2018-10-15
ABB | PVI-3.6-OUTD-S-US-Z-M-A [277V] | 3.6 kW, 277 Vac Utility Interactive Inverter with arc-fault detection and meter | 3.6 | 277 | 96 | Y | N | Multiple Listing of Power-One | 0.2 |  |  | 100 | 395 | 480 | 0.36 | 0.72 | 1.08 | 1.8 | 2.7 | 3.6 | 90 | 93.4 | 94.4 | 95.4 | 95.7 | 95.6 | 95.1 | 91.9 | 95.4 | 96.3 | 96.9 | 97 | 96.9 | 96.6 | 90.4 | 94.9 | 95.9 | 96.6 | 96.8 | 96.8 | 96.3 | 2017-07-01 | 2018-10-15
ABB | PVI-3.6-OUTD-US [208V] | 3.6 kW, 208 Vac Utility Interactive Inverter, model # may include -S- or -W | 3.6 | 208 | 96 | Y | N | Multiple Listing of Power-One | 0.1 | 3.6 | 0.1 | 100 | 310 | 480 | 0.36 | 0.72 | 1.08 | 1.8 | 2.7 | 3.6 | 92.2 | 94.7 | 95.4 | 95.9 | 95.9 | 95.6 | 95.6 | 92.7 | 95.5 | 96.1 | 96.4 | 96.4 | 96.1 | 96.1 | 90.3 | 94.5 | 95.3 | 95.9 | 96 | 95.7 | 95.6
ABB | PVI-3.6-OUTD-US [240V] | 3.6 kW, 240 Vac Utility Interactive Inverter, model # may include -S- or -W | 3.6 | 240 | 96 | Y | N | Multiple Listing of Power-One | 0.2 | 3.6 | 0.2 | 100 | 340 | 480 | 0.3 | 0.72 | 1.08 | 1.8 | 2.7 | 3.6 | 91.1 | 94.1 | 94.9 | 95.6 | 95.8 | 95.7 | 95.4 | 92.4 | 95.5 | 96.3 | 96.7 | 96.7 | 96.6 | 96.5 | 90.2 | 94.6 | 95.6 | 96.2 | 96.4 | 96.3 | 95.9
ABB | PVI-3.6-OUTD-US [277V] | 3.6 kW, 277 Vac Utility Interactive Inverter, model # may include -S- or -W | 3.6 | 277 | 96 | Y | N | Multiple Listing of Power-One | 0.2 | 3.6 | 0.2 | 100 | 395 | 480 | 0.36 | 0.72 | 1.08 | 1.8 | 2.7 | 3.6 | 90 | 93.4 | 94.4 | 95.4 | 95.7 | 95.6 | 95.1 | 91.9 | 95.4 | 96.3 | 96.9 | 97 | 96.9 | 96.6 | 90.4 | 94.9 | 95.9 | 96.6 | 96.8 | 96.8 | 96.3
ABB | PVI-3.8-I-OUTD-x-US-y-Z [240V] | 3.8 kW, 240 Vac Inverter, where x may include S and y = PG or NG | 3.8 | 240 | 96.5 | Y | N |  | 0.1 | 3.8 | 0.1 | 100 | 340 | 416 | 0.38 | 0.76 | 1.14 | 1.9 | 2.85 | 3.8 | 93.7 | 95.8 | 96.2 | 96.5 | 96.4 | 96.1 | 96.3 | 92.8 | 95.9 | 96.6 | 96.9 | 96.8 | 96.8 | 96.6 | 90.7 | 94.8 | 95.9 | 96.5 | 96.5 | 96.5 | 96.1
ABB | PVI-3.8-I-OUTD-x-US-y-Z [277V] | 3.8 kW, 277 Vac Inverter, where x may include S and y = PG or NG | 3.8 | 277 | 96.5 | Y | N |  | 0.1 | 3.8 | 0.1 | 100 | 362 | 416 | 0.38 | 0.76 | 1.14 | 1.9 | 2.85 | 3.8 | 92.9 | 95.4 | 96 | 96.3 | 96.4 | 96.1 | 96.1 | 92.3 | 95.6 | 96.4 | 96.9 | 96.9 | 96.9 | 96.6 | 91.3 | 95.2 | 96.2 | 96.8 | 96.8 | 96.9 | 96.4
ABB | PVI-3.8-OUTD-S-US [208V] | 3.3 kW, 208 Vac Utility Interactive Inverter with arc detector | 3.8 | 208 | 95.5 | Y | N | Multiple Listing of Power-One | 0.12 |  |  | 100 | 310 | 480 | 0.33 | 0.66 | 0.99 | 1.65 | 2.48 | 3.3 | 91.5 | 94.3 | 95.1 | 95.6 | 95.6 | 95.4 | 95.3 | 92.1 | 95.1 | 95.9 | 96.3 | 96.4 | 96.2 | 96.1 | 89.1 | 93.9 | 95 | 95.7 | 95.9 | 95.8 | 95.4
ABB | PVI-3.8-OUTD-S-US [240V] | 3.8 kW, 240 Vac Utility Interactive Inverter with arc detector | 3.8 | 240 | 96 | Y | N | Multiple Listing of Power-One | 0.16 |  |  | 100 | 340 | 480 | 0.38 | 0.76 | 1.14 | 1.9 | 2.85 | 3.8 | 91.4 | 94.2 | 94.9 | 95.5 | 95.6 | 95.5 | 95.3 | 92.6 | 95.5 | 96.2 | 96.6 | 96.7 | 96.6 | 96.4 | 90.3 | 94.5 | 95.5 | 96.2 | 96.3 | 96.3 | 95.9
ABB | PVI-3.8-OUTD-S-US [277V] | 3.8 kW, 277 Vac Utility Interactive Inverter with arc detector | 3.8 | 277 | 96 | Y | N | Multiple Listing of Power-One | 0.22 |  |  | 100 | 395 | 480 | 0.38 | 0.76 | 1.14 | 1.9 | 2.85 | 3.8 | 90.3 | 93.6 | 94.5 | 95.3 | 95.6 | 95.5 | 95.1 | 92 | 95.3 | 96.2 | 96.8 | 96.9 | 96.9 | 96.5 | 90.4 | 94.7 | 95.8 | 96.5 | 96.7 | 96.8 | 96.2
ABB | PVI-3.8-OUTD-S-US-A [208V] | 3.3 kW, 208 Vac Utility Interactive Inverter with arc detector | 3.8 | 208 | 95.5 | Y | N | Multiple Listing of Power-One | 0.12 |  |  | 100 | 310 | 480 | 0.33 | 0.66 | 0.99 | 1.65 | 2.48 | 3.3 | 91.5 | 94.3 | 95.1 | 95.6 | 95.6 | 95.4 | 95.3 | 92.1 | 95.1 | 95.9 | 96.3 | 96.4 | 96.2 | 96.1 | 89.1 | 93.9 | 95 | 95.7 | 95.9 | 95.8 | 95.4 | 2017-07-01 | 2018-10-15
ABB | PVI-3.8-OUTD-S-US-A [240V] | 3.8 kW, 240 Vac Utility Interactive Inverter with arc detector | 3.8 | 240 | 96 | Y | N | Multiple Listing of Power-One | 0.16 |  |  | 100 | 340 | 480 | 0.38 | 0.76 | 1.14 | 1.9 | 2.85 | 3.8 | 91.4 | 94.2 | 94.9 | 95.5 | 95.6 | 95.5 | 95.3 | 92.6 | 95.5 | 96.2 | 96.6 | 96.7 | 96.6 | 96.4 | 90.3 | 94.5 | 95.5 | 96.2 | 96.3 | 96.3 | 95.9 | 2017-07-01 | 2018-10-15
ABB | PVI-3.8-OUTD-S-US-A [277V] | 3.8 kW, 277 Vac Utility Interactive Inverter with arc detector | 3.8 | 277 | 96 | Y | N | Multiple Listing of Power-One | 0.22 |  |  | 100 | 395 | 480 | 0.38 | 0.76 | 1.14 | 1.9 | 2.85 | 3.8 | 90.3 | 93.6 | 94.5 | 95.3 | 95.6 | 95.5 | 95.1 | 92 | 95.3 | 96.2 | 96.8 | 96.9 | 96.9 | 96.5 | 90.4 | 94.7 | 95.8 | 96.5 | 96.7 | 96.8 | 96.2 | 2017-07-01 | 2018-10-15
ABB | PVI-3.8-OUTD-S-US-Z [208V] | 3.3 kW, 208 Vac Utility Interactive Inverter | 3.8 | 208 | 95.5 | Y | N | Multiple Listing of Power-One | 0.12 |  |  | 100 | 310 | 480 | 0.33 | 0.66 | 0.99 | 1.65 | 2.48 | 3.3 | 91.5 | 94.3 | 95.1 | 95.6 | 95.6 | 95.4 | 95.3 | 92.1 | 95.1 | 95.9 | 96.3 | 96.4 | 96.2 | 96.1 | 89.1 | 93.9 | 95 | 95.7 | 95.9 | 95.8 | 95.4
ABB | PVI-3.8-OUTD-S-US-Z [240V] | 3.3 kW, 208 Vac Utility Interactive Inverter | 3.8 | 240 | 96 | Y | N | Multiple Listing of Power-One | 0.16 |  |  | 100 | 340 | 480 | 0.38 | 0.76 | 1.14 | 1.9 | 2.85 | 3.8 | 91.4 | 94.2 | 94.9 | 95.5 | 95.6 | 95.5 | 95.3 | 92.6 | 95.5 | 96.2 | 96.6 | 96.7 | 96.6 | 96.4 | 90.3 | 94.5 | 95.5 | 96.2 | 96.3 | 96.3 | 95.9
ABB | PVI-3.8-OUTD-S-US-Z [277V] | 3.3 kW, 208 Vac Utility Interactive Inverter | 3.8 | 277 | 96 | Y | N | Multiple Listing of Power-One | 0.22 |  |  | 100 | 395 | 480 | 0.38 | 0.76 | 1.14 | 1.9 | 2.85 | 3.8 | 90.3 | 93.6 | 94.5 | 95.3 | 95.6 | 95.5 | 95.1 | 92 | 95.3 | 96.2 | 96.8 | 96.9 | 96.9 | 96.5 | 90.4 | 94.7 | 95.8 | 96.5 | 96.7 | 96.8 | 96.2
ABB | PVI-3.8-OUTD-S-US-Z-A [208V] | 3.3 kW, 208 Vac Utility Interactive Inverter with arc detector | 3.8 | 208 | 95.5 | Y | N | Multiple Listing of Power-One | 0.12 |  |  | 100 | 310 | 480 | 0.33 | 0.66 | 0.99 | 1.65 | 2.48 | 3.3 | 91.5 | 94.3 | 95.1 | 95.6 | 95.6 | 95.4 | 95.3 | 92.1 | 95.1 | 95.9 | 96.3 | 96.4 | 96.2 | 96.1 | 89.1 | 93.9 | 95 | 95.7 | 95.9 | 95.8 | 95.4 | 2017-07-01 | 2018-10-15
ABB | PVI-3.8-OUTD-S-US-Z-A [240V] | 3.8 kW, 240 Vac Utility Interactive Inverter with arc detector | 3.8 | 240 | 96 | Y | N | Multiple Listing of Power-One | 0.16 |  |  | 100 | 340 | 480 | 0.38 | 0.76 | 1.14 | 1.9 | 2.85 | 3.8 | 91.4 | 94.2 | 94.9 | 95.5 | 95.6 | 95.5 | 95.3 | 92.6 | 95.5 | 96.2 | 96.6 | 96.7 | 96.6 | 96.4 | 90.3 | 94.5 | 95.5 | 96.2 | 96.3 | 96.3 | 95.9 | 2017-07-01 | 2018-10-15
ABB | PVI-3.8-OUTD-S-US-Z-A [277V] | 3.8 kW, 277 Vac Utility Interactive Inverter with arc detector | 3.8 | 277 | 96 | Y | N | Multiple Listing of Power-One | 0.22 |  |  | 100 | 395 | 480 | 0.38 | 0.76 | 1.14 | 1.9 | 2.85 | 3.8 | 90.3 | 93.6 | 94.5 | 95.3 | 95.6 | 95.5 | 95.1 | 92 | 95.3 | 96.2 | 96.8 | 96.9 | 96.9 | 96.5 | 90.4 | 94.7 | 95.8 | 96.5 | 96.7 | 96.8 | 96.2 | 2017-07-01 | 2018-10-15
ABB | PVI-3.8-OUTD-S-US-Z-M-A [208V] | 3.3 kW, 208 Vac Utility Interactive Inverter with arc-fault detection and meter | 3.8 | 208 | 95.5 | Y | N | Multiple Listing of Power-One | 0.12 |  |  | 100 | 310 | 480 | 0.33 | 0.66 | 0.99 | 1.65 | 2.48 | 3.3 | 91.5 | 94.3 | 95.1 | 95.6 | 95.6 | 95.4 | 95.3 | 92.1 | 95.1 | 95.9 | 96.3 | 96.4 | 96.2 | 96.1 | 89.1 | 93.9 | 95 | 95.7 | 95.9 | 95.8 | 95.4 | 2017-07-01 | 2018-10-15
ABB | PVI-3.8-OUTD-S-US-Z-M-A [240V] | 3.8 kW, 240 Vac Utility Interactive Inverter with arc-fault detection and meter | 3.8 | 240 | 96 | Y | N | Multiple Listing of Power-One | 0.16 |  |  | 100 | 340 | 480 | 0.38 | 0.76 | 1.14 | 1.9 | 2.85 | 3.8 | 91.4 | 94.2 | 94.9 | 95.5 | 95.6 | 95.5 | 95.3 | 92.6 | 95.5 | 96.2 | 96.6 | 96.7 | 96.6 | 96.4 | 90.3 | 94.5 | 95.5 | 96.2 | 96.3 | 96.3 | 95.9 | 2017-07-01 | 2018-10-15
ABB | PVI-3.8-OUTD-S-US-Z-M-A [277V] | 3.8 kW, 277 Vac Utility Interactive Inverter with arc-fault detection and meter | 3.8 | 277 | 96 | Y | N | Multiple Listing of Power-One | 0.22 |  |  | 100 | 395 | 480 | 0.38 | 0.76 | 1.14 | 1.9 | 2.85 | 3.8 | 90.3 | 93.6 | 94.5 | 95.3 | 95.6 | 95.5 | 95.1 | 92 | 95.3 | 96.2 | 96.8 | 96.9 | 96.9 | 96.5 | 90.4 | 94.7 | 95.8 | 96.5 | 96.7 | 96.8 | 96.2 | 2017-07-01 | 2018-10-15
ABB | PVI-3.8-OUTD-US [208V] | 3.3 kW, 208 Vac Utility Interactive Inverter | 3.8 | 208 | 95.5 | Y | N | Multiple Listing of Power-One | 0.12 |  |  | 100 | 310 | 480 | 0.33 | 0.66 | 0.99 | 1.65 | 2.48 | 3.3 | 91.5 | 94.3 | 95.1 | 95.6 | 95.6 | 95.4 | 95.3 | 92.1 | 95.1 | 95.9 | 96.3 | 96.4 | 96.2 | 96.1 | 89.1 | 93.9 | 95 | 95.7 | 95.9 | 95.8 | 95.4
ABB | PVI-3.8-OUTD-US [240V] | 3.8 kW, 240 Vac Utility Interactive Inverter | 3.8 | 240 | 96 | Y | N | Multiple Listing of Power-One | 0.16 |  |  | 100 | 340 | 480 | 0.38 | 0.76 | 1.14 | 1.9 | 2.85 | 3.8 | 91.4 | 94.2 | 94.9 | 95.5 | 95.6 | 95.5 | 95.3 | 92.6 | 95.5 | 96.2 | 96.6 | 96.7 | 96.6 | 96.4 | 90.3 | 94.5 | 95.5 | 96.2 | 96.3 | 96.3 | 95.9
ABB | PVI-3.8-OUTD-US [277V] | 3.8 kW, 277 Vac Utility Interactive Inverter | 3.8 | 277 | 96 | Y | N | Multiple Listing of Power-One | 0.22 |  |  | 100 | 395 | 480 | 0.38 | 0.76 | 1.14 | 1.9 | 2.85 | 3.8 | 90.3 | 93.6 | 94.5 | 95.3 | 95.6 | 95.5 | 95.1 | 92 | 95.3 | 96.2 | 96.8 | 96.9 | 96.9 | 96.5 | 90.4 | 94.7 | 95.8 | 96.5 | 96.7 | 96.8 | 96.2
ABB | UNO-DM-3.8-TL-PLUS-US-SB-RA [240V] | 3.8 kW, 240 Vac Utility Interactive Inverter with arc detector, WLAN, and Rapid Shutdown power supply | 3.8 | 240 | 96.5 | Y | N |  | 1 | 3.8 | 1 | 200 | 355 | 480 | 0.38 | 0.76 | 1.14 | 1.9 | 2.85 | 3.8 | 92 | 95 | 95.7 | 95.9 | 96 | 95.8 | 95.7 | 93.7 | 96 | 96.6 | 96.9 | 97 | 96.8 | 96.7 | 91.7 | 95.2 | 96 | 96.6 | 96.7 | 96.5 | 96.3 | 2017-07-01 | 2018-10-15
ABB | UNO-DM-3.8-TL-PLUS-US-SE-RA [240V] | 3.8 kW, 240 Vac Utility Interactive Inverter with arc detector, Ethernet LAN, and Rapid Shutdown power supply | 3.8 | 240 | 96.5 | Y | N |  | 1 | 3.8 | 1 | 200 | 355 | 480 | 0.38 | 0.76 | 1.14 | 1.9 | 2.85 | 3.8 | 92 | 95 | 95.7 | 95.9 | 96 | 95.8 | 95.7 | 93.7 | 96 | 96.6 | 96.9 | 97 | 96.8 | 96.7 | 91.7 | 95.2 | 96 | 96.6 | 96.7 | 96.5 | 96.3 | 2017-07-01 | 2018-10-15
ABB | UNO-DM-3.8-TL-PLUS-US-SZM-RA [240V] | 3.8 kW, 240 Vac Interactive Utility Inverter with arc detector, revenue grade meter, Zigbee radio, and Rapid Shutdown power supply | 3.8 | 240 | 96.5 | Y | N | Multiple Listing of Power-One | 1 | 3.8 | 1 | 200 | 355 | 480 | 0.38 | 0.76 | 1.14 | 1.9 | 2.85 | 3.8 | 92 | 95 | 95.7 | 95.9 | 96 | 95.8 | 95.7 | 93.7 | 96 | 96.6 | 96.9 | 97 | 96.8 | 96.7 | 91.7 | 95.2 | 96 | 96.6 | 96.7 | 96.5 | 96.3 | 2017-07-01 | 2018-10-15
ABB | UNO-DM-3.8-TL-PLUS-US-SZ-RA [240V] | 3.8 kW, 240 Vac Utility Interactive Inverter with arc detector and Rapid Shutdown power supply | 3.8 | 240 | 96.5 | Y | N | Multiple Listing of Power-One | 1 | 3.8 | 1 | 200 | 355 | 480 | 0.38 | 0.76 | 1.14 | 1.9 | 2.85 | 3.8 | 92 | 95 | 95.7 | 95.9 | 96 | 95.8 | 95.7 | 93.7 | 96 | 96.6 | 96.9 | 97 | 96.8 | 96.7 | 91.7 | 95.2 | 96 | 96.6 | 96.7 | 96.5 | 96.3 | 2017-07-01 | 2018-10-15
ABB | PVI-4.2-OUTD-S-US [208V] | 4.2 kW, 208 Vac Utility Interactive Inverter (with Zigbee -Z) | 4.2 | 208 | 96 | Y | N | Multiple Listing of Power-One | 0.1 | 4.2 | 0.1 | 100 | 310 | 480 | 0.42 | 0.84 | 1.26 | 2.1 | 3.15 | 4.2 | 92.9 | 95 | 95.6 | 95.9 | 95.8 | 95.4 | 95.6 | 93.5 | 95.8 | 96.3 | 96.4 | 96.3 | 95.9 | 96.1 | 91.4 | 94.9 | 95.6 | 95.9 | 95.8 | 95.5 | 95.6
ABB | PVI-4.2-OUTD-S-US [240V] | 4.2 kW, 240 Vac Utility Interactive Inverter (with Zigbee -Z) | 4.2 | 240 | 96 | Y | N | Multiple Listing of Power-One | 0.2 | 4.2 | 0.2 | 100 | 340 | 480 | 0.42 | 0.84 | 1.26 | 2.1 | 3.15 | 4.2 | 91.8 | 94.4 | 95.2 | 95.8 | 95.8 | 95.4 | 95.5 | 93.3 | 95.9 | 96.5 | 96.7 | 96.7 | 96.5 | 96.5 | 91.3 | 95.1 | 95.9 | 96.3 | 96.4 | 96.2 | 96
ABB | PVI-4.2-OUTD-S-US [277V] | 4.2 kW, 277 Vac Utility Interactive Inverter (with Zigbee -Z) | 4.2 | 277 | 96 | Y | N | Multiple Listing of Power-One | 0.2 | 4.2 | 0.2 | 100 | 395 | 480 | 0.42 | 0.84 | 1.26 | 2.1 | 3.15 | 4.2 | 90.8 | 93.9 | 94.8 | 95.6 | 95.7 | 95.6 | 95.3 | 92.8 | 95.8 | 96.6 | 97 | 97 | 96.9 | 96.7 | 91.6 | 95.4 | 96.2 | 96.7 | 96.8 | 96.7 | 96.4
ABB | PVI-4.2-OUTD-S-US-A [208V] | 4.2 kW, 208 Vac Utility Interactive Inverter with arc detector | 4.2 | 208 | 96 | Y | N | Multiple Listing of Power-One | 0.1 | 4.2 | 0.1 | 100 | 310 | 480 | 0.42 | 0.84 | 1.26 | 2.1 | 3.15 | 4.2 | 92.9 | 95 | 95.6 | 95.9 | 95.8 | 95.4 | 95.6 | 93.5 | 95.8 | 96.3 | 96.4 | 96.3 | 95.9 | 96.1 | 91.4 | 94.9 | 95.6 | 95.9 | 95.8 | 95.5 | 95.6 | 2017-07-01 | 2018-10-15
ABB | PVI-4.2-OUTD-S-US-A [240V] | 4.2 kW, 240 Vac Utility Interactive Inverter with arc detector | 4.2 | 240 | 96 | Y | N | Multiple Listing of Power-One | 0.2 | 4.2 | 0.2 | 100 | 340 | 480 | 0.42 | 0.84 | 1.26 | 2.1 | 3.15 | 4.2 | 91.8 | 94.4 | 95.2 | 95.8 | 95.8 | 95.4 | 95.5 | 93.3 | 95.9 | 96.5 | 96.7 | 96.7 | 96.5 | 96.5 | 91.3 | 95.1 | 95.9 | 96.3 | 96.4 | 96.2 | 96 | 2017-07-01 | 2018-10-15
ABB | PVI-4.2-OUTD-S-US-A [277V] | 4.2 kW, 277 Vac Utility Interactive Inverter with arc detector | 4.2 | 277 | 96 | Y | N | Multiple Listing of Power-One | 0.2 | 4.2 | 0.2 | 100 | 395 | 480 | 0.42 | 0.84 | 1.26 | 2.1 | 3.15 | 4.2 | 90.8 | 93.9 | 94.8 | 95.6 | 95.7 | 95.6 | 95.3 | 92.8 | 95.8 | 96.6 | 97 | 97 | 96.9 | 96.7 | 91.6 | 95.4 | 96.2 | 96.7 | 96.8 | 96.7 | 96.4 | 2017-07-01 | 2018-10-15
ABB | PVI-4.2-OUTD-S-US-Z [208V] | 4.2 kW, 208 Vac Utility Interactive Inverter | 4.2 | 208 | 96 | Y | N |  | 0.1 | 4.2 | 0.1 | 100 | 310 | 480 | 0.42 | 0.84 | 1.26 | 2.1 | 3.15 | 4.2 | 92.9 | 95 | 95.6 | 95.9 | 95.8 | 95.4 | 95.6 | 93.5 | 95.8 | 96.3 | 96.4 | 96.3 | 95.9 | 96.1 | 91.4 | 94.9 | 95.6 | 95.9 | 95.8 | 95.5 | 95.6
ABB | PVI-4.2-OUTD-S-US-Z [240V] | 4.2 kW, 240 Vac Utility Interactive Inverter | 4.2 | 240 | 96 | Y | N |  | 0.2 | 4.2 | 0.2 | 100 | 340 | 480 | 0.42 | 0.84 | 1.26 | 2.1 | 3.15 | 4.2 | 91.8 | 94.4 | 95.2 | 95.8 | 95.8 | 95.4 | 95.5 | 93.3 | 95.9 | 96.5 | 96.7 | 96.7 | 96.5 | 96.5 | 91.3 | 95.1 | 95.9 | 96.3 | 96.4 | 96.2 | 96
ABB | PVI-4.2-OUTD-S-US-Z [277V] | 4.2 kW, 277 Vac Utility Interactive Inverter | 4.2 | 277 | 96 | Y | N |  | 0.2 | 4.2 | 0.2 | 100 | 395 | 480 | 0.42 | 0.84 | 1.26 | 2.1 | 3.15 | 4.2 | 90.8 | 93.9 | 94.8 | 95.6 | 95.7 | 95.6 | 95.3 | 92.8 | 95.8 | 96.6 | 97 | 97 | 96.9 | 96.7 | 91.6 | 95.4 | 96.2 | 96.7 | 96.8 | 96.7 | 96.4
ABB | PVI-4.2-OUTD-S-US-Z-A [208V] | 4.2 kW, 208 Vac Utility Interactive Inverter with arc detector | 4.2 | 208 | 96 | Y | N | Multiple Listing of Power-One | 0.1 | 4.2 | 0.1 | 100 | 310 | 480 | 0.42 | 0.84 | 1.26 | 2.1 | 3.15 | 4.2 | 92.9 | 95 | 95.6 | 95.9 | 95.8 | 95.4 | 95.6 | 93.5 | 95.8 | 96.3 | 96.4 | 96.3 | 95.9 | 96.1 | 91.4 | 94.9 | 95.6 | 95.9 | 95.8 | 95.5 | 95.6 | 2017-07-01 | 2018-10-15
ABB | PVI-4.2-OUTD-S-US-Z-A [240V] | 4.2 kW, 240 Vac Utility Interactive Inverter with arc detector | 4.2 | 240 | 96 | Y | N | Multiple Listing of Power-One | 0.2 | 4.2 | 0.2 | 100 | 340 | 480 | 0.42 | 0.84 | 1.26 | 2.1 | 3.15 | 4.2 | 91.8 | 94.4 | 95.2 | 95.8 | 95.8 | 95.4 | 95.5 | 93.3 | 95.9 | 96.5 | 96.7 | 96.7 | 96.5 | 96.5 | 91.3 | 95.1 | 95.9 | 96.3 | 96.4 | 96.2 | 96 | 2017-07-01 | 2018-10-15
ABB | PVI-4.2-OUTD-S-US-Z-A [277V] | 4.2 kW, 277 Vac Utility Interactive Inverter with arc detector | 4.2 | 277 | 96 | Y | N | Multiple Listing of Power-One | 0.2 | 4.2 | 0.2 | 100 | 395 | 480 | 0.42 | 0.84 | 1.26 | 2.1 | 3.15 | 4.2 | 90.8 | 93.9 | 94.8 | 95.6 | 95.7 | 95.6 | 95.3 | 92.8 | 95.8 | 96.6 | 97 | 97 | 96.9 | 96.7 | 91.6 | 95.4 | 96.2 | 96.7 | 96.8 | 96.7 | 96.4 | 2017-07-01 | 2018-10-15
ABB | PVI-4.2-OUTD-S-US-Z-M-A [208V] | 4.2 kW, 208 Vac Utility Interactive Inverter with arc-fault detection and meter | 4.2 | 208 | 96 | Y | N | Multiple Listing of Power-One | 0.1 |  |  | 100 | 310 | 480 | 0.42 | 0.84 | 1.26 | 2.1 | 3.15 | 4.2 | 92.9 | 95 | 95.6 | 95.9 | 95.8 | 95.4 | 95.6 | 93.5 | 95.8 | 96.3 | 96.4 | 96.3 | 95.9 | 96.1 | 91.4 | 94.9 | 95.6 | 95.9 | 95.8 | 95.5 | 95.6 | 2017-07-01 | 2018-10-15
ABB | PVI-4.2-OUTD-S-US-Z-M-A [240V] | 4.2 kW, 240 Vac Utility Interactive Inverter with arc-fault detection and meter | 4.2 | 240 | 96 | Y | N | Multiple Listing of Power-One | 0.2 |  |  | 100 | 340 | 480 | 0.42 | 0.84 | 1.26 | 2.1 | 3.15 | 4.2 | 91.8 | 94.4 | 95.2 | 95.8 | 95.8 | 95.4 | 95.5 | 93.3 | 95.9 | 96.5 | 96.7 | 96.7 | 96.5 | 96.5 | 91.3 | 95.1 | 95.9 | 96.3 | 96.4 | 96.2 | 96 | 2017-07-01 | 2018-10-15
ABB | PVI-4.2-OUTD-S-US-Z-M-A [277V] | 4.2 kW, 277 Vac Utility Interactive Inverter with arc-fault detection and meter | 4.2 | 277 | 96 | Y | N | Multiple Listing of Power-One | 0.2 |  |  | 100 | 395 | 480 | 0.42 | 0.84 | 1.26 | 2.1 | 3.15 | 4.2 | 90.8 | 93.9 | 94.8 | 95.6 | 95.7 | 95.6 | 95.3 | 92.8 | 95.8 | 96.6 | 97 | 97 | 96.9 | 96.7 | 91.6 | 95.4 | 96.2 | 96.7 | 96.8 | 96.7 | 96.4 | 2017-07-01 | 2018-10-15
ABB | PVI-4.2-OUTD-US [208V] | 4.2 kW, 208 Vac Utility Interactive Inverter. Model number may include -S- or -W | 4.2 | 208 | 96 | Y | N | Multiple Listing of Power-One | 0.1 | 4.2 | 0.1 | 100 | 310 | 480 | 0.42 | 0.84 | 1.26 | 2.1 | 3.15 | 4.2 | 92.9 | 95 | 95.6 | 95.9 | 95.8 | 95.4 | 95.6 | 93.5 | 95.8 | 96.3 | 96.4 | 96.3 | 95.9 | 96.1 | 91.4 | 94.9 | 95.6 | 95.9 | 95.8 | 95.5 | 95.6
ABB | PVI-4.2-OUTD-US [240V] | 4.2 kW, 240 Vac Utility Interactive Inverter. Model number may include -S- or -W | 4.2 | 240 | 96 | Y | N | Multiple Listing of Power-One | 0.2 | 4.2 | 0.2 | 100 | 340 | 480 | 0.42 | 0.84 | 1.26 | 2.1 | 3.15 | 4.2 | 91.8 | 94.4 | 95.2 | 95.8 | 95.8 | 95.4 | 95.5 | 93.3 | 95.9 | 96.5 | 96.7 | 96.7 | 96.5 | 96.5 | 91.3 | 95.1 | 95.9 | 96.3 | 96.4 | 96.2 | 96
ABB | PVI-4.2-OUTD-US [277V] | 4.2 kW, 277 Vac Utility Interactive Inverter. Model number may include -S- or -W | 4.2 | 277 | 96 | Y | N | Multiple Listing of Power-One | 0.2 | 4.2 | 0.2 | 100 | 395 | 480 | 0.42 | 0.84 | 1.26 | 2.1 | 3.15 | 4.2 | 90.8 | 93.9 | 94.8 | 95.6 | 95.7 | 95.6 | 95.3 | 92.8 | 95.8 | 96.6 | 97 | 97 | 96.9 | 96.7 | 91.6 | 95.4 | 96.2 | 96.7 | 96.8 | 96.7 | 96.4
ABB | PVI-4.6-1-OUTD-x-US-y [208V] | 4.6 kW, 208 Vac Inverter, where x may include S and y = PG or NG | 4.6 | 208 | 96 | Y | N | Multiple Listing of Power-One | 0.1 | 4.6 | 0.1 | 100 | 310 | 416 | 0.46 | 0.92 | 1.38 | 2.3 | 3.45 | 4.6 | 94.6 | 96.1 | 96.2 | 96.4 | 95.9 | 95.1 | 96 | 94.1 | 96.3 | 96.6 | 96.7 | 96.5 | 96.2 | 96.4 | 91.8 | 95.1 | 95.9 | 96.3 | 96 | 95.9 | 95.8
ABB | PVI-4.6-1-OUTD-x-US-y [240V] | 4.6 kW, 240 Vac Inverter, where x may include S and y = PG or NG | 4.6 | 240 | 96.5 | Y | N | Multiple Listing of Power-One | 0.1 | 4.6 | 0.1 | 100 | 340 | 416 | 0.46 | 0.92 | 1.38 | 2.3 | 3.45 | 4.6 | 94.1 | 96 | 96.2 | 96.5 | 96.2 | 95.6 | 96.1 | 93.8 | 96.3 | 96.7 | 96.9 | 96.8 | 96.6 | 96.6 | 92 | 95.4 | 96.2 | 96.6 | 96.5 | 96.5 | 96.2
ABB | PVI-4.6-1-OUTD-x-US-y [277V] | 4.6 kW, 277 Vac Inverter, where x may include S and y = PG or NG | 4.6 | 277 | 96.5 | Y | N | Multiple Listing of Power-One | 0.1 | 4.6 | 0.1 | 100 | 360 | 416 | 0.46 | 0.92 | 1.38 | 2.3 | 3.45 | 4.6 | 93.4 | 95.7 | 96.1 | 96.4 | 96.3 | 95.9 | 96.1 | 93.3 | 96.1 | 96.6 | 97 | 96.9 | 96.9 | 96.7 | 92.6 | 95.8 | 96.6 | 97 | 96.8 | 96.8 | 96.6
ABB | PVI-4.6-I-OUTD-x-US-y-Z [208V] | 4.6 kW, 208 Vac Inverter, where x may include S and y = PG or NG | 4.6 | 208 | 96 | Y | N |  | 0.1 | 4.6 | 0.1 | 100 | 310 | 416 | 0.46 | 0.92 | 1.38 | 2.3 | 3.45 | 4.6 | 94.6 | 96.1 | 96.2 | 96.4 | 95.9 | 95.1 | 96 | 94.1 | 96.3 | 96.6 | 96.7 | 96.5 | 96.2 | 96.4 | 91.8 | 95.1 | 95.9 | 96.3 | 96 | 95.9 | 95.8
ABB | PVI-4.6-I-OUTD-x-US-y-Z [240V] | 4.6 kW, 240 Vac Inverter, where x may include S and y = PG or NG | 4.6 | 240 | 96.5 | Y | N |  | 0.1 | 4.6 | 0.1 | 100 | 340 | 416 | 0.46 | 0.92 | 1.38 | 2.3 | 3.45 | 4.6 | 94.1 | 96 | 96.2 | 96.5 | 96.2 | 95.6 | 96.1 | 93.8 | 96.3 | 96.7 | 96.9 | 96.8 | 96.6 | 96.6 | 92 | 95.4 | 96.2 | 96.6 | 96.5 | 96.5 | 96.2
ABB | PVI-4.6-I-OUTD-x-US-y-Z [277V] | 4.6 kW, 277 Vac Inverter, where x may include S and y = PG or NG | 4.6 | 277 | 96.5 | Y | N |  | 0.1 | 4.6 | 0.1 | 100 | 360 | 416 | 0.46 | 0.92 | 1.38 | 2.3 | 3.45 | 4.6 | 93.4 | 95.7 | 96.1 | 96.4 | 96.3 | 95.9 | 96.1 | 93.3 | 96.1 | 96.6 | 97 | 96.9 | 96.9 | 96.7 | 92.6 | 95.8 | 96.6 | 97 | 96.8 | 96.8 | 96.6
ABB | UNO-DM-4.6-TL-PLUS-US-SB-RA [240V] | 4.6 kW, 240 Vac Utility Interactive Inverter with arc detector, WLAN, and Rapid Shutdown power supply | 4.6 | 240 | 96.5 | Y | N |  | 1 | 4.6 | 1 | 200 | 355 | 480 | 0.46 | 0.92 | 1.38 | 2.3 | 3.45 | 4.6 | 93.1 | 95.3 | 95.9 | 96 | 95.9 | 95.5 | 95.8 | 94.5 | 96.3 | 96.8 | 97 | 96.9 | 96.6 | 96.8 | 92.6 | 95.6 | 96.3 | 96.6 | 96.6 | 96.3 | 96.4 | 2017-07-01 | 2018-10-15
ABB | UNO-DM-4.6-TL-PLUS-US-SE-RA [240V] | 4.6 kW, 240 Vac Utility Interactive Inverter with arc detector, Ethernet LAN, and Rapid Shutdown power supply | 4.6 | 240 | 96.5 | Y | N |  | 1 | 4.6 | 1 | 200 | 355 | 480 | 0.46 | 0.92 | 1.38 | 2.3 | 3.45 | 4.6 | 93.1 | 95.3 | 95.9 | 96 | 95.9 | 95.5 | 95.8 | 94.5 | 96.3 | 96.8 | 97 | 96.9 | 96.6 | 96.8 | 92.6 | 95.6 | 96.3 | 96.6 | 96.6 | 96.3 | 96.4 | 2017-07-01 | 2018-10-15
ABB | UNO-DM-4.6-TL-PLUS-US-SZM-RA [240V] | 4.6 kW, 240 Vac Utility Interactive Inverter with arc detector, revenue grade meter, Zigbee radio, and Rapid Shutdown power supply | 4.6 | 240 | 96.5 | Y | N |  | 1 | 4.6 | 1 | 200 | 355 | 480 | 0.46 | 0.92 | 1.38 | 2.3 | 3.45 | 4.6 | 93.1 | 95.3 | 95.9 | 96 | 95.9 | 95.5 | 95.8 | 94.5 | 96.3 | 96.8 | 97 | 96.9 | 96.6 | 96.8 | 92.6 | 95.6 | 96.3 | 96.6 | 96.6 | 96.3 | 96.4 | 2017-07-01 | 2018-10-15
ABB | UNO-DM-4.6-TL-PLUS-US-SZ-RA [240V] | 4.6 kW, 240 Vac Utility Interactive Inverter with arc detector and Rapid Shutdown power supply | 4.6 | 240 | 96.5 | Y | N | Multiple Listing of Power-One | 1 | 4.6 | 1 | 200 | 355 | 480 | 0.46 | 0.92 | 1.38 | 2.3 | 3.45 | 4.6 | 93.1 | 95.3 | 95.9 | 96 | 95.9 | 95.5 | 95.8 | 94.5 | 96.3 | 96.8 | 97 | 96.9 | 96.6 | 96.8 | 92.6 | 95.6 | 96.3 | 96.6 | 96.6 | 96.3 | 96.4 | 2017-07-01 | 2018-10-15
ABB | PVI-5000-OUTD-S-US-Z [208V] | 5 kW, 208 Vac Utility Interactive Inverter with meter and with arc detector | 5 | 208 | 96 | Y | N | Multiple Listing of Power-One | 0.18 |  |  | 100 | 310 | 480 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 93.4 | 95.7 | 96.2 | 96.4 | 96.2 | 95.8 | 96.1 | 93.6 | 95.9 | 96.5 | 96.7 | 96.6 | 96.3 | 96.4 | 90.9 | 94.7 | 95.6 | 96.1 | 96.1 | 95.9 | 95.8
ABB | PVI-5000-OUTD-S-US-Z [240V] | 5 kW, 240 Vac Utility Interactive Inverter with meter and with arc detector | 5 | 240 | 96.5 | Y | N | Multiple Listing of Power-One | 0.24 |  |  | 100 | 345 | 480 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 92.5 | 95.5 | 96.1 | 96.4 | 96.3 | 96 | 96.1 | 93.8 | 96.2 | 96.7 | 97 | 96.9 | 96.6 | 96.7 | 91.5 | 95 | 95.9 | 96.4 | 96.5 | 96.3 | 96.1
ABB | PVI-5000-OUTD-S-US-Z [277V] | 5 kW, 277 Vac Utility Interactive Inverter with meter and with arc detector | 5 | 277 | 96.5 | Y | N | Multiple Listing of Power-One | 0.32 |  |  | 100 | 400 | 480 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 91.6 | 95 | 95.9 | 96.4 | 96.5 | 96.3 | 96.1 | 92.5 | 95.7 | 96.5 | 97.1 | 97.1 | 97 | 96.8 | 90.9 | 95 | 95.9 | 96.7 | 96.9 | 96.9 | 96.4
ABB | PVI-5000-OUTD-S-US-Z-A [208V] | 5 kW, 208 Vac Utility Interactive Inverter with meter and with arc detector | 5 | 208 | 96 | Y | N | Multiple Listing of Power-One | 0.18 |  |  | 100 | 310 | 480 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 93.4 | 95.7 | 96.2 | 96.4 | 96.2 | 95.8 | 96.1 | 93.6 | 95.9 | 96.5 | 96.7 | 96.6 | 96.3 | 96.4 | 90.9 | 94.7 | 95.6 | 96.1 | 96.1 | 95.9 | 95.8
ABB | PVI-5000-OUTD-S-US-Z-A [240V] | 5 kW, 240 Vac Utility Interactive Inverter with meter and with arc detector | 5 | 240 | 96.5 | Y | N | Multiple Listing of Power-One | 0.24 |  |  | 100 | 345 | 480 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 92.5 | 95.5 | 96.1 | 96.4 | 96.3 | 96 | 96.1 | 93.8 | 96.2 | 96.7 | 97 | 96.9 | 96.6 | 96.7 | 91.5 | 95 | 95.9 | 96.4 | 96.5 | 96.3 | 96.1
ABB | PVI-5000-OUTD-S-US-Z-A [277V] | 5 kW, 277 Vac Utility Interactive Inverter with meter and with arc detector | 5 | 277 | 96.5 | Y | N | Multiple Listing of Power-One | 0.32 |  |  | 100 | 400 | 480 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 91.6 | 95 | 95.9 | 96.4 | 96.5 | 96.3 | 96.1 | 92.5 | 95.7 | 96.5 | 97.1 | 97.1 | 97 | 96.8 | 90.9 | 95 | 95.9 | 96.7 | 96.9 | 96.9 | 96.4
ABB | PVI-5000-OUTD-US [208V] | 5 kW, 208 Vac Utility Interactive Inverter | 5 | 208 | 96 | Y | N | Multiple Listing of Power-One | 0.18 |  |  | 100 | 310 | 480 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 93.4 | 95.7 | 96.2 | 96.4 | 96.2 | 95.8 | 96.1 | 93.6 | 95.9 | 96.5 | 96.7 | 96.6 | 96.3 | 96.4 | 90.9 | 94.7 | 95.6 | 96.1 | 96.1 | 95.9 | 95.8
ABB | PVI-5000-OUTD-US [240V] | 5 kW, 240 Vac Utility Interactive Inverter | 5 | 240 | 96.5 | Y | N | Multiple Listing of Power-One | 0.24 |  |  | 100 | 345 | 480 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 92.5 | 95.5 | 96.1 | 96.4 | 96.3 | 96 | 96.1 | 93.8 | 96.2 | 96.7 | 97 | 96.9 | 96.6 | 96.7 | 91.5 | 95 | 95.9 | 96.4 | 96.5 | 96.3 | 96.1
ABB | PVI-5000-OUTD-US [277V] | 5 kW, 277 Vac Utility Interactive Inverter | 5 | 277 | 96.5 | Y | N | Multiple Listing of Power-One | 0.32 |  |  | 100 | 400 | 480 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 91.6 | 95 | 95.9 | 96.4 | 96.5 | 96.3 | 96.1 | 92.5 | 95.7 | 96.5 | 97.1 | 97.1 | 97 | 96.8 | 90.9 | 95 | 95.9 | 96.7 | 96.9 | 96.9 | 96.4
ABB | PVI-5000-OUTD-US-A [208V] | 5 kW, 208 Vac Utility Interactive Inverter with arc detector | 5 | 208 | 96 | Y | N | Multiple Listing of Power-One | 0.18 |  |  | 100 | 310 | 480 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 93.4 | 95.7 | 96.2 | 96.4 | 96.2 | 95.8 | 96.1 | 93.6 | 95.9 | 96.5 | 96.7 | 96.6 | 96.3 | 96.4 | 90.9 | 94.7 | 95.6 | 96.1 | 96.1 | 95.9 | 95.8 | 2017-07-01 | 2018-10-15
ABB | PVI-5000-OUTD-US-A [240V] | 5 kW, 240 Vac Utility Interactive Inverter with arc detector | 5 | 240 | 96.5 | Y | N | Multiple Listing of Power-One | 0.24 |  |  | 100 | 345 | 480 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 92.5 | 95.5 | 96.1 | 96.4 | 96.3 | 96 | 96.1 | 93.8 | 96.2 | 96.7 | 97 | 96.9 | 96.6 | 96.7 | 91.5 | 95 | 95.9 | 96.4 | 96.5 | 96.3 | 96.1 | 2017-07-01 | 2018-10-15
ABB | PVI-5000-OUTD-US-A [277V] | 5 kW, 277 Vac Utility Interactive Inverter with arc detector | 5 | 277 | 96.5 | Y | N | Multiple Listing of Power-One | 0.32 |  |  | 100 | 400 | 480 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 91.6 | 95 | 95.9 | 96.4 | 96.5 | 96.3 | 96.1 | 92.5 | 95.7 | 96.5 | 97.1 | 97.1 | 97 | 96.8 | 90.9 | 95 | 95.9 | 96.7 | 96.9 | 96.9 | 96.4 | 2017-07-01 | 2018-10-15
ABB | PVI-5000-OUTD-US-Z [208V] | 5 kW, 208 Vac Utility Interactive Inverter | 5 | 208 | 96 | Y | N | Multiple Listing of Power-One | 0.18 |  |  | 100 | 310 | 480 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 93.4 | 95.7 | 96.2 | 96.4 | 96.2 | 95.8 | 96.1 | 93.6 | 95.9 | 96.5 | 96.7 | 96.6 | 96.3 | 96.4 | 90.9 | 94.7 | 95.6 | 96.1 | 96.1 | 95.9 | 95.8
ABB | PVI-5000-OUTD-US-Z [240V] | 5 kW, 240 Vac Utility Interactive Inverter | 5 | 240 | 96.5 | Y | N | Multiple Listing of Power-One | 0.24 |  |  | 100 | 345 | 480 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 92.5 | 95.5 | 96.1 | 96.4 | 96.3 | 96 | 96.1 | 93.8 | 96.2 | 96.7 | 97 | 96.9 | 96.6 | 96.7 | 91.5 | 95 | 95.9 | 96.4 | 96.5 | 96.3 | 96.1
ABB | PVI-5000-OUTD-US-Z [277V] | 5 kW, 277 Vac Utility Interactive Inverter | 5 | 277 | 96.5 | Y | N | Multiple Listing of Power-One | 0.32 |  |  | 100 | 400 | 480 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 91.6 | 95 | 95.9 | 96.4 | 96.5 | 96.3 | 96.1 | 92.5 | 95.7 | 96.5 | 97.1 | 97.1 | 97 | 96.8 | 90.9 | 95 | 95.9 | 96.7 | 96.9 | 96.9 | 96.4
ABB | PVI-5000-OUTD-US-Z-A [208V] | 5 kW, 208 Vac Utility Interactive Inverter | 5 | 208 | 96 | Y | N | Multiple Listing of Power-One | 0.18 |  |  | 100 | 310 | 480 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 93.4 | 95.7 | 96.2 | 96.4 | 96.2 | 95.8 | 96.1 | 93.6 | 95.9 | 96.5 | 96.7 | 96.6 | 96.3 | 96.4 | 90.9 | 94.7 | 95.6 | 96.1 | 96.1 | 95.9 | 95.8 | 2017-07-01 | 2018-10-15
ABB | PVI-5000-OUTD-US-Z-A [240V] | 5 kW, 240 Vac Utility Interactive Inverter | 5 | 240 | 96.5 | Y | N | Multiple Listing of Power-One | 0.24 |  |  | 100 | 345 | 480 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 92.5 | 95.5 | 96.1 | 96.4 | 96.3 | 96 | 96.1 | 93.8 | 96.2 | 96.7 | 97 | 96.9 | 96.6 | 96.7 | 91.5 | 95 | 95.9 | 96.4 | 96.5 | 96.3 | 96.1 | 2017-07-01 | 2018-10-15
ABB | PVI-5000-OUTD-US-Z-A [277V] | 5 kW, 277 Vac Utility Interactive Inverter | 5 | 277 | 96.5 | Y | N | Multiple Listing of Power-One | 0.32 |  |  | 100 | 400 | 480 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 91.6 | 95 | 95.9 | 96.4 | 96.5 | 96.3 | 96.1 | 92.5 | 95.7 | 96.5 | 97.1 | 97.1 | 97 | 96.8 | 90.9 | 95 | 95.9 | 96.7 | 96.9 | 96.9 | 96.4 | 2017-07-01 | 2018-10-15
ABB | PVI-5000-OUTD-US-Z-M-A [208V] | 5 kW, 208 Vac Utility Interactive Inverter with arc-fault detection and meter | 5 | 208 | 96 | Y | N | Multiple Listing of Power-One | 0.18 |  |  | 100 | 310 | 480 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 93.4 | 95.7 | 96.2 | 96.4 | 96.2 | 95.8 | 96.1 | 93.6 | 95.9 | 96.5 | 96.7 | 96.6 | 96.3 | 96.4 | 90.9 | 94.7 | 95.6 | 96.1 | 96.1 | 95.9 | 95.8 | 2017-07-01 | 2018-10-15
ABB | PVI-5000-OUTD-US-Z-M-A [240V] | 5 kW, 240 Vac Utility Interactive Inverter with arc-fault detection and meter | 5 | 240 | 96.5 | Y | N | Multiple Listing of Power-One | 0.24 |  |  | 100 | 345 | 480 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 92.5 | 95.5 | 96.1 | 96.4 | 96.3 | 96 | 96.1 | 93.8 | 96.2 | 96.7 | 97 | 96.9 | 96.6 | 96.7 | 91.5 | 95 | 95.9 | 96.4 | 96.5 | 96.3 | 96.1 | 2017-07-01 | 2018-10-15
ABB | PVI-5000-OUTD-US-Z-M-A [277V] | 5 kW, 277 Vac Utility Interactive Inverter with arc-fault detection and meter | 5 | 277 | 96.5 | Y | N | Multiple Listing of Power-One | 0.32 |  |  | 100 | 400 | 480 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 91.6 | 95 | 95.9 | 96.4 | 96.5 | 96.3 | 96.1 | 92.5 | 95.7 | 96.5 | 97.1 | 97.1 | 97 | 96.8 | 90.9 | 95 | 95.9 | 96.7 | 96.9 | 96.9 | 96.4 | 2017-07-01 | 2018-10-15
ABB | PVI-6000-OUTD-S-US-A [208V] | 6 kW, 208 Vac Utility Interactive Inverter with meter and with arc detector | 6 | 208 | 96 | Y | N | Multiple Listing of Power-One | 0.18 |  |  | 100 | 310 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 94 | 96 | 96.4 | 96.3 | 96 | 95.5 | 96 | 94.3 | 96.2 | 96.6 | 96.7 | 96.4 | 96 | 96.4 | 92.1 | 95.1 | 95.9 | 96.1 | 96 | 95.7 | 95.8
ABB | PVI-6000-OUTD-S-US-A [240V] | 6 kW, 240 Vac Utility Interactive Inverter with meter and with arc detector | 6 | 240 | 96.5 | Y | N | Multiple Listing of Power-One | 0.24 |  |  | 100 | 345 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 93.5 | 95.8 | 96.3 | 96.4 | 96.2 | 95.8 | 96.1 | 94.6 | 96.5 | 96.9 | 96.9 | 96.8 | 96.5 | 96.7 | 92.6 | 95.5 | 96.1 | 96.5 | 96.4 | 96.2 | 96.2
ABB | PVI-6000-OUTD-S-US-A [277V] | 6 kW, 277 Vac Utility Interactive Inverter with meter and with arc detector | 6 | 277 | 96.5 | Y | N | Multiple Listing of Power-One | 0.32 |  |  | 100 | 400 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 92.5 | 95.5 | 96.2 | 96.4 | 96.4 | 96.1 | 96.1 | 93.5 | 96.2 | 96.8 | 97.1 | 97.1 | 97 | 96.9 | 92.2 | 95.5 | 96.3 | 96.8 | 96.9 | 96.9 | 96.5
ABB | PVI-6000-OUTD-S-US-Z [208V] | 6 kW, 208 Vac Utility Interactive Inverter with meter and with arc detector | 6 | 208 | 96 | Y | N | Multiple Listing of Power-One | 0.18 |  |  | 100 | 310 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 94 | 96 | 96.4 | 96.3 | 96 | 95.5 | 96 | 94.3 | 96.2 | 96.6 | 96.7 | 96.4 | 96 | 96.4 | 92.1 | 95.1 | 95.9 | 96.1 | 96 | 95.7 | 95.8
ABB | PVI-6000-OUTD-S-US-Z [240V] | 6 kW, 240 Vac Utility Interactive Inverter with meter and with arc detector | 6 | 240 | 96.5 | Y | N | Multiple Listing of Power-One | 0.24 |  |  | 100 | 345 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 93.5 | 95.8 | 96.3 | 96.4 | 96.2 | 95.8 | 96.1 | 94.6 | 96.5 | 96.9 | 96.9 | 96.8 | 96.5 | 96.7 | 92.6 | 95.5 | 96.1 | 96.5 | 96.4 | 96.2 | 96.2
ABB | PVI-6000-OUTD-S-US-Z [277V] | 6 kW, 277 Vac Utility Interactive Inverter with meter and with arc detector | 6 | 277 | 96.5 | Y | N | Multiple Listing of Power-One | 0.32 |  |  | 100 | 400 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 92.5 | 95.5 | 96.2 | 96.4 | 96.4 | 96.1 | 96.1 | 93.5 | 96.2 | 96.8 | 97.1 | 97.1 | 97 | 96.9 | 92.2 | 95.5 | 96.3 | 96.8 | 96.9 | 96.9 | 96.5
ABB | PVI-6000-OUTD-S-US-Z-A [208V] | 6 kW, 208 Vac Utility Interactive Inverter with meter and with arc detector | 6 | 208 | 96 | Y | N | Multiple Listing of Power-One | 0.18 |  |  | 100 | 310 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 94 | 96 | 96.4 | 96.3 | 96 | 95.5 | 96 | 94.3 | 96.2 | 96.6 | 96.7 | 96.4 | 96 | 96.4 | 92.1 | 95.1 | 95.9 | 96.1 | 96 | 95.7 | 95.8
ABB | PVI-6000-OUTD-S-US-Z-A [240V] | 6 kW, 240 Vac Utility Interactive Inverter with meter and with arc detector | 6 | 240 | 96.5 | Y | N | Multiple Listing of Power-One | 0.24 |  |  | 100 | 345 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 93.5 | 95.8 | 96.3 | 96.4 | 96.2 | 95.8 | 96.1 | 94.6 | 96.5 | 96.9 | 96.9 | 96.8 | 96.5 | 96.7 | 92.6 | 95.5 | 96.1 | 96.5 | 96.4 | 96.2 | 96.2
ABB | PVI-6000-OUTD-S-US-Z-A [277V] | 6 kW, 277 Vac Utility Interactive Inverter with meter and with arc detector | 6 | 277 | 96.5 | Y | N | Multiple Listing of Power-One | 0.32 |  |  | 100 | 400 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 92.5 | 95.5 | 96.2 | 96.4 | 96.4 | 96.1 | 96.1 | 93.5 | 96.2 | 96.8 | 97.1 | 97.1 | 97 | 96.9 | 92.2 | 95.5 | 96.3 | 96.8 | 96.9 | 96.9 | 96.5
ABB | PVI-6000-OUTD-US [208V] | 6 kW, 208 Vac Utility Interactive Inverter | 6 | 208 | 96 | Y | N | Multiple Listing of Power-One | 0.18 |  |  | 100 | 310 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 94 | 96 | 96.4 | 96.3 | 96 | 95.5 | 96 | 94.3 | 96.2 | 96.6 | 96.7 | 96.4 | 96 | 96.4 | 92.1 | 95.1 | 95.9 | 96.1 | 96 | 95.7 | 95.8
ABB | PVI-6000-OUTD-US [240V] | 6 kW, 240 Vac Utility Interactive Inverter | 6 | 240 | 96.5 | Y | N | Multiple Listing of Power-One | 0.24 |  |  | 100 | 345 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 93.5 | 95.8 | 96.3 | 96.4 | 96.2 | 95.8 | 96.1 | 94.6 | 96.5 | 96.9 | 96.9 | 96.8 | 96.5 | 96.7 | 92.6 | 95.5 | 96.1 | 96.5 | 96.4 | 96.2 | 96.2
ABB | PVI-6000-OUTD-US [277V] | 6 kW, 277 Vac Utility Interactive Inverter | 6 | 277 | 96.5 | Y | N | Multiple Listing of Power-One | 0.32 |  |  | 100 | 400 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 92.5 | 95.5 | 96.2 | 96.4 | 96.4 | 96.1 | 96.1 | 93.5 | 96.2 | 96.8 | 97.1 | 97.1 | 97 | 96.9 | 92.2 | 95.5 | 96.3 | 96.8 | 96.9 | 96.9 | 96.5
ABB | PVI-6000-OUTD-US-A [208V] | 6 kW, 208 Vac Utility Interactive Inverter | 6 | 208 | 96 | Y | N | Multiple Listing of Power-One | 0.18 |  |  | 100 | 310 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 94 | 96 | 96.4 | 96.3 | 96 | 95.5 | 96 | 94.3 | 96.2 | 96.6 | 96.7 | 96.4 | 96 | 96.4 | 92.1 | 95.1 | 95.9 | 96.1 | 96 | 95.7 | 95.8 | 2017-07-01 | 2018-10-15
ABB | PVI-6000-OUTD-US-A [240V] | 6 kW, 240 Vac Utility Interactive Inverter | 6 | 240 | 96.5 | Y | N | Multiple Listing of Power-One | 0.24 |  |  | 100 | 345 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 93.5 | 95.8 | 96.3 | 96.4 | 96.2 | 95.8 | 96.1 | 94.6 | 96.5 | 96.9 | 96.9 | 96.8 | 96.5 | 96.7 | 92.6 | 95.5 | 96.1 | 96.5 | 96.4 | 96.2 | 96.2 | 2017-07-01 | 2018-10-15
ABB | PVI-6000-OUTD-US-A [277V] | 6 kW, 277 Vac Utility Interactive Inverter | 6 | 277 | 96.5 | Y | N | Multiple Listing of Power-One | 0.32 |  |  | 100 | 400 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 92.5 | 95.5 | 96.2 | 96.4 | 96.4 | 96.1 | 96.1 | 93.5 | 96.2 | 96.8 | 97.1 | 97.1 | 97 | 96.9 | 92.2 | 95.5 | 96.3 | 96.8 | 96.9 | 96.9 | 96.5 | 2017-07-01 | 2018-10-15
ABB | PVI-6000-OUTD-US-Z [208V] | 6 kW, 208 Vac Utility Interactive Inverter | 6 | 208 | 96 | Y | N | Multiple Listing of Power-One | 0.18 |  |  | 100 | 310 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 94 | 96 | 96.4 | 96.3 | 96 | 95.5 | 96 | 94.3 | 96.2 | 96.6 | 96.7 | 96.4 | 96 | 96.4 | 92.1 | 95.1 | 95.9 | 96.1 | 96 | 95.7 | 95.8
ABB | PVI-6000-OUTD-US-Z [240V] | 6 kW, 240 Vac Utility Interactive Inverter | 6 | 240 | 96.5 | Y | N | Multiple Listing of Power-One | 0.24 |  |  | 100 | 345 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 93.5 | 95.8 | 96.3 | 96.4 | 96.2 | 95.8 | 96.1 | 94.6 | 96.5 | 96.9 | 96.9 | 96.8 | 96.5 | 96.7 | 92.6 | 95.5 | 96.1 | 96.5 | 96.4 | 96.2 | 96.2
ABB | PVI-6000-OUTD-US-Z [277V] | 6 kW, 277 Vac Utility Interactive Inverter | 6 | 277 | 96.5 | Y | N | Multiple Listing of Power-One | 0.32 |  |  | 100 | 400 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 92.5 | 95.5 | 96.2 | 96.4 | 96.4 | 96.1 | 96.1 | 93.5 | 96.2 | 96.8 | 97.1 | 97.1 | 97 | 96.9 | 92.2 | 95.5 | 96.3 | 96.8 | 96.9 | 96.9 | 96.5
ABB | PVI-6000-OUTD-US-Z-A [208V] | 6 kW, 208 Vac Utility Interactive Inverter | 6 | 208 | 96 | Y | N | Multiple Listing of Power-One | 0.18 |  |  | 100 | 310 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 94 | 96 | 96.4 | 96.3 | 96 | 95.5 | 96 | 94.3 | 96.2 | 96.6 | 96.7 | 96.4 | 96 | 96.4 | 92.1 | 95.1 | 95.9 | 96.1 | 96 | 95.7 | 95.8 | 2017-07-01 | 2018-10-15
ABB | PVI-6000-OUTD-US-Z-A [240V] | 6 kW, 240 Vac Utility Interactive Inverter | 6 | 240 | 96.5 | Y | N | Multiple Listing of Power-One | 0.24 |  |  | 100 | 345 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 93.5 | 95.8 | 96.3 | 96.4 | 96.2 | 95.8 | 96.1 | 94.6 | 96.5 | 96.9 | 96.9 | 96.8 | 96.5 | 96.7 | 92.6 | 95.5 | 96.1 | 96.5 | 96.4 | 96.2 | 96.2 | 2017-07-01 | 2018-10-15
ABB | PVI-6000-OUTD-US-Z-A [277V] | 6 kW, 277 Vac Utility Interactive Inverter | 6 | 277 | 96.5 | Y | N | Multiple Listing of Power-One | 0.32 |  |  | 100 | 400 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 92.5 | 95.5 | 96.2 | 96.4 | 96.4 | 96.1 | 96.1 | 93.5 | 96.2 | 96.8 | 97.1 | 97.1 | 97 | 96.9 | 92.2 | 95.5 | 96.3 | 96.8 | 96.9 | 96.9 | 96.5 | 2017-07-01 | 2018-10-15
ABB | PVI-6000-OUTD-US-Z-M-A [208V] | 6 kW, 208 Vac Utility Interactive Inverter with arc-fault detection and meter | 6 | 208 | 96 | Y | N | Multiple Listing of Power-One | 0.18 |  |  | 100 | 310 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 94 | 96 | 96.4 | 96.3 | 96 | 95.5 | 96 | 94.3 | 96.2 | 96.6 | 96.7 | 96.4 | 96 | 96.4 | 92.1 | 95.1 | 95.9 | 96.1 | 96 | 95.7 | 95.8 | 2017-07-01 | 2018-10-15
ABB | PVI-6000-OUTD-US-Z-M-A [240V] | 6 kW, 240 Vac Utility Interactive Inverter with arc-fault detection and meter | 6 | 240 | 96.5 | Y | N | Multiple Listing of Power-One | 0.24 |  |  | 100 | 345 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 93.5 | 95.8 | 96.3 | 96.4 | 96.2 | 95.8 | 96.1 | 94.6 | 96.5 | 96.9 | 96.9 | 96.8 | 96.5 | 96.7 | 92.6 | 95.5 | 96.1 | 96.5 | 96.4 | 96.2 | 96.2 | 2017-07-01 | 2018-10-15
ABB | PVI-6000-OUTD-US-Z-M-A [277V] | 6 kW, 277 Vac Utility Interactive Inverter with arc-fault detection and meter | 6 | 277 | 96.5 | Y | N | Multiple Listing of Power-One | 0.32 |  |  | 100 | 400 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 92.5 | 95.5 | 96.2 | 96.4 | 96.4 | 96.1 | 96.1 | 93.5 | 96.2 | 96.8 | 97.1 | 97.1 | 97 | 96.9 | 92.2 | 95.5 | 96.3 | 96.8 | 96.9 | 96.9 | 96.5 | 2017-07-01 | 2018-10-15
ABB | UNO-7.6-TL-OUTD-S-US-A [208V] | 7.6 kW, 208 Vac transformerless Utility Interactive Inverter with arc detector | 7.6 | 208 | 97 | Y | N | Multiple Listing of Power-One | 1.3 |  |  | 200 | 340 | 480 | 0.76 | 1.52 | 2.28 | 3.8 | 5.7 | 7.6 | 93.9 | 96 | 96.4 | 96.5 | 96.4 | 96.1 | 96.3 | 95.6 | 97.1 | 97.4 | 97.4 | 97.3 | 97 | 97.2 | 93.8 | 96.3 | 96.8 | 97.1 | 97 | 96.7 | 96.8 | 2017-07-01 | 2018-10-15
ABB | UNO-7.6-TL-OUTD-S-US-A [240V] | 7.6 kW, 240 Vac transformerless Utility Interactive Inverter with arc detector | 7.6 | 240 | 97 | Y | N | Multiple Listing of Power-One | 1.4 |  |  | 200 | 380 | 480 | 0.76 | 1.52 | 2.28 | 3.8 | 5.7 | 7.6 | 93.1 | 95.7 | 96.3 | 96.6 | 96.5 | 96.3 | 96.3 | 95.4 | 97.1 | 97.5 | 97.7 | 97.6 | 97.4 | 97.5 | 93.9 | 96.5 | 97.1 | 97.4 | 97.4 | 97.2 | 97.2 | 2017-07-01 | 2018-10-15
ABB | UNO-7.6-TL-OUTD-S-US-A [277V] | 7.6 kW, 277 Vac transformerless Utility Interactive Inverter with arc detector | 7.6 | 277 | 97 | Y | N | Multiple Listing of Power-One | 1.5 |  |  | 200 | 380 | 480 | 0.76 | 1.52 | 2.28 | 3.8 | 5.7 | 7.6 | 92.1 | 95.3 | 96.1 | 96.6 | 96.6 | 96.4 | 96.3 | 93.9 | 96.4 | 97 | 97.4 | 97.4 | 97.3 | 97.2 | 94.2 | 96.7 | 97.3 | 97.7 | 97.7 | 97.7 | 97.5 | 2017-07-01 | 2018-10-15
ABB | UNO-7.6-TL-OUTD-S-US-Z-A [208V] | 7.6 kW, 208 Vac transformerless Utility Interactive Inverter with arc detector | 7.6 | 208 | 97 | Y | N | Multiple Listing of Power-One | 1.3 |  |  | 200 | 340 | 480 | 0.76 | 1.52 | 2.28 | 3.8 | 5.7 | 7.6 | 93.9 | 96 | 96.4 | 96.5 | 96.4 | 96.1 | 96.3 | 95.6 | 97.1 | 97.4 | 97.4 | 97.3 | 97 | 97.2 | 93.8 | 96.3 | 96.8 | 97.1 | 97 | 96.7 | 96.8 | 2017-07-01 | 2018-10-15
ABB | UNO-7.6-TL-OUTD-S-US-Z-A [240V] | 7.6 kW, 240 Vac transformerless Utility Interactive Inverter with arc detector | 7.6 | 240 | 97 | Y | N | Multiple Listing of Power-One | 1.4 |  |  | 200 | 380 | 480 | 0.76 | 1.52 | 2.28 | 3.8 | 5.7 | 7.6 | 93.1 | 95.7 | 96.3 | 96.6 | 96.5 | 96.3 | 96.3 | 95.4 | 97.1 | 97.5 | 97.7 | 97.6 | 97.4 | 97.5 | 93.9 | 96.5 | 97.1 | 97.4 | 97.4 | 97.2 | 97.2 | 2017-07-01 | 2018-10-15
ABB | UNO-7.6-TL-OUTD-S-US-Z-A [277V] | 7.6 kW, 277 Vac transformerless Utility Interactive Inverter with arc detector | 7.6 | 277 | 97 | Y | N | Multiple Listing of Power-One | 1.5 |  |  | 200 | 380 | 480 | 0.76 | 1.52 | 2.28 | 3.8 | 5.7 | 7.6 | 92.1 | 95.3 | 96.1 | 96.6 | 96.6 | 96.4 | 96.3 | 93.9 | 96.4 | 97 | 97.4 | 97.4 | 97.3 | 97.2 | 94.2 | 96.7 | 97.3 | 97.7 | 97.7 | 97.7 | 97.5 | 2017-07-01 | 2018-10-15
ABB | UNO-7.6-TL-OUTD-S-US-Z-M [208V] | 7.6 kW, 208 Vac transformerless Utility Interactive Inverter with arc detector | 7.6 | 208 | 97 | Y | N |  | 1.3 |  |  | 200 | 340 | 480 | 0.76 | 1.52 | 2.28 | 3.8 | 5.7 | 7.6 | 93.9 | 96 | 96.4 | 96.5 | 96.4 | 96.1 | 96.3 | 95.6 | 97.1 | 97.4 | 97.4 | 97.3 | 97 | 97.2 | 93.8 | 96.3 | 96.8 | 97.1 | 97 | 96.7 | 96.8
ABB | UNO-7.6-TL-OUTD-S-US-Z-M [240V] | 7.6 kW, 240 Vac transformerless Utility Interactive Inverter with arc detector | 7.6 | 240 | 97 | Y | N |  | 1.4 |  |  | 200 | 380 | 480 | 0.76 | 1.52 | 2.28 | 3.8 | 5.7 | 7.6 | 93.1 | 95.7 | 96.3 | 96.6 | 96.5 | 96.3 | 96.3 | 95.4 | 97.1 | 97.5 | 97.7 | 97.6 | 97.4 | 97.5 | 93.9 | 96.5 | 97.1 | 97.4 | 97.4 | 97.2 | 97.2
ABB | UNO-7.6-TL-OUTD-S-US-Z-M [277V] | 7.6 kW, 277 Vac transformerless Utility Interactive Inverter with arc detector | 7.6 | 277 | 97 | Y | N |  | 1.5 |  |  | 200 | 380 | 480 | 0.76 | 1.52 | 2.28 | 3.8 | 5.7 | 7.6 | 92.1 | 95.3 | 96.1 | 96.6 | 96.6 | 96.4 | 96.3 | 93.9 | 96.4 | 97 | 97.4 | 97.4 | 97.3 | 97.2 | 94.2 | 96.7 | 97.3 | 97.7 | 97.7 | 97.7 | 97.5
ABB | UNO-7.6-TL-OUTD-S-US-Z-M-A [208V] | 7.6 kW, 208 Vac transformerless Utility Interactive Inverter with arc detector | 7.6 | 208 | 97 | Y | N | Multiple Listing of Power-One | 1.3 |  |  | 200 | 340 | 480 | 0.76 | 1.52 | 2.28 | 3.8 | 5.7 | 7.6 | 93.9 | 96 | 96.4 | 96.5 | 96.4 | 96.1 | 96.3 | 95.6 | 97.1 | 97.4 | 97.4 | 97.3 | 97 | 97.2 | 93.8 | 96.3 | 96.8 | 97.1 | 97 | 96.7 | 96.8 | 2017-07-01 | 2018-10-15
ABB | UNO-7.6-TL-OUTD-S-US-Z-M-A [240V] | 7.6 kW, 240 Vac transformerless Utility Interactive Inverter with arc detector | 7.6 | 240 | 97 | Y | N | Multiple Listing of Power-One | 1.4 |  |  | 200 | 380 | 480 | 0.76 | 1.52 | 2.28 | 3.8 | 5.7 | 7.6 | 93.1 | 95.7 | 96.3 | 96.6 | 96.5 | 96.3 | 96.3 | 95.4 | 97.1 | 97.5 | 97.7 | 97.6 | 97.4 | 97.5 | 93.9 | 96.5 | 97.1 | 97.4 | 97.4 | 97.2 | 97.2 | 2017-07-01 | 2018-10-15
ABB | UNO-7.6-TL-OUTD-S-US-Z-M-A [277V] | 7.6 kW, 277 Vac transformerless Utility Interactive Inverter with arc detector | 7.6 | 277 | 97 | Y | N | Multiple Listing of Power-One | 1.5 |  |  | 200 | 380 | 480 | 0.76 | 1.52 | 2.28 | 3.8 | 5.7 | 7.6 | 92.1 | 95.3 | 96.1 | 96.6 | 96.6 | 96.4 | 96.3 | 93.9 | 96.4 | 97 | 97.4 | 97.4 | 97.3 | 97.2 | 94.2 | 96.7 | 97.3 | 97.7 | 97.7 | 97.7 | 97.5 | 2017-07-01 | 2018-10-15
ABB | UNO-8.6-TL-OUTD-S-US-A [240V] | 8.6 kW, 240 Vac transformerless Utility Interactive Inverter with arc detector | 8.6 | 240 | 97 | Y | N | Multiple Listing of Power-One | 1.4 |  |  | 200 | 380 | 480 | 0.86 | 1.72 | 2.58 | 4.3 | 6.45 | 8.6 | 93.7 | 95.9 | 96.4 | 96.6 | 96.4 | 96.2 | 96.3 | 95.7 | 97.3 | 97.6 | 97.7 | 97.6 | 97.4 | 97.5 | 94.5 | 96.7 | 97.2 | 97.4 | 97.4 | 97.2 | 97.2 | 2017-07-01 | 2018-10-15
ABB | UNO-8.6-TL-OUTD-S-US-A [277V] | 8.6 kW, 277 Vac transformerless Utility Interactive Inverter with arc detector | 8.6 | 277 | 97 | Y | N | Multiple Listing of Power-One | 1.5 |  |  | 200 | 380 | 480 | 0.86 | 1.72 | 2.58 | 4.3 | 6.45 | 8.6 | 92.8 | 95.6 | 96.3 | 96.6 | 96.5 | 96.3 | 96.3 | 94.5 | 96.6 | 97.1 | 97.4 | 97.4 | 97.3 | 97.2 | 94.8 | 96.9 | 97.5 | 97.8 | 97.7 | 97.6 | 97.5 | 2017-07-01 | 2018-10-15
ABB | UNO-8.6-TL-OUTD-S-US-Z-A [240V] | 8.6 kW, 240 Vac transformerless Utility Interactive Inverter with arc detector | 8.6 | 240 | 97 | Y | N | Multiple Listing of Power-One | 1.4 |  |  | 200 | 380 | 480 | 0.86 | 1.72 | 2.58 | 4.3 | 6.45 | 8.6 | 93.7 | 95.9 | 96.4 | 96.6 | 96.4 | 96.2 | 96.3 | 95.7 | 97.3 | 97.6 | 97.7 | 97.6 | 97.4 | 97.5 | 94.5 | 96.7 | 97.2 | 97.4 | 97.4 | 97.2 | 97.2 | 2017-07-01 | 2018-10-15
ABB | UNO-8.6-TL-OUTD-S-US-Z-A [277V] | 8.6 kW, 277 Vac transformerless Utility Interactive Inverter with arc detector | 8.6 | 277 | 97 | Y | N | Multiple Listing of Power-One | 1.5 |  |  | 200 | 380 | 480 | 0.86 | 1.72 | 2.58 | 4.3 | 6.45 | 8.6 | 92.8 | 95.6 | 96.3 | 96.6 | 96.5 | 96.3 | 96.3 | 94.5 | 96.6 | 97.1 | 97.4 | 97.4 | 97.3 | 97.2 | 94.8 | 96.9 | 97.5 | 97.8 | 97.7 | 97.6 | 97.5 | 2017-07-01 | 2018-10-15
ABB | UNO-8.6-TL-OUTD-S-US-Z-M [240V] | 8.6 kW, 240 Vac transformerless Utility Interactive Inverter with arc detector | 8.6 | 240 | 97 | Y | N |  | 1.4 |  |  | 200 | 380 | 480 | 0.86 | 1.72 | 2.58 | 4.3 | 6.45 | 8.6 | 93.7 | 95.9 | 96.4 | 96.6 | 96.4 | 96.2 | 96.3 | 95.7 | 97.3 | 97.6 | 97.7 | 97.6 | 97.4 | 97.5 | 94.5 | 96.7 | 97.2 | 97.4 | 97.4 | 97.2 | 97.2
ABB | UNO-8.6-TL-OUTD-S-US-Z-M [277V] | 8.6 kW, 277 Vac transformerless Utility Interactive Inverter with arc detector | 8.6 | 277 | 97 | Y | N |  | 1.5 |  |  | 200 | 380 | 480 | 0.86 | 1.72 | 2.58 | 4.3 | 6.45 | 8.6 | 92.8 | 95.6 | 96.3 | 96.6 | 96.5 | 96.3 | 96.3 | 94.5 | 96.6 | 97.1 | 97.4 | 97.4 | 97.3 | 97.2 | 94.8 | 96.9 | 97.5 | 97.8 | 97.7 | 97.6 | 97.5
ABB | UNO-8.6-TL-OUTD-S-US-Z-M-A [240V] | 8.6 kW, 240 Vac transformerless Utility Interactive Inverter with arc detector | 8.6 | 240 | 97 | Y | N | Multiple Listing of Power-One | 1.4 |  |  | 200 | 380 | 480 | 0.86 | 1.72 | 2.58 | 4.3 | 6.45 | 8.6 | 93.7 | 95.9 | 96.4 | 96.6 | 96.4 | 96.2 | 96.3 | 95.7 | 97.3 | 97.6 | 97.7 | 97.6 | 97.4 | 97.5 | 94.5 | 96.7 | 97.2 | 97.4 | 97.4 | 97.2 | 97.2 | 2017-07-01 | 2018-10-15
ABB | UNO-8.6-TL-OUTD-S-US-Z-M-A [277V] | 8.6 kW, 277 Vac transformerless Utility Interactive Inverter with arc detector | 8.6 | 277 | 97 | Y | N | Multiple Listing of Power-One | 1.5 |  |  | 200 | 380 | 480 | 0.86 | 1.72 | 2.58 | 4.3 | 6.45 | 8.6 | 92.8 | 95.6 | 96.3 | 96.6 | 96.5 | 96.3 | 96.3 | 94.5 | 96.6 | 97.1 | 97.4 | 97.4 | 97.3 | 97.2 | 94.8 | 96.9 | 97.5 | 97.8 | 97.7 | 97.6 | 97.5 | 2017-07-01 | 2018-10-15
ABB | PVI-10.0-I-OUTD-x-US-208-y [208V] | 10 kW, 208 Vac Inverter, where x = (blank), S, S1, or S2 and y = PG or NG | 10 | 208 | 96 | Y | N | Multiple Listing of Power-One | 0.1 | 10 | 0.1 | 220 | 320 | 416 | 1 | 2 | 3 | 5 | 7.5 | 10 | 94.5 | 96.1 | 96.2 | 96.3 | 95.7 | 94.8 | 95.8 | 94.4 | 96.3 | 96.5 | 96.5 | 96.3 | 95.7 | 96.2 | 93.1 | 95.7 | 96.2 | 96.2 | 95.9 | 95.5 | 95.8
ABB | PVI-10.0-I-OUTD-x-US-480-y-z [480V] | 10 kW, 480 Vac Inverter, where x = (blank), S, S1, or S2; y = PG or NG; and z = (blank) or 12A | 10 | 480 | 97 | Y | N | Multiple Listing of Power-One | 0.4 | 10 | 0.4 | 220 | 362 | 416 | 1 | 2 | 3 | 5 | 7.5 | 10 | 92.7 | 95.4 | 96.2 | 96.9 | 96.8 | 96.4 | 96.5 | 92.6 | 96 | 96.8 | 97.2 | 97.3 | 97.3 | 97 | 92.3 | 95.9 | 96.8 | 97.3 | 97.3 | 97.3 | 97
ABB | PVI-12.0-I-OUTD-x-US-480-y [480V] | 12 kW, 480 Vac Inverter, where x = (blank), S, S1, or S2 and y =PG or NG | 12 | 480 | 97 | Y | N | Multiple Listing of Power-One | 0.4 | 12 | 0.4 | 250 | 370 | 416 | 1.2 | 2.4 | 3.6 | 6 | 9 | 12 | 93.7 | 96 | 96.5 | 97 | 96.9 | 96.4 | 96.7 | 93.6 | 96.3 | 97 | 97.2 | 97.3 | 97.2 | 97 | 93.4 | 96.4 | 97 | 97.2 | 97.3 | 97.3 | 97.1
ABB | TRIO-20.0-TL-OUTD-S1A-US-480 [480V] | 20 kW, 480 Vac Inverter | 20 | 480 | 97.5 | Y | N | Multiple Listing of Power-One | 0.61 |  |  | 450 | 700 | 800 | 2 | 4 | 6 | 10 | 15 | 20 | 93.5 | 95.4 | 96.3 | 96.9 | 97 | 97 | 96.7 | 94.5 | 96.7 | 97.3 | 97.7 | 97.7 | 97.7 | 97.5 | 95.4 | 97.2 | 97.8 | 98.1 | 98.2 | 98.1 | 97.9
ABB | TRIO-20.0-TL-OUTD-S1A-US-480-A [480V] | 20 kW, 480 Vac Inverter with arc detector | 20 | 480 | 97.5 | Y | N |  | 0.61 |  |  | 450 | 700 | 800 | 2 | 4 | 6 | 10 | 15 | 20 | 93.5 | 95.4 | 96.3 | 96.9 | 97 | 97 | 96.7 | 94.5 | 96.7 | 97.3 | 97.7 | 97.7 | 97.7 | 97.5 | 95.4 | 97.2 | 97.8 | 98.1 | 98.2 | 98.1 | 97.9
ABB | TRIO-20.0-TL-OUTD-S1B-US-480 [480V] | 20 kW, 480 Vac Inverter with arc detector | 20 | 480 | 97.5 | Y | N | Multiple Listing of Power-One | 0.61 |  |  | 450 | 700 | 800 | 2 | 4 | 6 | 10 | 15 | 20 | 93.5 | 95.4 | 96.3 | 96.9 | 97 | 97 | 96.7 | 94.5 | 96.7 | 97.3 | 97.7 | 97.7 | 97.7 | 97.5 | 95.4 | 97.2 | 97.8 | 98.1 | 98.2 | 98.1 | 97.9
ABB | TRIO-20.0-TL-OUTD-S1B-US-480-A [480V] | 20 kW, 480 Vac Inverter with arc detector | 20 | 480 | 97.5 | Y | N |  | 0.61 |  |  | 450 | 700 | 800 | 2 | 4 | 6 | 10 | 15 | 20 | 93.5 | 95.4 | 96.3 | 96.9 | 97 | 97 | 96.7 | 94.5 | 96.7 | 97.3 | 97.7 | 97.7 | 97.7 | 97.5 | 95.4 | 97.2 | 97.8 | 98.1 | 98.2 | 98.1 | 97.9
ABB | TRIO-20.0-TL-OUTD-S1-US-480 [480V] | 20 kW, 480 Vac Inverter | 20 | 480 | 97.5 | Y | N | Multiple Listing of Power-One | 0.61 |  |  | 450 | 700 | 800 | 2 | 4 | 6 | 10 | 15 | 20 | 93.5 | 95.4 | 96.3 | 96.9 | 97 | 97 | 96.7 | 94.5 | 96.7 | 97.3 | 97.7 | 97.7 | 97.7 | 97.5 | 95.4 | 97.2 | 97.8 | 98.1 | 98.2 | 98.1 | 97.9
ABB | TRIO-20.0-TL-OUTD-S1-US-480-A [480V] | 20 kW, 480 Vac Inverter with arc detector | 20 | 480 | 97.5 | Y | N |  | 0.61 |  |  | 450 | 700 | 800 | 2 | 4 | 6 | 10 | 15 | 20 | 93.5 | 95.4 | 96.3 | 96.9 | 97 | 97 | 96.7 | 94.5 | 96.7 | 97.3 | 97.7 | 97.7 | 97.7 | 97.5 | 95.4 | 97.2 | 97.8 | 98.1 | 98.2 | 98.1 | 97.9
ABB | TRIO-20.0-TL-OUTD-S-US-480 [480V] | 20 kW, 480 Vac Inverter with arc detector | 20 | 480 | 97.5 | Y | N | Multiple Listing of Power-One | 0.61 |  |  | 450 | 700 | 800 | 2 | 4 | 6 | 10 | 15 | 20 | 93.5 | 95.4 | 96.3 | 96.9 | 97 | 97 | 96.7 | 94.5 | 96.7 | 97.3 | 97.7 | 97.7 | 97.7 | 97.5 | 95.4 | 97.2 | 97.8 | 98.1 | 98.2 | 98.1 | 97.9
ABB | TRIO-20.0-TL-OUTD-S-US-480-A [480V] | 20 kW, 480 Vac Inverter with arc detector | 20 | 480 | 97.5 | Y | N |  | 0.61 |  |  | 450 | 700 | 800 | 2 | 4 | 6 | 10 | 15 | 20 | 93.5 | 95.4 | 96.3 | 96.9 | 97 | 97 | 96.7 | 94.5 | 96.7 | 97.3 | 97.7 | 97.7 | 97.7 | 97.5 | 95.4 | 97.2 | 97.8 | 98.1 | 98.2 | 98.1 | 97.9
ABB | TRIO-27.6-TL-OUTD-S1A-US-480 [480V] | 27.6 kW, 480 Vac Inverter | 27.6 | 480 | 97.5 | Y | N | Multiple Listing of Power-One | 0.61 |  |  | 520 | 715 | 800 | 2.76 | 5.52 | 8.28 | 13.8 | 20.7 | 27.6 | 94.8 | 96.4 | 97 | 97.4 | 97.4 | 97.3 | 97.2 | 95.4 | 97.1 | 97.6 | 97.8 | 97.9 | 97.8 | 97.7 | 96.1 | 97.6 | 98 | 98.2 | 98.2 | 98.2 | 98.1
ABB | TRIO-27.6-TL-OUTD-S1A-US-480-A [480V] | 27.6 kW, 480 Vac Inverter with arc detector | 27.6 | 480 | 97.5 | Y | N |  | 0.61 |  |  | 520 | 715 | 800 | 2.76 | 5.52 | 8.28 | 13.8 | 20.7 | 27.6 | 94.8 | 96.4 | 97 | 97.4 | 97.4 | 97.3 | 97.2 | 95.4 | 97.1 | 97.6 | 97.8 | 97.9 | 97.8 | 97.7 | 96.1 | 97.6 | 98 | 98.2 | 98.2 | 98.2 | 98.1
ABB | TRIO-27.6-TL-OUTD-S1B-US-480 [480V] | 27.6 kW, 480 Vac Inverter | 27.6 | 480 | 97.5 | Y | N | Multiple Listing of Power-One | 0.61 |  |  | 520 | 715 | 800 | 2.76 | 5.52 | 8.28 | 13.8 | 20.7 | 27.6 | 94.8 | 96.4 | 97 | 97.4 | 97.4 | 97.3 | 97.2 | 95.4 | 97.1 | 97.6 | 97.8 | 97.9 | 97.8 | 97.7 | 96.1 | 97.6 | 98 | 98.2 | 98.2 | 98.2 | 98.1
ABB | TRIO-27.6-TL-OUTD-S1B-US-480-A [480V] | 27.6 kW, 480 Vac Inverter with arc detector | 27.6 | 480 | 97.5 | Y | N |  | 0.61 |  |  | 520 | 715 | 800 | 2.76 | 5.52 | 8.28 | 13.8 | 20.7 | 27.6 | 94.8 | 96.4 | 97 | 97.4 | 97.4 | 97.3 | 97.2 | 95.4 | 97.1 | 97.6 | 97.8 | 97.9 | 97.8 | 97.7 | 96.1 | 97.6 | 98 | 98.2 | 98.2 | 98.2 | 98.1
ABB | TRIO-27.6-TL-OUTD-S1-US-480 [480V] | 27.6 kW, 480 Vac Inverter | 27.6 | 480 | 97.5 | Y | N | Multiple Listing of Power-One | 0.61 |  |  | 520 | 715 | 800 | 2.76 | 5.52 | 8.28 | 13.8 | 20.7 | 27.6 | 94.8 | 96.4 | 97 | 97.4 | 97.4 | 97.3 | 97.2 | 95.4 | 97.1 | 97.6 | 97.8 | 97.9 | 97.8 | 97.7 | 96.1 | 97.6 | 98 | 98.2 | 98.2 | 98.2 | 98.1
ABB | TRIO-27.6-TL-OUTD-S1-US-480-A [480V] | 27.6 kW, 480 Vac Inverter with arc detector | 27.6 | 480 | 97.5 | Y | N |  | 0.61 |  |  | 520 | 715 | 800 | 2.76 | 5.52 | 8.28 | 13.8 | 20.7 | 27.6 | 94.8 | 96.4 | 97 | 97.4 | 97.4 | 97.3 | 97.2 | 95.4 | 97.1 | 97.6 | 97.8 | 97.9 | 97.8 | 97.7 | 96.1 | 97.6 | 98 | 98.2 | 98.2 | 98.2 | 98.1
ABB | TRIO-27.6-TL-OUTD-S-US-480 [480V] | 27.6 kW, 480 Vac Inverter | 27.6 | 480 | 97.5 | Y | N | Multiple Listing of Power-One | 0.61 |  |  | 520 | 715 | 800 | 2.76 | 5.52 | 8.28 | 13.8 | 20.7 | 27.6 | 94.8 | 96.4 | 97 | 97.4 | 97.4 | 97.3 | 97.2 | 95.4 | 97.1 | 97.6 | 97.8 | 97.9 | 97.8 | 97.7 | 96.1 | 97.6 | 98 | 98.2 | 98.2 | 98.2 | 98.1
ABB | TRIO-27.6-TL-OUTD-S-US-480-A [480V] | 27.6 kW, 480 Vac Inverter with arc detector | 27.6 | 480 | 97.5 | Y | N |  | 0.61 |  |  | 520 | 715 | 800 | 2.76 | 5.52 | 8.28 | 13.8 | 20.7 | 27.6 | 94.8 | 96.4 | 97 | 97.4 | 97.4 | 97.3 | 97.2 | 95.4 | 97.1 | 97.6 | 97.8 | 97.9 | 97.8 | 97.7 | 96.1 | 97.6 | 98 | 98.2 | 98.2 | 98.2 | 98.1
ABB | PVI-CENTRAL-50-US [208V] | 50 kW, 208 Vac Utility Interactive Inverter | 50 | 208 | 95 | Y | N | Multiple Listing of Power-One | 33 | 50 | 33 | 330 | 370 | 480 | 5 | 10 | 15 | 25 | 37.5 | 50 | 90.7 | 94.5 | 95.4 | 95.6 | 95.3 | 94.7 | 95.1 | 90.4 | 94.4 | 95.3 | 95.6 | 95.2 | 94.6 | 95 | 89.7 | 94 | 94.8 | 95.2 | 94.9 | 94.4 | 94.7
ABB | PVI-CENTRAL-50-US [480V] | 50 kW, 480 Vac Utility Interactive Inverter | 50 | 480 | 95 | Y | N | Multiple Listing of Power-One | 41 | 50 | 41 | 330 | 370 | 480 | 5 | 10 | 15 | 25 | 37.5 | 50 | 90.5 | 94.4 | 95.3 | 95.7 | 95.6 | 95.1 | 95.3 | 90.2 | 94.2 | 95.2 | 95.6 | 95.5 | 95 | 95.2 | 89.5 | 93.8 | 94.9 | 95.3 | 95.3 | 94.8 | 94.9
ABB | TRIO-50.0-TL-OUTD-US-480 [480V] | 50 kW, 480 Vac Utility Interactive Inverter with arc detector | 50 | 480 | 98 | Y | N | Multiple Listing of Power-One | 1 | 50 | 1 | 520 | 720 | 800 | 5 | 10 | 15 | 25 | 37.5 | 50 | 96.3426 | 97.3941 | 97.7305 | 97.8494 | 97.8642 | 97.7358 | 97.8 | 96.859 | 98.0033 | 98.3351 | 98.526 | 98.5515 | 98.4933 | 98.4222 | 95.9226 | 97.5683 | 98.0341 | 98.3179 | 98.3432 | 98.3043 | 98.1633 | 2017-07-01 | 2018-10-15
ABB | TRIO-60.0-TL-OUTD-US-480 [480V] | 60 kW, 480 Vac Utility Interactive Inverter with arc detector | 60 | 480 | 98 | Y | N | Multiple Listing of Power-One | 0.8 | 60 | 0.8 | 570 | 720 | 800 | 6 | 12 | 18 | 30 | 45 | 60 | 96.7 | 97.7 | 97.9 | 98 | 98 | 97.8 | 97.9 | 97.2 | 98.1 | 98.4 | 98.5 | 98.5 | 98.4 | 98.4 | 96.4 | 97.8 | 98.1 | 98.3 | 98.3 | 98.2 | 98.2 | 2017-07-01 | 2018-10-15
ABB | PVI-CENTRAL-100-US [208V] | 100 kW, 208 Vac Utility Interactive Inverter | 100 | 208 | 95 | Y | N | Multiple Listing of Power-One | 47 | 100 | 47 | 330 | 370 | 480 | 10 | 20 | 30 | 50 | 75 | 100 | 91.5 | 94.7 | 95.4 | 95.6 | 95.3 | 94.7 | 95.2 | 91.2 | 94.5 | 95.3 | 95.5 | 95.2 | 94.6 | 95.1 | 90.3 | 94.1 | 94.9 | 95.2 | 95 | 94.4 | 94.7
ABB | PVI-CENTRAL-100-US [480V] | 100 kW, 480 Vac Utility Interactive Inverter | 100 | 480 | 95 | Y | N | Multiple Listing of Power-One | 50 | 100 | 50 | 330 | 370 | 480 | 10 | 20 | 30 | 50 | 75 | 100 | 91.5 | 94.8 | 95.5 | 95.7 | 95.5 | 94.7 | 95.3 | 91.2 | 94.6 | 95.3 | 95.6 | 95.4 | 94.6 | 95.2 | 90.3 | 94.2 | 95 | 95.3 | 95.1 | 94.4 | 94.8
ABB | PVI-CENTRAL-250-US [480V] | 250 kW, 480 Vac Utility Interactive Inverter | 250 | 480 | 97 | Y | N | Multiple Listing of Power-One | 105.3 | 250 | 105.3 | 320 | 360 | 480 | 25 | 50 | 75 | 125 | 187.5 | 250 | 95.7 | 97.5 | 97.5 | 97.6 | 97 | 96.6 | 97.1 | 95.4 | 97.2 | 97.3 | 97.4 | 96.8 | 96.5 | 96.9 | 94.1 | 96 | 96.3 | 96.7 | 96.5 | 96 | 96.3
ABB | PVI-CENTRAL-300-US [480V] | 300 kW, 480 Vac Utility Interactive Inverter | 300 | 480 | 97 | Y | N | Multiple Listing of Power-One | 119 | 300 | 119 | 320 | 360 | 480 | 30 | 60 | 90 | 150 | 225 | 300 | 96.2 | 97.5 | 97.6 | 97.6 | 97.1 | 96.5 | 97.2 | 95.8 | 97.3 | 97.4 | 97.4 | 96.9 | 96.4 | 97 | 94.8 | 96.2 | 96.3 | 96.6 | 96.3 | 95.8 | 96.3
ABB | ULTRA-750-TL-OUTD-2-US-690-x-y-z [690V] | 750 kW, 690 Vac Utility Interactive Inverter with Medium Voltage NEMA TP1 transformer | 750 | 690 | 96.5 | Y | N | Multiple Listing of Power-One | 301.7 |  |  | 585 | 746 | 800 | 75 | 150 | 225 | 375 | 562.5 | 750 | 94.5 | 95.8 | 96.2 | 96.2 | 95.9 | 95.1 | 95.9 | 95 | 96.5 | 96.7 | 96.9 | 96.5 | 95.9 | 96.5 | 95.1 | 96.6 | 96.9 | 97 | 96.7 | 96.1 | 96.7
ABB | ULTRA-750-TL-OUTD-4-US-690-x-y-z [690V] | 750 kW, 690 Vac Utility Interactive Inverter with Medium Voltage NEMA TP1 transformer | 750 | 690 | 96.5 | Y | N | Multiple Listing of Power-One | 346.8 |  |  | 585 | 746 | 800 | 75 | 150 | 225 | 375 | 562.5 | 750 | 94.4 | 96 | 96.4 | 96.5 | 96.1 | 95.4 | 96.1 | 94.9 | 96.5 | 96.8 | 97.1 | 96.8 | 96.2 | 96.7 | 95 | 96.6 | 96.9 | 97.1 | 96.9 | 96.4 | 96.8
ABB | ULTRA-750-TL-OUTD-1-US-690-x-y-z [690V] | 750 kW, 690 Vac Utility Interactive Inverter with Medium Voltage NEMA TP1 transformer | 780 | 690 | 96.5 | Y | N | Multiple Listing of Power-One | 302 |  |  | 585 | 746 | 800 | 78 | 156 | 234 | 390 | 585 | 780 | 94.4 | 95.8 | 96.1 | 96.2 | 95.8 | 95.1 | 95.8 | 94.9 | 96.4 | 96.7 | 96.9 | 96.5 | 96 | 96.5 | 95.1 | 96.6 | 96.9 | 97 | 96.7 | 96.2 | 96.7
ABB | ULTRA-750-TL-OUTD-3-US-690-x-y-z [690V] | 750 kW, 690 Vac Utility Interactive Inverter with Medium Voltage NEMA TP1 transformer | 780 | 690 | 96.5 | Y | N | Multiple Listing of Power-One | 346.8 |  |  | 585 | 746 | 800 | 78 | 156 | 234 | 390 | 585 | 780 | 94.5 | 96 | 96.4 | 96.4 | 96 | 95.3 | 96.1 | 95 | 96.5 | 97 | 97.1 | 96.8 | 96.2 | 96.7 | 95.1 | 96.6 | 97.1 | 97.2 | 96.9 | 96.3 | 96.9
ABB | ULTRA-1100-TL-OUTD-2-US-690-x-y-z [690V] | 1100 kW, 690 Vac Utility Interactive Inverter with Medium Voltage NEMA TP1 transformer | 1000 | 690 | 96.5 | Y | N | Multiple Listing of Power-One | 328.8 |  |  | 585 | 746 | 800 | 100 | 200 | 300 | 500 | 750 | 1000 | 94.5 | 96.1 | 96.5 | 96.5 | 96.2 | 95.4 | 96.2 | 94.9 | 96.7 | 97.1 | 97.1 | 96.8 | 96.2 | 96.8 | 95.1 | 96.9 | 97.2 | 97.3 | 96.9 | 96.4 | 96.9
ABB | ULTRA-1100-TL-OUTD-4-US-690-x-y-z [690V] | 1100 kW, 690 Vac Utility Interactive Inverter with Medium Voltage NEMA TP1 transformer | 1000 | 690 | 97 | Y | N | Multiple Listing of Power-One | 381.6 |  |  | 585 | 746 | 800 | 100 | 200 | 300 | 500 | 750 | 1000 | 94.5 | 96.2 | 96.6 | 96.8 | 96.4 | 95.8 | 96.4 | 95 | 96.8 | 97.2 | 97.3 | 97 | 96.5 | 97 | 95.1 | 96.9 | 97.4 | 97.4 | 97.1 | 96.6 | 97.1
ABB | ULTRA-1100-TL-OUTD-1-US-690-x-y-z [690V] | 1100 kW, 690 Vac Utility Interactive Inverter with Medium Voltage NEMA TP1 transformer | 1154 | 690 | 96.5 | Y | N | Multiple Listing of Power-One | 329 |  |  | 585 | 746 | 800 | 117 | 234 | 351 | 585 | 877.5 | 1170 | 94.4 | 96 | 96.4 | 96.5 | 96.1 | 95.4 | 96.1 | 95 | 96.6 | 97 | 97.1 | 96.8 | 96.2 | 96.8 | 95.1 | 96.8 | 97.2 | 97.3 | 97 | 96.4 | 97
ABB | ULTRA-1100-TL-OUTD-3-US-690-x-y-z [690V] | 1100 kW, 690 Vac Utility Interactive Inverter with Medium Voltage NEMA TP1 transformer | 1170 | 690 | 97 | Y | N | Multiple Listing of Power-One | 381.6 |  |  | 585 | 746 | 800 | 117 | 234 | 351 | 585 | 877.5 | 1170 | 94.6 | 96.3 | 96.6 | 96.7 | 96.3 | 95.6 | 96.3 | 95.2 | 96.8 | 97.3 | 97.3 | 96.9 | 96.3 | 96.9 | 95.3 | 96.9 | 97.4 | 97.4 | 97 | 96.5 | 97
ABB | ULTRA-1500-TL-OUTD-2-US-690-x-y-z [690V] | 1500 kW, 690 Vac Utility Interactive Inverter with Medium Voltage NEMA TP1 transformer | 1500 | 690 | 96.5 | Y | N | Multiple Listing of Power-One | 373.9 |  |  | 585 | 746 | 800 | 150 | 300 | 450 | 750 | 1125 | 1500 | 94.9 | 96.3 | 96.5 | 96.7 | 96.3 | 95.6 | 96.3 | 95.3 | 96.8 | 97 | 97.2 | 96.9 | 96.3 | 96.9 | 95.4 | 96.9 | 97.2 | 97.4 | 97 | 96.5 | 97
ABB | ULTRA-1500-TL-OUTD-4-US-690-x-y-z [690V] | 1500 kW, 690 Vac Utility Interactive Inverter with Medium Voltage NEMA TP1 transformer | 1500 | 690 | 97 | Y | N | Multiple Listing of Power-One | 430.1 |  |  | 585 | 746 | 800 | 150 | 300 | 450 | 750 | 1125 | 1500 | 94.9 | 96.5 | 96.8 | 97 | 96.5 | 95.8 | 96.5 | 95.4 | 97 | 97.3 | 97.5 | 97.1 | 96.6 | 97.1 | 95.5 | 97.1 | 97.4 | 97.6 | 97.3 | 96.7 | 97.2
ABB | ULTRA-1500-TL-OUTD-1-US-690-x-y-z [690V] | 1500 kW, 690 Vac Utility Interactive Inverter with Medium Voltage NEMA TP1 transformer | 1550 | 690 | 96.5 | Y | N | Multiple Listing of Power-One | 374 |  |  | 585 | 746 | 800 | 156 | 312 | 468 | 780 | 1170 | 1560 | 94.9 | 96.3 | 96.5 | 96.8 | 96.2 | 95.4 | 96.2 | 95.3 | 96.8 | 97.1 | 97.2 | 96.9 | 96.3 | 96.9 | 95.5 | 97 | 97.2 | 97.4 | 97.1 | 96.5 | 97
ABB | ULTRA-1500-TL-OUTD-3-US-690-x-y-z [690V] | 1500 kW, 690 Vac Utility Interactive Inverter with Medium Voltage NEMA TP1 transformer | 1560 | 690 | 97 | Y | N | Multiple Listing of Power-One | 430.1 |  |  | 585 | 746 | 800 | 156 | 312 | 468 | 780 | 1170 | 1560 | 94.9 | 96.5 | 96.8 | 97 | 96.4 | 95.7 | 96.5 | 95.4 | 97 | 97.3 | 97.5 | 97.1 | 96.6 | 97.1 | 95.5 | 97.1 | 97.4 | 97.6 | 97.2 | 96.7 | 97.2
ABB | PVS980-58-1818kVA-I [600V] | 1827 kW Utility Interactive Inverter | 1827.3 | 600 | 97.5 | Y | N | Weighted efficiency includes transformer efficiency of ABB JC04770. | 231.8 |  |  | 850 | 975 | 1100 | 182.73 | 365.46 | 548.19 | 913.65 | 1370.48 | 1827.3 | 96.15 | 97.62 | 97.94 | 97.98 | 97.74 | 97.35 | 97.72 | 95.5 | 97.18 | 97.56 | 97.64 | 97.39 | 97 | 97.36 | 95.16 | 97.03 | 97.44 | 97.54 | 97.3 | 96.93 | 97.25 |  | 2018-05-01
ABB | PVS980-58-2000kVA-K [660V] | 2000 kW Utility Interactive Inverter | 2027.06 | 660 | 97.5 | Y | N | Weighted efficiency includes transformer efficiency of ABB JC04770. | 230.9 |  |  | 935 | 1018 | 1100 | 202.71 | 405.41 | 608.12 | 1013.53 | 1520.3 | 2027.06 | 96.11 | 97.63 | 97.98 | 98.06 | 97.83 | 97.44 | 97.8 | 95.51 | 97.23 | 97.64 | 97.74 | 97.51 | 97.14 | 97.46 | 95.41 | 97.16 | 97.57 | 97.66 | 97.46 | 97.07 | 97.4 |  | 2018-05-01
Ablerex Electronics | ES 2200-US-240 [240V] | 2110 W, 240 Vac Utility Interactive Inverter | 2.11 | 240 | 94.5 | Y | N |  | 0.25 |  |  | 100 | 375 | 400 | 0.21 | 0.42 | 0.63 | 1.06 | 1.58 | 2.11 | 85.3 | 91.6 | 92.9 | 94.3 | 94.6 | 94.5 | 93.8 | 82.1 | 91.9 | 94.2 | 95.6 | 96.1 | 96.4 | 95 | 82.2 | 91.5 | 93.8 | 95.6 | 96.1 | 96.3 | 95
Ablerex Electronics | ES 3300-US-240 [240V] | 3180 W, 240 Vac Utility Interactive Inverter | 3.18 | 240 | 95 | Y | N |  | 0.25 |  |  | 100 | 375 | 400 | 0.32 | 0.64 | 0.95 | 1.59 | 2.39 | 3.18 | 88.8 | 92.9 | 94.1 | 94.6 | 94.3 | 94 | 94 | 88.8 | 94.4 | 95.3 | 96.2 | 96.3 | 95.9 | 95.7 | 89.5 | 93.7 | 95.3 | 96.2 | 96.3 | 96.1 | 95.7
Ablerex Electronics | ES 4200-US-240 [240V] | 4100W, 240 Vac Utility Interactive Inverter | 4.16 | 240 | 95.5 | Y | N |  | 0.2 |  |  | 100 | 380 | 400 | 0.42 | 0.83 | 1.25 | 2.08 | 3.12 | 4.16 | 90.6 | 93.8 | 94.5 | 94.8 | 94.6 | 94.2 | 94.4 | 91.4 | 95 | 95.7 | 96.1 | 96.2 | 95.9 | 95.9 | 90.7 | 94.7 | 95.5 | 96.1 | 96.1 | 95.9 | 95.7
Ablerex Electronics | ES 4200-US-240A [240V] | 4160W, 240 Vac Utility Interactive Inverter | 4.16 | 240 | 95.5 | Y | N |  | 0.2 |  |  | 100 | 380 | 400 | 0.42 | 0.83 | 1.25 | 2.08 | 3.12 | 4.16 | 90.6 | 93.8 | 94.5 | 94.8 | 94.6 | 94.2 | 94.4 | 91.4 | 95 | 95.7 | 96.1 | 96.2 | 95.9 | 95.9 | 90.7 | 94.7 | 95.5 | 96.1 | 96.1 | 95.9 | 95.7
Ablerex Electronics | ES 5000-US-240 [240V] | 5000 W, 240 Vac Utility Interactive Inverter | 5.24 | 240 | 95.5 | Y | N |  | 0.2 |  |  | 100 | 380 | 400 | 0.52 | 1.05 | 1.57 | 2.62 | 3.93 | 5.24 | 91.8 | 94.1 | 94.6 | 94.7 | 94.3 | 93.5 | 94.3 | 92.5 | 95.1 | 96.1 | 96.2 | 95.9 | 95.6 | 95.8 | 92.3 | 95.3 | 95.8 | 96.1 | 95.9 | 95.5 | 95.8
Ablerex Electronics | ES 5000-US-240A [240V] | 5000 W, 240 Vac Utility Interactive Inverter | 5.24 | 240 | 95.5 | Y | N |  | 0.2 |  |  | 100 | 380 | 400 | 0.52 | 1.05 | 1.57 | 2.62 | 3.93 | 5.24 | 91.8 | 94.1 | 94.6 | 94.7 | 94.3 | 93.5 | 94.3 | 92.5 | 95.1 | 96.1 | 96.2 | 95.9 | 95.6 | 95.8 | 92.3 | 95.3 | 95.8 | 96.1 | 95.9 | 95.5 | 95.8
Advanced Energy Industries | AE_3TL-12_10 [480V] | 12 kW, 480 Vac string Inverter | 12 | 480 | 97.5 | N | N |  | 0.47 |  |  | 450 | 720 | 900 | 1.2 | 2.4 | 3.6 | 6 | 9 | 12 | 93.2 | 96 | 96.5 | 97.3 | 97.4 | 97.3 | 97 | 93.9 | 97 | 97 | 97.8 | 98 | 98.1 | 97.6 | 93 | 96.7 | 96.4 | 97.4 | 97.6 | 97.8 | 97.2
Advanced Energy Industries | AE_3TL-12_10-08 [480V] | 12 kW, 480 Vac string Inverter | 12 | 480 | 97.5 | Y | N |  | 0.47 |  |  | 450 | 720 | 900 | 1.2 | 2.4 | 3.6 | 6 | 9 | 12 | 93.2 | 96 | 96.5 | 97.3 | 97.4 | 97.3 | 97 | 93.9 | 97 | 97 | 97.8 | 98 | 98.1 | 97.6 | 93 | 96.7 | 96.4 | 97.4 | 97.6 | 97.8 | 97.2
Advanced Energy Industries | AE_3TL-12_6 [480V] | 12 kW, 480 Vac string Inverter | 12 | 480 | 97.5 | N | N |  | 0.47 |  |  | 450 | 720 | 900 | 1.2 | 2.4 | 3.6 | 6 | 9 | 12 | 93.2 | 96 | 96.5 | 97.3 | 97.4 | 97.3 | 97 | 93.9 | 97 | 97 | 97.8 | 98 | 98.1 | 97.6 | 93 | 96.7 | 96.4 | 97.4 | 97.6 | 97.8 | 97.2
Advanced Energy Industries | AE_3TL-G3_12_10 [480V] | 12 kW, 480 Vac string Inverter | 12 | 480 | 97.5 | N | N |  | 0.47 |  |  | 450 | 720 | 900 | 1.2 | 2.4 | 3.6 | 6 | 9 | 12 | 93.2 | 96 | 96.5 | 97.3 | 97.4 | 97.3 | 97 | 93.9 | 97 | 97 | 97.8 | 98 | 98.1 | 97.6 | 93 | 96.7 | 96.4 | 97.4 | 97.6 | 97.8 | 97.2
Advanced Energy Industries | AE_3TL-G3_12_10-8 [480V] | 12 kW, 480 Vac string Inverter | 12 | 480 | 97.5 | N | N |  | 0.47 |  |  | 450 | 720 | 900 | 1.2 | 2.4 | 3.6 | 6 | 9 | 12 | 93.2 | 96 | 96.5 | 97.3 | 97.4 | 97.3 | 97 | 93.9 | 97 | 97 | 97.8 | 98 | 98.1 | 97.6 | 93 | 96.7 | 96.4 | 97.4 | 97.6 | 97.8 | 97.2
Advanced Energy Industries | 804R012 [480V] | 12 kW, 480 Vac, 3-phase Utility Interactive Inverter | 12.12 | 480 | 97.5 | Y | N |  | 0.87 |  |  | 450 | 720 | 900 | 1.21 | 2.42 | 3.64 | 6.06 | 9.09 | 12.12 | 94.9 | 96.1 | 96.9 | 97.4 | 97.5 | 97.3 | 97.2 | 96 | 96.5 | 97.4 | 97.9 | 98.1 | 98.1 | 97.8 | 95.2 | 95.9 | 96.8 | 97.4 | 97.6 | 97.7 | 97.3
Advanced Energy Industries | AE_3TL-12_6-08 [480V] | 12 kW, 480 Vac string Inverter | 12.12 | 480 | 97.5 | Y | N |  | 0.87 |  |  | 450 | 720 | 900 | 1.21 | 2.42 | 3.64 | 6.06 | 9.09 | 12.12 | 94.9 | 96.1 | 96.9 | 97.4 | 97.5 | 97.3 | 97.2 | 96 | 96.5 | 97.4 | 97.9 | 98.1 | 98.1 | 97.8 | 95.2 | 95.9 | 96.8 | 97.4 | 97.6 | 97.7 | 97.3
Advanced Energy Industries | AE_3TL-G3_12_6 [480V] | 12 kW, 480 Vac string Inverter | 12.12 | 480 | 97.5 | N | N |  | 0.87 |  |  | 450 | 720 | 900 | 1.21 | 2.42 | 3.64 | 6.06 | 9.09 | 12.12 | 94.9 | 96.1 | 96.9 | 97.4 | 97.5 | 97.3 | 97.2 | 96 | 96.5 | 97.4 | 97.9 | 98.1 | 98.1 | 97.8 | 95.2 | 95.9 | 96.8 | 97.4 | 97.6 | 97.7 | 97.3
Advanced Energy Industries | AE_3TL-G3_12_6-08 [480V] | 12 kW, 480 Vac string Inverter | 12.12 | 480 | 97.5 | N | N |  | 0.87 |  |  | 450 | 720 | 900 | 1.21 | 2.42 | 3.64 | 6.06 | 9.09 | 12.12 | 94.9 | 96.1 | 96.9 | 97.4 | 97.5 | 97.3 | 97.2 | 96 | 96.5 | 97.4 | 97.9 | 98.1 | 98.1 | 97.8 | 95.2 | 95.9 | 96.8 | 97.4 | 97.6 | 97.7 | 97.3
Advanced Energy Industries | AE_3TL-16_10 [480V] | 16 kW, 480 Vac string Inverter | 16 | 480 | 97.5 | N | N |  | 0.47 |  |  | 500 | 720 | 900 | 1.6 | 3.2 | 4.8 | 8 | 12 | 16 | 94.9 | 96.4 | 97.2 | 97.6 | 97.5 | 97.4 | 97.3 | 95.3 | 96.7 | 97.5 | 98 | 98 | 98 | 97.8 | 94.7 | 96.1 | 97 | 97.6 | 97.7 | 97.7 | 97.4
Advanced Energy Industries | AE_3TL-16_10-08 [480V] | 16 kW, 480 Vac string Inverter | 16 | 480 | 97.5 | Y | N |  | 0.47 |  |  | 500 | 720 | 900 | 1.6 | 3.2 | 4.8 | 8 | 12 | 16 | 94.9 | 96.4 | 97.2 | 97.6 | 97.5 | 97.4 | 97.3 | 95.3 | 96.7 | 97.5 | 98 | 98 | 98 | 97.8 | 94.7 | 96.1 | 97 | 97.6 | 97.7 | 97.7 | 97.4
Advanced Energy Industries | AE_3TL-16_6 [480V] | 16 kW, 480 Vac string Inverter | 16 | 480 | 97.5 | N | N |  | 0.47 |  |  | 500 | 720 | 900 | 1.6 | 3.2 | 4.8 | 8 | 12 | 16 | 94.9 | 96.4 | 97.2 | 97.6 | 97.5 | 97.4 | 97.3 | 95.3 | 96.7 | 97.5 | 98 | 98 | 98 | 97.8 | 94.7 | 96.1 | 97 | 97.6 | 97.7 | 97.7 | 97.4
Advanced Energy Industries | AE_3TL-G3_16_10 [480V] | 16 kW, 480 Vac string Inverter | 16 | 480 | 97.5 | N | N |  | 0.47 |  |  | 500 | 720 | 900 | 1.6 | 3.2 | 4.8 | 8 | 12 | 16 | 94.9 | 96.4 | 97.2 | 97.6 | 97.5 | 97.4 | 97.3 | 95.3 | 96.7 | 97.5 | 98 | 98 | 98 | 97.8 | 94.7 | 96.1 | 97 | 97.6 | 97.7 | 97.7 | 97.4
Advanced Energy Industries | AE_3TL-G3_16_10-08 [480V] | 16 kW, 480 Vac string Inverter | 16 | 480 | 97.5 | N | N |  | 0.47 |  |  | 500 | 720 | 900 | 1.6 | 3.2 | 4.8 | 8 | 12 | 16 | 94.9 | 96.4 | 97.2 | 97.6 | 97.5 | 97.4 | 97.3 | 95.3 | 96.7 | 97.5 | 98 | 98 | 98 | 97.8 | 94.7 | 96.1 | 97 | 97.6 | 97.7 | 97.7 | 97.4
Advanced Energy Industries | 804R016 [480V] | 16 kW, 480 Vac, 3-phase Utility Interactive Inverter | 16.1 | 480 | 97.5 | Y | N |  | 0.087 |  |  | 500 | 720 | 900 | 1.61 | 3.22 | 4.83 | 8.05 | 12.08 | 16.1 | 96 | 96.8 | 97.4 | 97.6 | 97.6 | 97.4 | 97.5 | 96.6 | 97.3 | 97.7 | 98 | 98.1 | 98 | 97.9 | 95.9 | 96.5 | 97.2 | 97.6 | 97.7 | 97.7 | 97.5
Advanced Energy Industries | AE_3TL-16_6-08 [480V] | 16 kW, 480 Vac string Inverter | 16.1 | 480 | 97.5 | Y | N |  | 0.087 |  |  | 500 | 720 | 900 | 1.61 | 3.22 | 4.83 | 8.05 | 12.08 | 16.1 | 96 | 96.8 | 97.4 | 97.6 | 97.6 | 97.4 | 97.5 | 96.6 | 97.3 | 97.7 | 98 | 98.1 | 98 | 97.9 | 95.9 | 96.5 | 97.2 | 97.6 | 97.7 | 97.7 | 97.5
Advanced Energy Industries | AE_3TL-G3_16_6 [480V] | 16 kW, 480 Vac string Inverter | 16.1 | 480 | 97.5 | N | N |  | 0.09 |  |  | 500 | 720 | 900 | 1.61 | 3.22 | 4.83 | 8.05 | 12.08 | 16.1 | 96 | 96.8 | 97.4 | 97.6 | 97.6 | 97.4 | 97.5 | 96.6 | 97.3 | 97.7 | 98 | 98.1 | 98 | 97.9 | 95.9 | 96.5 | 97.2 | 97.6 | 97.7 | 97.7 | 97.5
Advanced Energy Industries | AE_3TL-G3_16_6-08 [480V] | 16 kW, 480 Vac string Inverter | 16.1 | 480 | 97.5 | N | N |  | 0.09 |  |  | 500 | 720 | 900 | 1.61 | 3.22 | 4.83 | 8.05 | 12.08 | 16.1 | 96 | 96.8 | 97.4 | 97.6 | 97.6 | 97.4 | 97.5 | 96.6 | 97.3 | 97.7 | 98 | 98.1 | 98 | 97.9 | 95.9 | 96.5 | 97.2 | 97.6 | 97.7 | 97.7 | 97.5
Advanced Energy Industries | 804R020 [480V] | 20 kW, 480 Vac, 3-phase Utility Interactive Inverter | 19.65 | 480 | 97.5 | Y | N |  | 0.087 |  |  | 550 | 720 | 900 | 1.97 | 3.93 | 5.9 | 9.83 | 14.74 | 19.65 | 96.5 | 97.3 | 97.7 | 97.8 | 97.7 | 97.5 | 97.6 | 96.7 | 97.5 | 97.9 | 98.1 | 98.1 | 98 | 98 | 96 | 96.6 | 97.2 | 97.6 | 97.6 | 97.5 | 97.4
Advanced Energy Industries | AE_3TL-20_6-08 [480V] | 20 kW, 480 Vac string Inverter | 19.65 | 480 | 97.5 | Y | N |  | 0.087 |  |  | 550 | 720 | 900 | 1.97 | 3.93 | 5.9 | 9.83 | 14.74 | 19.65 | 96.5 | 97.3 | 97.7 | 97.8 | 97.7 | 97.5 | 97.6 | 96.7 | 97.5 | 97.9 | 98.1 | 98.1 | 98 | 98 | 96 | 96.6 | 97.2 | 97.6 | 97.6 | 97.5 | 97.4
Advanced Energy Industries | AE_3TL-G3_20_6 [480V] | 20 kW, 480 Vac string Inverter | 19.65 | 480 | 97.5 | N | N |  | 0.09 |  |  | 550 | 720 | 900 | 1.97 | 3.93 | 5.9 | 9.83 | 14.74 | 19.65 | 96.5 | 97.3 | 97.7 | 97.8 | 97.7 | 97.5 | 97.6 | 96.7 | 97.5 | 97.9 | 98.1 | 98.1 | 98 | 98 | 96 | 96.6 | 97.2 | 97.6 | 97.6 | 97.5 | 97.4
Advanced Energy Industries | AE_3TL-G3_20_6-08 [480V] | 20 kW, 480 Vac string Inverter | 19.65 | 480 | 97.5 | N | N |  | 0.09 |  |  | 550 | 720 | 900 | 1.97 | 3.93 | 5.9 | 9.83 | 14.74 | 19.65 | 96.5 | 97.3 | 97.7 | 97.8 | 97.7 | 97.5 | 97.6 | 96.7 | 97.5 | 97.9 | 98.1 | 98.1 | 98 | 98 | 96 | 96.6 | 97.2 | 97.6 | 97.6 | 97.5 | 97.4
Advanced Energy Industries | AE_3TL-20_10 [480V] | 20 kW, 480 Vac string Inverter | 20 | 480 | 97.5 | N | N |  | 0.47 |  |  | 550 | 720 | 900 | 2 | 4 | 6 | 10 | 15 | 20 | 95.4 | 96.6 | 97.4 | 97.7 | 97.7 | 97.5 | 97.5 | 95.9 | 96.8 | 97.7 | 98 | 98.1 | 98 | 97.9 | 94.8 | 96.2 | 97.1 | 97.6 | 97.7 | 97.6 | 97.4
Advanced Energy Industries | AE_3TL-20_10-08 [480V] | 20 kW, 480 Vac string Inverter | 20 | 480 | 97.5 | Y | N |  | 0.47 |  |  | 550 | 720 | 900 | 2 | 4 | 6 | 10 | 15 | 20 | 95.4 | 96.6 | 97.4 | 97.7 | 97.7 | 97.5 | 97.5 | 95.9 | 96.8 | 97.7 | 98 | 98.1 | 98 | 97.9 | 94.8 | 96.2 | 97.1 | 97.6 | 97.7 | 97.6 | 97.4
Advanced Energy Industries | AE_3TL-20_6 [480V] | 20 kW, 480 Vac string Inverter | 20 | 480 | 97.5 | N | N |  | 0.47 |  |  | 550 | 720 | 900 | 2 | 4 | 6 | 10 | 15 | 20 | 95.4 | 96.6 | 97.4 | 97.7 | 97.7 | 97.5 | 97.5 | 95.9 | 96.8 | 97.7 | 98 | 98.1 | 98 | 97.9 | 94.8 | 96.2 | 97.1 | 97.6 | 97.7 | 97.6 | 97.4
Advanced Energy Industries | AE_3TL-G3_20_10 [480V] | 20 kW, 480 Vac string Inverter | 20 | 480 | 97.5 | N | N |  | 0.47 |  |  | 550 | 720 | 900 | 2 | 4 | 6 | 10 | 15 | 20 | 95.4 | 96.6 | 97.4 | 97.7 | 97.7 | 97.5 | 97.5 | 95.9 | 96.8 | 97.7 | 98 | 98.1 | 98 | 97.9 | 94.8 | 96.2 | 97.1 | 97.6 | 97.7 | 97.6 | 97.4
Advanced Energy Industries | AE_3TL-G3_20_10-08 [480V] | 20 kW, 480 Vac string Inverter | 20 | 480 | 97.5 | N | N |  | 0.47 |  |  | 550 | 720 | 900 | 2 | 4 | 6 | 10 | 15 | 20 | 95.4 | 96.6 | 97.4 | 97.7 | 97.7 | 97.5 | 97.5 | 95.9 | 96.8 | 97.7 | 98 | 98.1 | 98 | 97.9 | 94.8 | 96.2 | 97.1 | 97.6 | 97.7 | 97.6 | 97.4
Advanced Energy Industries | AE_3TL-23_10 [480V] | 23 kW, 480 Vac string Inverter | 20.04 | 480 | 98 | N | N |  | 0.47 |  |  | 600 | 720 | 900 | 2 | 4 | 6 | 10 | 15 | 20 | 96.6 | 97.4 | 97.8 | 98 | 97.9 | 97.6 | 97.8 | 96.9 | 97.5 | 97.9 | 98.1 | 98 | 97.9 | 98 | 96.3 | 97 | 97.5 | 97.8 | 97.7 | 97.5 | 97.6
Advanced Energy Industries | AE_3TL-23_10-08 [480V] | 23 kW, 480 Vac string Inverter | 20.04 | 480 | 98 | Y | N |  | 0.47 |  |  | 600 | 720 | 900 | 2 | 4.01 | 6.01 | 10.02 | 15.03 | 20.04 | 96.6 | 97.4 | 97.8 | 98 | 97.9 | 97.6 | 97.8 | 96.9 | 97.5 | 97.9 | 98.1 | 98 | 97.9 | 98 | 96.3 | 97 | 97.5 | 97.8 | 97.7 | 97.5 | 97.6
Advanced Energy Industries | 804R024 [480V] | 22.2 kW, 480 Vac, 3-phase Utility Interactive Inverter | 22.23 | 480 | 98 | Y | N |  | 0.49 |  |  | 600 | 720 | 900 | 2.22 | 4.45 | 6.67 | 11.12 | 16.67 | 22.23 | 97.2 | 97.7 | 97.9 | 97.9 | 97.8 | 97.6 | 97.8 | 97.3 | 97.7 | 98 | 98.1 | 98 | 97.8 | 98 | 96.7 | 97.1 | 97.5 | 97.7 | 97.6 | 97.5 | 97.6
Advanced Energy Industries | AE_3TL-23_06 [480V] | 23 kW, 480 Vac string Inverter | 22.23 | 480 | 98 | N | N |  | 0.49 |  |  | 600 | 720 | 900 | 2.2 | 4.4 | 6.7 | 11.1 | 16.7 | 22.2 | 97.2 | 97.7 | 97.9 | 97.9 | 97.8 | 97.6 | 97.8 | 97.3 | 97.7 | 98 | 98.1 | 98 | 97.8 | 98 | 96.7 | 97.1 | 97.5 | 97.7 | 97.6 | 97.5 | 97.6
Advanced Energy Industries | AE_3TL-23_6-08 [480V] | 23 kW, 480 Vac string Inverter | 22.23 | 480 | 98 | Y | N |  | 0.49 |  |  | 600 | 720 | 900 | 2.22 | 4.45 | 6.67 | 11.12 | 16.67 | 22.23 | 97.2 | 97.7 | 97.9 | 97.9 | 97.8 | 97.6 | 97.8 | 97.3 | 97.7 | 98 | 98.1 | 98 | 97.8 | 98 | 96.7 | 97.1 | 97.5 | 97.7 | 97.6 | 97.5 | 97.6
Advanced Energy Industries | AE 35TX-208 [208V] | 35 kW, 208 Vac, 3-Phase Utility Interactive Inverter | 35 | 208 | 95.5 | Y | N |  | 38.63 |  |  | 295 | 341 | 480 | 3.5 | 7 | 10.5 | 17.5 | 26.25 | 35 | 93.3 | 95.6 | 96.2 | 96.2 | 95.8 | 95.3 | 95.8 | 92.6 | 95.3 | 95.9 | 95.9 | 95.6 | 95.1 | 95.5 | 90.5 | 94.1 | 94.9 | 95.1 | 94.9 | 94.5 | 94.7
Advanced Energy Industries | AE 35TX-480 [480V] | 35 kW, 480 Vac, 3-Phase Utility Interactive Inverter | 35 | 480 | 96 | Y | N |  | 37.79 |  |  | 295 | 341 | 480 | 3.5 | 7 | 10.5 | 17.5 | 26.25 | 35 | 94.1 | 96.4 | 96.9 | 97 | 96.8 | 96.3 | 96.7 | 93.3 | 95.9 | 96.5 | 96.7 | 96.5 | 96 | 96.4 | 91.1 | 94.7 | 95.4 | 95.7 | 95.6 | 95.2 | 95.3
Advanced Energy Industries | AE 35TX-600 [600V] | 35 kW, 600 Vac, 3-Phase Utility Interactive Inverter | 35 | 600 | 95.5 | Y | N |  | 37.27 |  |  | 295 | 341 | 480 | 3.5 | 7 | 10.5 | 17.5 | 26.25 | 35 | 93.6 | 95.9 | 96.3 | 96.4 | 96.1 | 95.7 | 96.1 | 93 | 95.5 | 96 | 96.1 | 96 | 95.6 | 95.8 | 91 | 94.5 | 95.1 | 95.4 | 95.3 | 95 | 95.1
Advanced Energy Industries | AE 50TX-208 [208V] | 50 kW, 208 Vac, 3-Phase Utility Interactive Inverter with 295-600 Vdc input | 50 | 208 | 96 | Y | N |  | 33 |  |  | 295 | 341 | 480 | 5 | 10 | 15 | 25 | 37.5 | 50 | 95 | 96.7 | 96.6 | 96.6 | 96 | 95.3 | 96.2 | 94.4 | 96.3 | 96.3 | 96.3 | 95.8 | 95.2 | 95.9 | 92.7 | 95.5 | 95.4 | 95.6 | 95.2 | 94.7 | 95.2
Advanced Energy Industries | AE 50TX-480 [480V] | 50 kW, 480 Vac, 3-Phase Utility Interactive Inverter with 295-600 Vdc input | 50 | 480 | 96 | Y | N |  | 33 |  |  | 295 | 341 | 480 | 5 | 10 | 15 | 25 | 37.5 | 50 | 95.7 | 96.8 | 97.2 | 97 | 96.4 | 95.9 | 96.6 | 95.2 | 96.5 | 97 | 96.8 | 96.2 | 95.8 | 96.4 | 93.8 | 95.6 | 96.3 | 96 | 95.6 | 95.3 | 95.7
Advanced Energy Industries | AE 50TX-600 [600V] | 50 kW, 600 Vac, 3-Phase Utility Interactive Inverter | 50 | 600 | 96 | Y | N |  | 43 |  |  | 295 | 341 | 480 | 5 | 10 | 15 | 25 | 37.5 | 50 | 94.2 | 96.2 | 96.6 | 96.6 | 96.2 | 95.7 | 96.2 | 93.6 | 95.9 | 96.3 | 96.3 | 96 | 95.6 | 95.9 | 91.6 | 94.8 | 95.4 | 95.5 | 95.3 | 95 | 95.1
Advanced Energy Industries | AE 75TX-208 [208V] | 75 kW, 208 Vac, 3-Phase Utility Interactive Inverter with 295-600 Vdc input | 75 | 208 | 95.5 | Y | N |  | 50 |  |  | 295 | 341 | 480 | 7.5 | 15 | 22.5 | 37.5 | 56.25 | 75 | 92.7 | 95.6 | 96.1 | 96 | 95.9 | 95.6 | 95.8 | 92 | 95.2 | 95.8 | 95.8 | 95.7 | 95.3 | 95.5 | 89.8 | 93.8 | 94.8 | 94.9 | 95 | 94.6 | 94.6
Advanced Energy Industries | AE 75TX-480 [480V] | 75 kW, 480 Vac, 3-Phase Utility Interactive Inverter with 295-600 Vdc input | 75 | 480 | 95.5 | Y | N |  | 50 |  |  | 295 | 341 | 480 | 7.5 | 15 | 22.5 | 37.5 | 56.25 | 75 | 92.7 | 95.6 | 96.2 | 96.6 | 96.4 | 96.1 | 96.2 | 91.9 | 95 | 95.6 | 96.3 | 96.1 | 95.8 | 95.9 | 89.2 | 93.3 | 94.1 | 95.2 | 95.1 | 95 | 94.6
Advanced Energy Industries | AE 75TX-600 [600V] | 75 kW, 600 Vac, 3-Phase Utility Interactive Inverter | 75 | 600 | 96 | Y | N |  | 105.8 |  |  | 295 | 341 | 480 | 7.5 | 15 | 22.5 | 37.5 | 56.25 | 75 | 92.3 | 95.5 | 96.2 | 96.5 | 96.5 | 96.2 | 96.2 | 91.5 | 95.1 | 95.9 | 96.3 | 96.3 | 96.1 | 96 | 89.4 | 93.9 | 95 | 95.5 | 95.7 | 95.6 | 95.3
Advanced Energy Industries | AE 100TX-208 [208V] | 100 kW, 208 Vac, 3-Phase Utility Interactive Inverter with 295-600 Vdc input | 100 | 208 | 95.5 | Y | N |  | 42 |  |  | 295 | 341 | 480 | 10 | 20 | 30 | 50 | 75 | 100 | 94.2 | 96.4 | 96.3 | 96.3 | 95.8 | 95.2 | 95.9 | 93.6 | 96 | 96.1 | 96.1 | 95.7 | 95.1 | 95.7 | 91.7 | 95 | 95.2 | 95.3 | 95.1 | 94.6 | 95
Advanced Energy Industries | AE 100TX-480 [480V] | 100 kW, 480 Vac 3-Phase Utility Interactive Inverter with 295-600 Vdc input | 100 | 480 | 96 | Y | N |  | 36 |  |  | 295 | 341 | 480 | 10 | 20 | 30 | 50 | 75 | 100 | 94.4 | 96.6 | 97.1 | 97 | 96.2 | 95.8 | 96.4 | 93.7 | 96.2 | 96.8 | 96.7 | 96 | 95.6 | 96.1 | 91.9 | 95 | 95.9 | 96 | 95.2 | 94.9 | 95.3
Advanced Energy Industries | AE 100TX-600 [600V] | 100 kW, 600 Vac, 3-Phase Utility Interactive Inverter | 100 | 600 | 96 | Y | N |  | 99.56 |  |  | 295 | 341 | 480 | 10 | 20 | 30 | 50 | 75 | 100 | 93.8 | 96.1 | 96.5 | 96.6 | 96.3 | 95.9 | 96.3 | 93.2 | 95.8 | 96.3 | 96.4 | 96.1 | 95.8 | 96.1 | 91.5 | 94.8 | 95.5 | 95.8 | 95.6 | 95.2 | 95.4
Advanced Energy Industries | AE 250TX-480 [480V] | 250 kW, 480 Vac, 3-Phase Utility Interactive Inverter | 249.5 | 480 | 96.5 | Y | N |  | 54.14 |  |  | 295 | 341 | 480 | 24.95 | 49.9 | 74.85 | 124.8 | 187.1 | 249.5 | 96 | 97 | 96.9 | 96.9 | 96.6 | 96.1 | 96.7 | 95.6 | 96.6 | 96.7 | 96.8 | 96.4 | 96 | 96.5 | 94.7 | 95.8 | 96.2 | 96.2 | 95.9 | 95.4 | 95.9
Advanced Energy Industries | AE 250TX-600 [600V] | 250 kW, 600 Vac, 3-Phase Utility Interactive Inverter | 249.5 | 600 | 96.5 | Y | N |  | 101 |  |  | 295 | 341 | 480 | 24.95 | 49.9 | 74.85 | 124.8 | 187.1 | 249.5 | 95.2 | 96.8 | 97.1 | 97.1 | 96.8 | 96.4 | 96.8 | 94.8 | 96.5 | 96.8 | 96.9 | 96.6 | 96.3 | 96.6 | 93.4 | 95.6 | 96.1 | 96.2 | 96 | 95.7 | 95.9
Advanced Energy Industries | AE 250NX (3159200-XXXX) [480V] | 250 kW, 480 Vac, 3-phase Utility Interactive Inverter | 250 | 480 | 97.5 | N | N |  | 60 |  |  | 660 | 740 | 960 | 25 | 50 | 75 | 125 | 187.5 | 250 | 96 | 97.7 | 98.1 | 98.1 | 98 | 97.7 | 97.9 | 95.5 | 97.3 | 97.7 | 97.8 | 97.8 | 97.5 | 97.6 | 92.8 | 95.8 | 96.4 | 96.9 | 96.8 | 96.7 | 96.6
Advanced Energy Industries | Solaron 250 kW (3159200-XXXX) [480V] | 250 kW, 480 Vac, 3-phase Utility Interactive Inverter | 250 | 480 | 97.5 | N | N |  | 60 |  |  | 660 | 740 | 960 | 25 | 50 | 75 | 125 | 187.5 | 250 | 95.98 | 97.75 | 98.11 | 98.11 | 98.02 | 97.75 | 97.94 | 95.47 | 97.33 | 97.74 | 97.82 | 97.76 | 97.55 | 97.65 | 92.81 | 95.79 | 96.4 | 96.91 | 96.81 | 96.66 | 96.56
Advanced Energy Industries | AE 260TX-480 [480V] | 260 kW, 480 Vac, 3-Phase Utility Interactive Inverter with 295-600 Vdc input | 260 | 480 | 97 | Y | N |  | 67 |  |  | 295 | 341 | 480 | 26 | 52 | 78 | 130 | 195 | 260 | 96 | 97.5 | 97.7 | 97.6 | 97.1 | 96.4 | 97.2 | 95.6 | 97.3 | 97.5 | 97.4 | 97 | 96.4 | 97 | 94.4 | 96.5 | 96.9 | 97 | 96.6 | 96.1 | 96.6
Advanced Energy Industries | AE 260TX-480-LV [480V] | 260 kW, 480 Vac, 3-Phase Utility Interactive Inverter with 265-600 Vdc input | 260 | 480 | 96.5 | Y | N |  | 67 |  |  | 265 | 319 | 480 | 26 | 52 | 78 | 130 | 195 | 260 | 96.1 | 97.6 | 97.8 | 97.5 | 96.9 | 96 | 97.1 | 95.6 | 97.3 | 97.5 | 97.3 | 96.7 | 95.9 | 96.9 | 94 | 96.2 | 96.7 | 96.8 | 96.2 | 95.5 | 96.3
Advanced Energy Industries | AE 333NX (3159000-XXXX) [480V] | 333 kW, 480 Vac, 3-phase Utility Interactive Inverter | 333 | 480 | 97.5 | N | N |  | 60 |  |  | 660 | 740 | 960 | 33.3 | 66.6 | 99.9 | 166.5 | 249.8 | 333 | 96.6 | 98 | 98.3 | 98.2 | 98 | 97.5 | 98 | 95.8 | 97.5 | 97.8 | 97.8 | 97.6 | 97.4 | 97.6 | 94.5 | 96.6 | 97 | 97 | 96.7 | 96.3 | 96.7
Advanced Energy Industries | Solaron 333 kW (3159000-XXXX) [480V] | 333 kW, 480 Vac, 3-phase Utility Interactive Inverter | 333 | 480 | 97.5 | N | N |  | 60 |  |  | 660 | 740 | 960 | 33.3 | 66.6 | 99.9 | 166.5 | 249.8 | 333 | 96.59 | 98.03 | 98.28 | 98.23 | 98.01 | 97.48 | 98.01 | 95.8 | 97.52 | 97.84 | 97.85 | 97.62 | 97.36 | 97.6 | 94.47 | 96.6 | 97.01 | 97.01 | 96.73 | 96.3 | 96.7
Advanced Energy Industries | AE 500NX (3159500-XXXX) [480V] | 500 kW, 480 Vac, 3-phase Utility Interactive Inverter | 500 | 480 | 97.5 | N | N |  | 85 |  |  | 660 | 740 | 960 | 50 | 100 | 150 | 250 | 375 | 500 | 98 | 98.5 | 98.5 | 98.3 | 97.8 | 97 | 98 | 97.3 | 98 | 98.1 | 97.9 | 97.6 | 97 | 97.7 | 95.8 | 96.9 | 97 | 96.8 | 96.2 | 95.5 | 96.4
Advanced Energy Industries | AE 500NX-HE (3159502-XXXX) [480V] | 500 kW, 480 Vac, 3-phase Utility Interactive Inverter | 500 | 480 | 98 | N | N |  | 88 |  |  | 660 | 740 | 960 | 50 | 100 | 150 | 250 | 375 | 500 | 97.4 | 98.6 | 98.7 | 98.7 | 98.4 | 97.9 | 98.4 | 96.7 | 98 | 98.3 | 98.3 | 98.2 | 97.9 | 98.1 | 94.9 | 96.9 | 97.3 | 97.3 | 97.2 | 96.7 | 97.1
Advanced Energy Industries | AE 500TX-480 [480V] | 500 kW, 480 Vac, 3-phase Utility Interactive Inverter | 500 | 480 | 97 | N | N |  | 58 |  |  | 310 | 353 | 480 | 50 | 100 | 150 | 250 | 375 | 500 | 96.98 | 97.76 | 97.82 | 97.66 | 97.22 | 96.7 | 97.37 | 96.68 | 97.54 | 97.59 | 97.42 | 97.02 | 96.49 | 97.16 | 95.74 | 96.84 | 96.96 | 96.82 | 96.47 | 95.98 | 96.57
Advanced Energy Industries | AE 500TX-600 [600V] | 500 kW, 600 Vac, 3-phase Utility Interactive Inverter | 500 | 600 | 97 | N | N |  | 69.04 |  |  | 310 | 353 | 480 | 50 | 100 | 150 | 250 | 375 | 500 | 96.4 | 97.3 | 97.4 | 97.3 | 96.8 | 96.3 | 97 | 96.1 | 97.1 | 97.2 | 97.1 | 96.7 | 96.3 | 96.8 | 95 | 96.5 | 96.7 | 96.7 | 96.4 | 96 | 96.5
Advanced Energy Industries | Solaron 500 HE (3159502-XXXX) [480V] | 500 kW, 480 Vac, 3-phase Utility Interactive Inverter | 500 | 480 | 98 | N | N |  | 88 |  |  | 660 | 740 | 960 | 50 | 100 | 150 | 250 | 375 | 500 | 97.4 | 98.6 | 98.7 | 98.7 | 98.4 | 97.9 | 98.4 | 96.7 | 98 | 98.3 | 98.3 | 98.2 | 97.9 | 98.1 | 94.9 | 96.9 | 97.3 | 97.3 | 97.2 | 96.7 | 97.1
Advanced Energy Industries | Solaron 500kW (3159500-XXXX) [480V] | 500 kW, 480 Vac, 3-phase Utility Interactive Inverter | 500 | 480 | 97.5 | N | N |  | 85 |  |  | 660 | 740 | 960 | 50 | 100 | 150 | 250 | 375 | 500 | 97.99 | 98.49 | 98.52 | 98.33 | 97.79 | 97.02 | 97.99 | 97.32 | 97.99 | 98.08 | 97.89 | 97.65 | 97.05 | 97.73 | 95.79 | 96.9 | 97 | 96.77 | 96.16 | 95.5 | 96.38
Advanced Energy Industries | AE 1000NX (3159700-XXXX) | Utility Interactive Photovoltaic Inverter | 1000 |  | 98 | Y | N |  | 192.8 |  |  | 1100 | 1230 | 1600 | 100 | 200 | 300 | 500 | 750 | 1000 | 94.3 | 96.9 | 97.7 | 98.1 | 98.1 | 98.1 | 97.9 | 95.4 | 97.3 | 97.8 | 98.1 | 98.1 | 98.1 | 97.9 | 94.6 | 96.8 | 97.3 | 97.7 | 97.8 | 97.7 | 97.5
Advanced Solar Photonics | PV240 [208V] | 3.7 kW, 208 Vac Utility Interactive Inverter | 3.69 | 208 | 97 | Y | N |  | 0.21 |  |  | 100 | 360 | 470 | 0.37 | 0.74 | 1.11 | 1.85 | 2.77 | 3.69 | 94.7 | 96.6 | 97.3 | 97.7 | 97.6 | 97.4 | 97.4 | 94.1 | 96.4 | 97.2 | 97.6 | 97.5 | 97.4 | 97.3 | 92.5 | 95.5 | 96.6 | 97.2 | 97.2 | 97.2 | 96.9
Advanced Solar Photonics | PV240 [240V] | 4 kW, 240 Vac Utility Interactive Inverter | 3.98 | 240 | 97 | Y | N |  | 0.16 |  |  | 100 | 360 | 450 | 0.398 | 0.796 | 1.194 | 1.99 | 2.985 | 3.98 | 92 | 95.13 | 96.3 | 97.03 | 97 | 96.87 | 96.62 | 94.07 | 96.5 | 97.41 | 97.32 | 97.09 | 97.69 | 97.06 | 92.29 | 95.79 | 96.93 | 97.46 | 97.63 | 97.59 | 97.2
Advanced Solar Photonics | PV240 [277V] | 4 kW, 277 Vac Utility Interactive Inverter | 3.98 | 277 | 97 | Y | N |  | 0.11 |  |  | 100 | 360 | 450 | 0.398 | 0.796 | 1.194 | 1.99 | 2.985 | 3.98 | 90.72 | 94.5 | 95.98 | 96.87 | 97.03 | 96.96 | 96.49 | 92.75 | 95.85 | 96.88 | 97.51 | 97.66 | 97.62 | 97.25 | 93.04 | 96.04 | 97.18 | 97.87 | 98.02 | 97.89 | 97.59
Advanced Solar Photonics | PV250 [208V] | 4.5 kW, 208 Vac Utility Interactive Inverter | 4.47 | 208 | 97 | Y | N |  | 0.07 |  |  | 100 | 360 | 470 | 0.45 | 0.89 | 1.34 | 2.24 | 3.35 | 4.47 | 94.5 | 96.9 | 97.5 | 97.7 | 97.6 | 97.4 | 97.4 | 94 | 96.6 | 97.2 | 97.5 | 97.5 | 97.3 | 97.2 | 92.6 | 95.4 | 96.3 | 97.1 | 97.2 | 97.1 | 96.8
Advanced Solar Photonics | PV250 [240V] | 4.8 kW, 240 Vac Utility Interactive Inverter | 4.83 | 240 | 97 | Y | N |  | 0.12 |  |  | 100 | 360 | 450 | 0.48 | 0.97 | 1.45 | 2.42 | 3.62 | 4.83 | 92.8 | 95.8 | 96.6 | 96.9 | 96.9 | 96.8 | 96.6 | 94.7 | 96.8 | 97.2 | 97.7 | 97.5 | 97.6 | 97.4 | 93.2 | 96.3 | 97 | 97.5 | 97.5 | 97.5 | 97.2
Advanced Solar Photonics | PV250 [277V] | 4.8 kW, 277 Vac Utility Interactive Inverter | 4.83 | 277 | 97 | Y | N |  | 0.09 |  |  | 100 | 360 | 450 | 0.48 | 0.97 | 1.45 | 2.42 | 3.62 | 4.83 | 91 | 94.4 | 95.7 | 96.6 | 96.9 | 96.9 | 96.3 | 93.3 | 96.3 | 97 | 97.5 | 97.6 | 97.6 | 97.3 | 94 | 96.7 | 97.3 | 97.8 | 97.9 | 97.9 | 97.6
Advanced Solar Photonics | PV260 [208V] | 6 kW, 208 Vac Utility Interactive Inverter | 5.98 | 208 | 97 | Y | N |  | 0.11 |  |  | 100 | 360 | 470 | 0.6 | 1.2 | 1.79 | 2.99 | 4.49 | 5.98 | 95.9 | 97.2 | 97.5 | 97.5 | 97.3 | 97 | 97.3 | 94.9 | 96.9 | 97.4 | 97.4 | 97.3 | 97 | 97.2 | 93 | 96 | 96.6 | 97.1 | 97 | 96.8 | 96.7
Advanced Solar Photonics | PV260 [277V] | 6 kW, 277 Vac Utility Interactive Inverter | 6 | 277 | 97 | Y | N |  | 0.07 |  |  | 100 | 360 | 450 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 91.46 | 94.66 | 95.86 | 96.6 | 96.84 | 96.78 | 96.35 | 93.31 | 96.16 | 96.87 | 97.36 | 97.44 | 97.37 | 97.12 | 94.29 | 96.68 | 97.28 | 97.88 | 97.82 | 97.7 | 97.56
Advanced Solar Photonics | PV260 [240V] | 6 kW, 240 Vac Utility Interactive Inverter | 6.01 | 240 | 97 | Y | N |  | 0.08 |  |  | 100 | 360 | 450 | 0.601 | 1.202 | 1.803 | 3.005 | 4.508 | 6.01 | 93.77 | 96.12 | 96.45 | 96.82 | 96.82 | 96.64 | 96.61 | 95.48 | 97.14 | 97.68 | 97.75 | 97.65 | 97.4 | 97.55 | 93.92 | 96.18 | 97.13 | 97.45 | 97.39 | 97.23 | 97.16
Advanced Solar Photonics | PV270 [208V] | 7 kW, 208 Vac Utility Interactive Inverter | 6.92 | 208 | 97 | Y | N |  | 0.17 |  |  | 100 | 360 | 450 | 0.692 | 1.384 | 2.076 | 3.46 | 5.19 | 6.92 | 94.26 | 96.15 | 96.67 | 96.79 | 96.7 | 96.41 | 96.58 | 95.45 | 96.96 | 97.46 | 97.64 | 97.5 | 97.26 | 97.4 | 93.99 | 96.24 | 96.92 | 97.31 | 97.31 | 97.18 | 97.07
Advanced Solar Photonics | PV270 [240V] | 7 kW, 240 Vac Utility Interactive Inverter | 6.95 | 240 | 97 | Y | N |  | 0.09 |  |  | 100 | 360 | 470 | 0.695 | 1.39 | 2.085 | 3.475 | 5.213 | 6.95 | 96.14 | 97.28 | 97.53 | 97.29 | 96.98 | 96.47 | 97.07 | 95.62 | 97.01 | 97.37 | 97.14 | 96.94 | 96.55 | 96.96 | 93.81 | 95.96 | 96.63 | 96.9 | 96.68 | 96.36 | 96.55
Advanced Solar Photonics | PV270 [277V] | 7 kW, 277 Vac Utility Interactive Inverter | 7.01 | 277 | 97 | Y | N |  | 0.02 |  |  | 100 | 360 | 450 | 0.701 | 1.402 | 2.103 | 3.505 | 5.258 | 7.01 | 93.35 | 95.87 | 96.55 | 96.76 | 96.63 | 96.41 | 96.46 | 94.76 | 96.57 | 97.16 | 97.45 | 97.1 | 97.06 | 97.06 | 94.91 | 96.87 | 97.37 | 97.75 | 97.6 | 97.43 | 97.45
AE Solar Energy | AE3.8 [208V] | 3.7 kW, 208 Vac Utility Interactive Inverter | 3.69 | 208 | 97 | Y | N |  | 0.21 |  |  | 100 | 360 | 470 | 0.369 | 0.738 | 1.107 | 1.845 | 2.768 | 3.69 | 94.68 | 96.62 | 97.3 | 97.7 | 97.62 | 97.43 | 97.42 | 94.13 | 96.35 | 97.17 | 97.65 | 97.51 | 97.39 | 97.3 | 92.51 | 95.49 | 96.56 | 97.15 | 97.23 | 97.2 | 96.85
AE Solar Energy | AE3.8 [240V] | 3.7 kW, 240 Vac Utility Interactive Inverter | 3.71 | 240 | 97 | Y | N |  | 0.06 |  |  | 100 | 360 | 450 | 0.371 | 0.742 | 1.113 | 1.855 | 2.783 | 3.71 | 92 | 95.13 | 96.3 | 97.03 | 97 | 96.87 | 96.62 | 94.07 | 96.5 | 97.41 | 97.32 | 97.09 | 97.69 | 97.06 | 92.29 | 95.79 | 96.93 | 97.46 | 97.63 | 97.59 | 97.2
AE Solar Energy | AE3.8 [277V] | 3.7 kW, 277 Vac Utility Interactive Inverter | 3.71 | 277 | 97 | Y | N |  | 0.14 |  |  | 100 | 360 | 450 | 0.371 | 0.742 | 1.113 | 1.855 | 2.783 | 3.71 | 90.77 | 94.61 | 95.92 | 96.83 | 97.03 | 97.03 | 96.48 | 92.91 | 95.94 | 96.82 | 97.55 | 97.64 | 97.61 | 97.25 | 93.36 | 96.29 | 97.17 | 97.84 | 97.9 | 97.92 | 97.54
AE Solar Energy | AE5.0 [208V] | 4.5 kW, 208 Vac Utility Interactive Inverter | 4.47 | 208 | 97 | Y | N |  | 0.07 |  |  | 100 | 360 | 470 | 0.447 | 0.894 | 1.341 | 2.235 | 3.353 | 4.47 | 94.53 | 96.91 | 97.46 | 97.74 | 97.58 | 97.38 | 97.44 | 94.04 | 96.55 | 97.17 | 97.49 | 97.47 | 97.3 | 97.25 | 92.64 | 95.42 | 96.3 | 97.15 | 97.17 | 97.06 | 96.78
AE Solar Energy | AE5.0 [240V] | 4.8 kW, 240 Vac Utility Interactive Inverter | 4.83 | 240 | 97 | Y | N |  | 0.12 |  |  | 100 | 360 | 450 | 0.483 | 0.966 | 1.449 | 2.415 | 3.623 | 4.83 | 92.83 | 95.8 | 96.65 | 96.94 | 96.86 | 96.76 | 96.63 | 94.65 | 96.82 | 97.23 | 97.75 | 97.55 | 97.65 | 97.4 | 93.23 | 96.3 | 97 | 97.53 | 97.53 | 97.47 | 97.23
AE Solar Energy | AE5.0 [277V] | 4.8 kW, 277 Vac Utility Interactive Inverter | 4.83 | 277 | 97 | Y | N |  | 0.09 |  |  | 100 | 360 | 450 | 0.483 | 0.966 | 1.449 | 2.415 | 3.623 | 4.83 | 90.98 | 94.41 | 95.72 | 96.56 | 96.89 | 96.89 | 96.32 | 93.27 | 96.27 | 97.02 | 97.46 | 97.64 | 97.59 | 97.28 | 94 | 96.65 | 97.32 | 97.8 | 97.9 | 97.9 | 97.59
AE Solar Energy | AE6.0 [208V] | 6 kW, 208 Vac Utility Interactive Inverter | 5.98 | 208 | 97 | Y | N |  | 0.11 |  |  | 100 | 360 | 470 | 0.598 | 1.196 | 1.794 | 2.99 | 4.485 | 5.98 | 95.88 | 97.18 | 97.51 | 97.51 | 97.31 | 96.96 | 97.3 | 94.92 | 96.89 | 97.39 | 97.42 | 97.27 | 96.96 | 97.19 | 93.01 | 95.98 | 96.59 | 97.09 | 96.96 | 96.81 | 96.72
AE Solar Energy | AE6.0 [277V] | 6 kW, 277 Vac Utility Interactive Inverter | 6 | 277 | 97 | Y | N |  | 0.07 |  |  | 100 | 360 | 450 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 91.46 | 94.66 | 95.86 | 96.6 | 96.84 | 96.78 | 96.35 | 93.31 | 96.16 | 96.87 | 97.36 | 97.44 | 97.37 | 97.12 | 94.29 | 96.68 | 97.28 | 97.88 | 97.82 | 97.7 | 97.56
AE Solar Energy | AE6.0 [240V] | 6 kW, 240 Vac Utility Interactive Inverter | 6.01 | 240 | 97 | Y | N |  | 0.08 |  |  | 100 | 360 | 450 | 0.601 | 1.202 | 1.803 | 3.005 | 4.508 | 6.01 | 93.77 | 96.12 | 96.45 | 96.82 | 96.82 | 96.64 | 96.61 | 95.48 | 97.14 | 97.68 | 97.75 | 97.65 | 97.4 | 97.55 | 93.92 | 96.18 | 97.13 | 97.45 | 97.39 | 97.23 | 97.16
AE Solar Energy | AE7.0 [208V] | 7 kW, 208 Vac Utility Interactive Inverter | 6.92 | 208 | 97 | Y | N |  | 0.17 |  |  | 100 | 360 | 450 | 0.692 | 1.384 | 2.076 | 3.46 | 5.19 | 6.92 | 94.26 | 96.15 | 96.67 | 96.79 | 96.7 | 96.41 | 96.58 | 95.45 | 96.96 | 97.46 | 97.64 | 97.5 | 97.26 | 97.4 | 93.99 | 96.24 | 96.92 | 97.31 | 97.31 | 97.18 | 97.07
AE Solar Energy | AE7.0 [240V] | 7 kW, 240 Vac Utility Interactive Inverter | 6.95 | 240 | 97 | Y | N |  | 0.09 |  |  | 100 | 360 | 470 | 0.695 | 1.39 | 2.085 | 3.475 | 5.213 | 6.95 | 96.14 | 97.28 | 97.53 | 97.29 | 96.98 | 96.47 | 97.07 | 95.62 | 97.01 | 97.37 | 97.14 | 96.94 | 96.55 | 96.96 | 93.81 | 95.96 | 96.63 | 96.9 | 96.68 | 96.36 | 96.55
AE Solar Energy | AE7.0 [277V] | 7 kW, 277 Vac Utility Interactive Inverter | 7.01 | 277 | 97 | Y | N |  | 0.02 |  |  | 100 | 360 | 450 | 0.701 | 1.402 | 2.103 | 3.505 | 5.258 | 7.01 | 93.35 | 95.87 | 96.55 | 96.76 | 96.63 | 96.41 | 96.46 | 94.76 | 96.57 | 97.16 | 97.45 | 97.1 | 97.06 | 97.06 | 94.91 | 96.87 | 97.37 | 97.75 | 97.6 | 97.43 | 97.45
AEconversion GMbH | INV250-45US xxxxx [208V] | 250 W, 208 Vac Utility Interactive modular Inverter | 0.24 | 208 | 91.5 | N | Y |  | 0.02 |  |  | 20 | 30 | 40 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 82.9 | 89.7 | 91.7 | 92.8 | 92.7 | 91.9 | 92 | 82.5 | 89.2 | 91.5 | 92.6 | 92.4 | 91.7 | 91.8 | 81.6 | 88.7 | 90.8 | 92.3 | 92 | 91.4 | 91.3
AEconversion GMbH | INV250-45US xxxxx [240V] | 250 W, 240 Vac Utility Interactive modular Inverter | 0.24 | 240 | 92 | N | Y |  | 0.03 |  |  | 20 | 30 | 40 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 82.1 | 89.3 | 91.7 | 93.2 | 93.3 | 92.9 | 92.4 | 81.8 | 88.6 | 91.1 | 92.8 | 93.1 | 92.7 | 92.1 | 80.6 | 87.7 | 90.3 | 92.3 | 92.7 | 92.4 | 91.6
AEconversion GMbH | INV350-60US xxxxx [208V] | 350 W, 208 Vac Utility Interactive modular Inverter | 0.3 | 208 | 91.5 | N | Y |  | 0.02 |  |  | 20 | 35 | 50 | 0.03 | 0.06 | 0.09 | 0.15 | 0.23 | 0.3 | 86.5 | 90.9 | 92.7 | 92.9 | 92.1 | 90.6 | 92 | 85.5 | 90.3 | 92.2 | 92.5 | 91.7 | 90 | 91.5 | 84.2 | 89.4 | 91.4 | 92 | 91.2 | 89.5 | 90.9
AEconversion GMbH | INV350-60US xxxxx [240V] | 350 W, 240 Vac Utility Interactive modular Inverter | 0.3 | 240 | 92.5 | N | Y |  | 0.03 |  |  | 20 | 35 | 50 | 0.03 | 0.06 | 0.09 | 0.15 | 0.23 | 0.3 | 85.9 | 90.9 | 92.8 | 93.7 | 93.4 | 92.2 | 92.9 | 84.9 | 90.1 | 92.2 | 93.2 | 93 | 92.1 | 92.4 | 83.5 | 89.3 | 91.6 | 92.7 | 92.6 | 91.7 | 91.9
AEconversion GMbH | INV500-90US-xxxxx [208V] | 500 W, 208 Vac Utility Interactive modular Inverter, xxxxx are communication variants | 0.48 | 208 | 94 | N | Y |  | 0.028 |  |  | 40 | 60 | 80 | 0.05 | 0.1 | 0.14 | 0.24 | 0.36 | 0.48 | 89.2 | 93.8 | 94.6 | 94.7 | 94.3 | 93.5 | 94.2 | 88.5 | 93.1 | 94.1 | 94.4 | 94 | 93.3 | 93.8 | 87.3 | 92.4 | 93.6 | 94 | 93.7 | 92.9 | 93.4
AEconversion GMbH | INV500-90US-xxxxx [240V] | 500 W, 240 Vac Utility Interactive modular Inverter, xxxxx are communication variants | 0.48 | 240 | 94.5 | N | Y |  | 0.035 |  |  | 40 | 60 | 80 | 0.05 | 0.1 | 0.14 | 0.24 | 0.36 | 0.48 | 89.1 | 93.6 | 94.8 | 95.3 | 95.1 | 94.7 | 94.8 | 88.1 | 93 | 94.3 | 94.9 | 94.8 | 94.4 | 94.4 | 86.9 | 92.4 | 93.9 | 94.6 | 94.5 | 94.1 | 94
AEG Power Solutions | Protect MPV.015.01 [480V] | 15 kW, 480 Vac, 3-phase Utility Interactive Inverter | 15 | 480 | 96.5 | N | N |  | 19 |  |  | 305 | 405 | 595 | 1.5 | 3 | 4.5 | 7.5 | 11.25 | 15 | 94.2 | 95.9 | 95.9 | 96.3 | 96.4 | 96 | 96.2 | 91.1 | 94.8 | 96.2 | 96.3 | 96.9 | 96.6 | 96.3 | 93.8 | 96.1 | 96.4 | 96.9 | 97 | 96.9 | 96.8
AEG Power Solutions | Protect MPV.030.01 [480V] | 30 kW, 480 Vac, 3-phase Utility Interactive Inverter | 30 | 480 | 96.5 | N | N |  | 38 |  |  | 305 | 405 | 595 | 3 | 6 | 9 | 15 | 22.5 | 30 | 94.2 | 95.9 | 95.9 | 96.3 | 96.4 | 96 | 96.2 | 91.1 | 94.8 | 96.2 | 96.3 | 96.9 | 96.6 | 96.3 | 93.8 | 96.1 | 96.4 | 96.9 | 97 | 96.9 | 96.8
AEG Power Solutions | Protect MPV.045.01 [480V] | 45 kW, 480 Vac, 3-phase Utility Interactive Inverter | 44.41 | 480 | 96.5 | N | N |  | 54.94 |  |  | 305 | 405 | 595 | 4.44 | 8.88 | 13.32 | 22.21 | 33.31 | 44.41 | 94.2 | 95.9 | 95.9 | 96.3 | 96.4 | 96 | 96.2 | 91.1 | 94.8 | 96.2 | 96.3 | 96.9 | 96.6 | 96.3 | 93.8 | 96.1 | 96.4 | 96.9 | 97 | 96.9 | 96.8
AEG Power Solutions | Protect MPV.060.01 [480V] | 60 kW, 480 Vac, 3-phase Utility Interactive Inverter | 60 | 480 | 96.5 | N | N |  | 73.3 |  |  | 305 | 405 | 595 | 6 | 12 | 18 | 30 | 45 | 60 | 94.2 | 95.9 | 95.9 | 96.3 | 96.4 | 96 | 96.2 | 91.1 | 94.8 | 96.2 | 96.3 | 96.9 | 96.6 | 96.3 | 93.8 | 96.1 | 96.4 | 96.9 | 97 | 96.9 | 96.8
AEG Power Solutions | Protect MPV.075.01 [480V] | 75 kW, 480 Vac, 3-phase Utility Interactive Inverter | 75 | 480 | 96.5 | N | N |  | 90 |  |  | 305 | 405 | 595 | 7.5 | 15 | 22.5 | 37.5 | 56.25 | 75 | 94.2 | 95.9 | 95.9 | 96.3 | 96.4 | 96 | 96.2 | 91.1 | 94.8 | 96.2 | 96.3 | 96.9 | 96.6 | 96.3 | 93.8 | 96.1 | 96.4 | 96.9 | 97 | 96.9 | 96.8
AEG Power Solutions | Protect MPV.090.01 [480V] | 90 kW, 480 Vac, 3-phase Utility Interactive Inverter | 90 | 480 | 96.5 | N | N |  | 108 |  |  | 305 | 405 | 595 | 9 | 18 | 27 | 45 | 67.5 | 90 | 94.2 | 95.9 | 95.9 | 96.3 | 96.4 | 96 | 96.2 | 91.1 | 94.8 | 96.2 | 96.3 | 96.9 | 96.6 | 96.3 | 93.8 | 96.1 | 96.4 | 96.9 | 97 | 96.9 | 96.8
AEG Power Solutions | Protect MPV.105.01 [480V] | 105 kW, 480 Vac, 3-phase Utility Interactive Inverter | 105 | 480 | 96.5 | N | N |  | 126 |  |  | 305 | 405 | 595 | 10.5 | 21 | 31.5 | 52.5 | 78.75 | 105 | 94.2 | 95.9 | 95.9 | 96.3 | 96.4 | 96 | 96.2 | 91.1 | 94.8 | 96.2 | 96.3 | 96.9 | 96.6 | 96.3 | 93.8 | 96.1 | 96.4 | 96.9 | 97 | 96.9 | 96.8
AEG Power Solutions | Protect MPV.120.01 [480V] | 120 kW, 480 Vac, 3-phase Utility Interactive Inverter | 120 | 480 | 96.5 | N | N |  | 144 |  |  | 305 | 405 | 595 | 12 | 24 | 36 | 60 | 90 | 120 | 94.2 | 95.9 | 95.9 | 96.3 | 96.4 | 96 | 96.2 | 91.1 | 94.8 | 96.2 | 96.3 | 96.9 | 96.6 | 96.3 | 93.8 | 96.1 | 96.4 | 96.9 | 97 | 96.9 | 96.8
AEG Power Solutions | Protect MPV.135.01 [480V] | 135 kW, 480 Vac, 3-phase Utility Interactive Inverter | 135 | 480 | 96.5 | N | N |  | 162 |  |  | 305 | 405 | 595 | 13.5 | 27 | 40.5 | 67.5 | 101.3 | 135 | 94.2 | 95.9 | 95.9 | 96.3 | 96.4 | 96 | 96.2 | 91.1 | 94.8 | 96.2 | 96.3 | 96.9 | 96.6 | 96.3 | 93.8 | 96.1 | 96.4 | 96.9 | 97 | 96.9 | 96.8
AEG Power Solutions | Protect MPV.150.01 [480V] | 150 kW, 480 Vac, 3-phase Utility Interactive Inverter | 150 | 480 | 96.5 | N | N |  | 180 |  |  | 305 | 405 | 595 | 15 | 30 | 45 | 75 | 112.5 | 150 | 94.2 | 95.9 | 95.9 | 96.3 | 96.4 | 96 | 96.2 | 91.1 | 94.8 | 96.2 | 96.3 | 96.9 | 96.6 | 96.3 | 93.8 | 96.1 | 96.4 | 96.9 | 97 | 96.9 | 96.8
AEG Power Solutions | Protect PV.500-UL | 500 kW Utility Interactive Inverter for use with MV transformer | 510 |  | 96.5 | Y | N |  | 123 |  |  | 500 | 660 | 820 | 51 | 102 | 153 | 255 | 382.5 | 510 | 95.1 | 97 | 97.5 | 97.6 | 97.3 | 96.9 | 97.3 | 92.3 | 95.5 | 96.4 | 96.9 | 96.8 | 96.5 | 96.5 | 91.2 | 94.7 | 95.8 | 96.4 | 96.4 | 96.2 | 96
Aero-Sharp | X01-030L2E1 [240V] | 3000 W, 240 Vac Utility Interactive Inverter | 2.98 | 240 | 92.5 | Y | N |  | 0.7 |  |  | 100 | 275 | 400 | 0.3 | 0.6 | 0.89 | 1.49 | 2.24 | 2.98 | 78.68 | 88.27 | 90.8 | 92.32 | 92.57 | 92.26 | 91.52 | 78.21 | 89.57 | 91.75 | 93.35 | 93.77 | 93.77 | 92.61 | 83.64 | 90.93 | 92.79 | 94.2 | 94.43 | 94.27 | 93.57
Aero-Sharp | X01-040L2E1 [240V] | 4000 W, 240 Vac Utility Interactive Inverter | 4.012 | 240 | 93.5 | Y | N |  | 0.71 |  |  | 100 | 275 | 400 | 0.4012 | 0.8024 | 1.204 | 2.006 | 3.009 | 4.012 | 84.63 | 90.56 | 92.15 | 92.88 | 92.64 | 91.99 | 92.17 | 84.91 | 91.73 | 93.31 | 94.16 | 94.19 | 93.84 | 93.57 | 88.7 | 93.32 | 94.61 | 95.09 | 94.97 | 94.6 | 94.6
Aero-Sharp | X01-050L2E1 [240V] | 5000 W, 240 Vac Utility Interactive Inverter | 4.986 | 240 | 93.5 | Y | N |  | 0.78 |  |  | 100 | 275 | 400 | 0.4986 | 0.9972 | 1.496 | 2.493 | 3.74 | 4.986 | 84.4 | 91.02 | 92.46 | 93.16 | 92.82 | 92.19 | 92.39 | 85.63 | 91.8 | 93.48 | 94.33 | 94.29 | 93.94 | 93.71 | 85.23 | 92.29 | 93.74 | 94.68 | 94.7 | 94.37 | 94.07
Aero-Sharp | X01-060L2E1 [240V] | 6000 W, 240 Vac Utility Interactive Inverter | 5.993 | 240 | 93.5 | Y | N |  | 0.8 |  |  | 100 | 275 | 400 | 0.5993 | 1.199 | 1.798 | 2.997 | 4.495 | 5.993 | 87.08 | 91.91 | 92.98 | 93.18 | 92.58 | 91.69 | 92.45 | 88.35 | 93.41 | 94.35 | 94.41 | 94.14 | 93.55 | 93.93 | 88.05 | 93.2 | 94.38 | 94.92 | 94.75 | 94.33 | 94.37
Agepower Limit | Agepower AP 1500TL-US [208V] | 1500 W, 208 Vac Utility Interactive Inverter | 1.5 | 208 | 96 | Y | N |  | 0.07 |  |  | 100 | 330 | 360 | 0.15 | 0.3 | 0.45 | 0.75 | 1.125 | 1.5 | 91.1 | 94.9 | 96 | 96.4 | 96.2 | 96 | 95.9 | 91.7 | 95.5 | 96.5 | 96.8 | 96.7 | 96.5 | 96.4 | 91.5 | 95.2 | 96.2 | 96.7 | 96.7 | 96.5 | 96.3
Agepower Limit | Agepower AP 1500TL-US [240V] | 1650 W, 240 Vac Utility Interactive Inverter | 1.65 | 240 | 96 | Y | N |  | 0.11 |  |  | 100 | 330 | 360 | 0.17 | 0.33 | 0.5 | 0.83 | 1.24 | 1.65 | 89.5 | 94.2 | 95.5 | 96.3 | 96.3 | 96 | 95.8 | 90.2 | 94.7 | 95.9 | 96.6 | 96.6 | 96.5 | 96.2 | 91.3 | 95.4 | 96.5 | 97 | 97 | 96.8 | 96.6
Agepower Limit | Agepower AP 1500TL-US [277V] | 1650 W, 277 Vac Utility Interactive Inverter | 1.65 | 277 | 96 | Y | N |  | 0.13 |  |  | 100 | 330 | 360 | 0.17 | 0.33 | 0.5 | 0.83 | 1.24 | 1.65 | 89.2 | 93.5 | 95 | 96.1 | 96.2 | 96.1 | 95.6 | 89.3 | 94 | 95.6 | 96.4 | 96.6 | 96.7 | 96 | 89.3 | 94.3 | 95.7 | 96.6 | 96.8 | 96.8 | 96.2
Agepower Limit | Agepower AP 2000TL-US [208V] | 1800 W, 208 Vac Utility Interactive Inverter | 1.8 | 208 | 96.5 | Y | N |  | 0.09 |  |  | 100 | 360 | 400 | 0.18 | 0.36 | 0.54 | 0.9 | 1.35 | 1.8 | 92.3 | 95.4 | 96 | 96.4 | 96.3 | 96 | 96.1 | 92.8 | 96 | 96.6 | 96.8 | 96.6 | 96.4 | 96.5 | 92.7 | 95.7 | 96.3 | 96.6 | 96.5 | 96.3 | 96.3
Agepower Limit | Agepower AP 2000TL-US [240V] | 2000 W, 240 Vac Utility Interactive Inverter | 2 | 240 | 96.5 | Y | N |  | 0.1 |  |  | 100 | 360 | 400 | 0.2 | 0.4 | 0.6 | 1 | 1.5 | 2 | 91.4 | 94.6 | 95.7 | 96.3 | 96.4 | 96.1 | 96 | 92.9 | 96.1 | 96.8 | 97.1 | 97.1 | 96.9 | 96.9 | 92.3 | 95.8 | 96.6 | 96.9 | 97 | 96.8 | 96.7
Agepower Limit | Agepower AP 2000TL-US [277V] | 2000 W, 277 Vac Utility Interactive Inverter | 2 | 277 | 96.5 | Y | N |  | 0.14 |  |  | 100 | 360 | 400 | 0.2 | 0.4 | 0.6 | 1 | 1.5 | 2 | 89.3 | 93.7 | 95.1 | 96 | 96.3 | 96.1 | 95.7 | 91.1 | 94.8 | 95.9 | 96.5 | 96.8 | 96.8 | 96.3 | 92.9 | 96.1 | 96.9 | 97.3 | 97.4 | 97.3 | 97.1
Agepower Limit | Agepower AP 3000TL-US [208V] | 2500 W, 208 Vac Utility Interactive Inverter | 2.5 | 208 | 96.5 | Y | N |  | 0.1 |  |  | 100 | 360 | 400 | 0.25 | 0.5 | 0.75 | 1.25 | 1.88 | 2.5 | 92.3 | 95.4 | 96.2 | 96.5 | 96.2 | 95.8 | 96 | 93.9 | 96.2 | 96.8 | 97 | 96.8 | 96.4 | 96.7 | 92.7 | 95.8 | 96.5 | 96.8 | 96.6 | 96.3 | 96.4
Agepower Limit | Agepower AP 3000TL-US [240V] | 3000 W, 240 Vac Utility Interactive Inverter | 2.8 | 240 | 96.5 | Y | N |  | 0.15 |  |  | 100 | 360 | 400 | 0.28 | 0.56 | 0.84 | 1.4 | 2.1 | 2.8 | 91 | 94.4 | 95.6 | 96.4 | 96.4 | 96.1 | 96 | 94 | 96.6 | 97.1 | 97.5 | 97.4 | 97 | 97.2 | 93.3 | 96.1 | 96.8 | 97.4 | 97.3 | 97 | 97
Agepower Limit | Agepower AP 3000TL-US [277V] | 3000 W, 277 Vac Utility Interactive Inverter | 2.8 | 277 | 96.5 | Y | N |  | 0.19 |  |  | 100 | 360 | 400 | 0.28 | 0.56 | 0.84 | 1.4 | 2.1 | 2.8 | 89.4 | 93.4 | 94.8 | 95.9 | 96.2 | 96 | 95.5 | 91.6 | 95.2 | 96.3 | 96.9 | 97 | 96.8 | 96.6 | 94.1 | 96.6 | 97.3 | 97.7 | 97.6 | 97.4 | 97.4
Agepower Limit | Agepower AP 3600MTL-US [208V] | 3600 W, 208 Vac Utility Interactive Inverter | 3.6 | 208 | 97 | Y | N |  | 0.23 |  |  | 100 | 375 | 450 | 0.36 | 0.72 | 1.08 | 1.8 | 2.7 | 3.6 | 91.9 | 94.6 | 95.5 | 96.4 | 96.5 | 96.3 | 96.1 | 94.5 | 96.7 | 97.3 | 97.6 | 97.4 | 97.2 | 97.3 | 93 | 96 | 96.9 | 97.3 | 97.3 | 97.1 | 97
Agepower Limit | Agepower AP 3600MTL-US [240V] | 3600 W, 240 Vac Utility Interactive Inverter | 3.6 | 240 | 97 | Y | N |  | 0.31 |  |  | 100 | 375 | 450 | 0.36 | 0.72 | 1.08 | 1.8 | 2.7 | 3.6 | 92.4 | 94.6 | 95.5 | 96.5 | 96.7 | 96.7 | 96.2 | 95.3 | 97.1 | 97.5 | 97.8 | 97.7 | 97.5 | 97.6 | 94.2 | 96.5 | 97.1 | 97.5 | 97.6 | 97.4 | 97.3
Agepower Limit | Agepower AP 3600MTL-US [277V] | 3600 W, 277 Vac Utility Interactive Inverter | 3.6 | 277 | 97 | Y | N |  | 0.4 |  |  | 100 | 375 | 450 | 0.36 | 0.72 | 1.08 | 1.8 | 2.7 | 3.6 | 91.2 | 93.9 | 94.7 | 96.1 | 96.6 | 96.6 | 95.9 | 93.4 | 96 | 96.6 | 97.4 | 97.5 | 97.5 | 97.2 | 94.5 | 96.8 | 97.4 | 97.9 | 98 | 97.9 | 97.7
Agepower Limit | Agepower AP 4200MTL-US [208V] | 4200 W, 208 Vac Utility Interactive Inverter | 4.2 | 208 | 97 | Y | N |  | 0.25 |  |  | 100 | 375 | 450 | 0.42 | 0.84 | 1.26 | 2.1 | 3.15 | 4.2 | 91.6 | 94.4 | 95.5 | 96.6 | 96.8 | 96.7 | 96.3 | 94.1 | 96.5 | 97.1 | 97.3 | 97.1 | 96.7 | 97 | 93.6 | 96.2 | 96.8 | 97.2 | 97.5 | 97.1 | 97.1
Agepower Limit | Agepower AP 4200MTL-US [240V] | 4200 W, 240 Vac Utility Interactive Inverter | 4.2 | 240 | 97 | Y | N |  | 0.33 |  |  | 100 | 375 | 450 | 0.42 | 0.84 | 1.26 | 2.1 | 3.15 | 4.2 | 92.4 | 94.6 | 95.5 | 96.5 | 96.7 | 96.7 | 96.2 | 95.3 | 97.1 | 97.5 | 97.8 | 97.7 | 97.5 | 97.6 | 94.2 | 96.5 | 97.1 | 97.5 | 97.6 | 97.4 | 97.3
Agepower Limit | Agepower AP 4200MTL-US [277V] | 4200 W, 277 Vac Utility Interactive Inverter | 4.2 | 277 | 97 | Y | N |  | 0.4 |  |  | 100 | 375 | 450 | 0.42 | 0.84 | 1.26 | 2.1 | 3.15 | 4.2 | 91.4 | 94.4 | 96 | 96.6 | 96.8 | 96.6 | 96.3 | 92.1 | 95.2 | 96.3 | 97.3 | 97.6 | 97.1 | 97 | 93.6 | 96.3 | 97.2 | 97.6 | 97.6 | 97.6 | 97.4
Agepower Limit | Agepower AP 5000MTL-US [208V] | 4600 W, 208 Vac Utility Interactive Inverter | 4.6 | 208 | 97 | Y | N |  | 0.26 |  |  | 100 | 375 | 450 | 0.46 | 0.92 | 1.38 | 2.3 | 3.45 | 4.6 | 94.7 | 96.5 | 96.8 | 96.9 | 96.5 | 96 | 96.5 | 95.4 | 97 | 97.3 | 97.4 | 97 | 96.5 | 97 | 94.3 | 96.4 | 96.9 | 97.1 | 97 | 96.5 | 96.8
Agepower Limit | Agepower AP 5000MTL-US [240V] | 4600 W, 240 Vac Utility Interactive Inverter | 4.6 | 240 | 97 | Y | N |  | 0.36 |  |  | 100 | 375 | 450 | 0.46 | 0.92 | 1.38 | 2.3 | 3.45 | 4.6 | 92.8 | 95.2 | 96 | 96.7 | 96.6 | 96.4 | 96.3 | 95.8 | 97.3 | 97.7 | 97.8 | 97.5 | 97.1 | 97.5 | 96.7 | 96.7 | 97.2 | 97.5 | 97.4 | 97.1 | 97.3
Agepower Limit | Agepower AP 5000MTL-US [277V] | 4600 W, 277 Vac Utility Interactive Inverter | 4.6 | 277 | 97 | Y | N |  | 0.43 |  |  | 100 | 375 | 450 | 0.46 | 0.92 | 1.38 | 2.3 | 3.45 | 4.6 | 92.2 | 94.9 | 95.6 | 96.6 | 96.8 | 96.8 | 96.4 | 94.6 | 96.7 | 97.2 | 97.6 | 97.6 | 97.4 | 97.4 | 95.4 | 97.1 | 97.6 | 97.9 | 97.8 | 97.7 | 97.7
Agepower Limit | Agepower AP 10000 TL3-US [277V] | 10000 W, 277 Vac Utility Interactive Inverter | 10.1 | 277 | 95.5 | Y | N |  | 0.01 |  |  | 250 | 420 | 480 | 1.1 | 2.2 | 3.3 | 5.5 | 7.58 | 10.1 | 89.5 | 93.1 | 94.1 | 94.9 | 95 | 95 | 94.6 | 90.1 | 93.9 | 95.2 | 96 | 96.3 | 96.4 | 95.7 | 89.9 | 94.2 | 95.4 | 96.3 | 96.7 | 96.8 | 96
Agepower Limit | Agepower AP 12000 TL3-US [277V] | 11620 W, 277 Vac Utility Interactive Inverter | 11.62 | 277 | 95.5 | Y | N |  | 0.01 |  |  | 250 | 420 | 480 | 1.16 | 2.32 | 3.49 | 5.81 | 8.72 | 11.62 | 89.8 | 93.4 | 94.4 | 95.2 | 94.9 | 95 | 94.6 | 90.2 | 94.2 | 95.3 | 96.2 | 96.4 | 96.5 | 95.9 | 91 | 94.6 | 95.6 | 96.4 | 96.6 | 96.7 | 96.1
Agepower Limit | Agepower AP 18000 TL3-US [277V] | 18220 W, 277 Vac Utility Interactive Inverter | 18.31 | 277 | 96 | Y | N |  | 0.01 |  |  | 250 | 420 | 480 | 1.83 | 3.66 | 5.49 | 9.15 | 13.73 | 18.31 | 92.3 | 94.9 | 95.4 | 95.2 | 95.5 | 95.4 | 95.3 | 92.5 | 95.8 | 96.4 | 96.8 | 96.9 | 96.6 | 96.6 | 92.9 | 95.8 | 96.5 | 96.9 | 97.1 | 96.8 | 96.7
Agepower Limit | Agepower AP 20000 TL3-US [277V] | 20000 W, 277 Vac Utility Interactive Inverter | 20.42 | 277 | 96.5 | Y | N |  | 0.2 |  |  | 250 | 420 | 480 | 2.04 | 4.08 | 6.12 | 10.21 | 15.31 | 20.42 | 92.7 | 95.1 | 95.5 | 95.6 | 95.7 | 95.7 | 95.5 | 93.1 | 96 | 96.5 | 96.8 | 96.8 | 96.8 | 96.6 | 93.5 | 96 | 96.6 | 97 | 97.1 | 97 | 96.8
Alpha Technologies | Solaris 3500 XP [240V] | 3.5 kW, 240 Vac, NEMA Type 3R, Grid Interactive PV Inverter & Battery Backed UPS, MPPT | 3.5 | 240 | 90.5 | Y | N |  | 15 |  |  | 48 | 51 | 52 | 0.35 | 0.7 | 1.05 | 1.75 | 2.63 | 3.5 | 87.5 | 91 | 92.3 | 91.6 | 90.4 | 88.4 | 90.7 | 86.3 | 90.8 | 92.3 | 91.3 | 90.1 | 88.2 | 90.4 | 85 | 90.6 | 92.2 | 91.6 | 90.4 | 88.7 | 90.6
Altenergy Power System Inc. | YC200-NA [240V] | 220 W, 240 Vac Utility Interactive Inverter | 0.22 | 240 | 94 | N | Y |  | 0.08 |  |  | 27 | 36 | 45 | 0.022 | 0.044 | 0.066 | 0.11 | 0.165 | 0.22 | 90.1 | 92.4 | 92.8 | 94.6 | 94.8 | 94.3 | 94.2 | 89.9 | 91.3 | 92.9 | 93.9 | 94.8 | 94.9 | 94 | 90.6 | 89.7 | 91.8 | 93.4 | 94.4 | 94.8 | 93.5 |  | 2017-12-15
Altenergy Power System Inc. | YC250A [240V] | 225 W, 240 Vac Utility Interactive Inverter | 0.225 | 240 | 94 | N | Y |  | 0.15 |  |  | 24 | 35 | 45 | 0.0225 | 0.045 | 0.0675 | 0.1125 | 0.1688 | 0.225 | 88.43 | 93.05 | 93.8 | 94.71 | 94.57 | 93.17 | 94.11 | 89.77 | 92.52 | 93.7 | 94.51 | 95.06 | 95.02 | 94.44 | 88.24 | 90.29 | 92.46 | 93.92 | 94.84 | 95.14 | 93.89 |  | 2017-12-15
Altenergy Power System Inc. | YC250I [240V] | 225 W, 240 Vac Utility Interactive Inverter | 0.225 | 240 | 94 | N | Y |  | 0.15 |  |  | 24 | 35 | 45 | 0.0225 | 0.045 | 0.0675 | 0.1125 | 0.1688 | 0.225 | 88.43 | 93.05 | 93.8 | 94.71 | 94.57 | 93.17 | 94.11 | 89.77 | 92.52 | 93.7 | 94.51 | 95.06 | 95.02 | 94.44 | 88.24 | 90.29 | 92.46 | 93.92 | 94.84 | 95.14 | 93.89 |  | 2017-12-15
Altenergy Power System Inc. | YC500A [208V] | 500 W, 208 Vac, Utility Interactive Inverter | 0.5 | 208 | 95 | N | Y |  | 0.12 |  |  | 24 | 35 | 45 | 0.05 | 0.1 | 0.15 | 0.25 | 0.375 | 0.5 | 93.7 | 95.1 | 95.4 | 95.4 | 94.4 | 92.7 | 94.6 | 94.3 | 95.2 | 95.5 | 95.5 | 95.5 | 94.9 | 95.4 | 94.2 | 94.2 | 93.9 | 94.9 | 95.5 | 95.3 | 95 |  | 2017-12-15
Altenergy Power System Inc. | YC500A [240V] | 500 W, 240 Vac, Utility Interactive Inverter | 0.5 | 240 | 95 | N | Y |  | 0.15 |  |  | 24 | 35 | 45 | 0.05 | 0.1 | 0.15 | 0.25 | 0.375 | 0.5 | 93.3 | 95.1 | 93.8 | 95.6 | 94.5 | 93 | 94.6 | 92.5 | 95.1 | 95.6 | 95.6 | 95.7 | 95.3 | 95.5 | 94 | 94.5 | 93.6 | 95 | 95.7 | 95.6 | 95.2 |  | 2017-12-15
Altenergy Power System Inc. | YC500I [208V] | 500 W, 208 Vac, Utility Interactive Inverter | 0.5 | 208 | 95 | N | Y |  | 0.12 |  |  | 24 | 35 | 45 | 0.05 | 0.1 | 0.15 | 0.25 | 0.375 | 0.5 | 93.7 | 95.1 | 95.4 | 95.4 | 94.4 | 92.7 | 94.6 | 94.3 | 95.2 | 95.5 | 95.5 | 95.5 | 94.9 | 95.4 | 94.2 | 94.2 | 93.9 | 94.9 | 95.5 | 95.3 | 95 |  | 2017-12-15
Altenergy Power System Inc. | YC500I [240V] | 500 W, 240 Vac, Utility Interactive Inverter | 0.5 | 240 | 95 | N | Y |  | 0.15 |  |  | 24 | 35 | 45 | 0.05 | 0.1 | 0.15 | 0.25 | 0.375 | 0.5 | 93.3 | 95.1 | 93.8 | 95.6 | 94.5 | 93 | 94.6 | 92.5 | 95.1 | 95.6 | 95.6 | 95.7 | 95.3 | 95.5 | 94 | 94.5 | 93.6 | 95 | 95.7 | 95.6 | 95.2 |  | 2017-12-15
Altenergy Power System Inc. | YC600 [240V] | 548 W, 240 Vac Utility Interactive Microinverter, Rack mounted | 0.55 | 240 | 96.5 | N | Y |  | 0.02 |  |  | 24 | 36 | 45 | 0.0548 | 0.1096 | 0.1644 | 0.274 | 0.411 | 0.548 | 94.4 | 95.9 | 96 | 96.4 | 96.3 | 96.1 | 96.2 | 94.1 | 95.8 | 96.2 | 96.5 | 96.7 | 96.6 | 96.4 | 93.7 | 95.7 | 95.8 | 96.4 | 96.7 | 96.7 | 96.4 | 2018-03-01 | 2018-10-15
Altenergy Power System Inc. | YC1000-3-208 [480V] | 900 W, 3-phase, Utility Interactive Inverter | 0.9 | 480 | 94.5 | N | Y |  | 0.11 |  |  | 33 | 40 | 48 | 0.09 | 0.18 | 0.27 | 0.45 | 0.68 | 0.9 | 90.3 | 94.2 | 94.4 | 94.8 | 94.6 | 93.7 | 94.4 | 89.4 | 93.8 | 94.5 | 94.6 | 94.7 | 94.1 | 94.4 | 88.9 | 93.1 | 94.2 | 94.2 | 94.6 | 94.1 | 94.1 |  | 2017-12-15
Altenergy Power System Inc. | YC1000-3-480 [480V] | 0.9 kW, 480 Vac, 3-phase Utility Interactive Inverter | 0.9 | 480 | 94.5 | N | Y |  | 0.88 |  |  | 28 | 36 | 48 | 0.09 | 0.18 | 0.27 | 0.45 | 0.675 | 0.9 | 89.9 | 93.9 | 92.7 | 94.9 | 95.2 | 94.7 | 94.6 | 88.9 | 93.6 | 94.3 | 94.5 | 95.3 | 95.2 | 94.7 | 81.8 | 92.2 | 93.9 | 93.3 | 94.8 | 95.1 | 93.7 |  | 2017-12-15
Altenergy Power System Inc. | YC1000-3-K480 | 1200 W, 3-phase, Utility Interactive Inverter | 1.16 |  | 94.5 | N | Y |  | 0.83 |  |  | 50 | 51.5 | 55 | 0.12 | 0.23 | 0.35 | 0.58 | 0.87 | 1.16 | 91.1 | 94.7 | 95.3 | 95.4 | 95 | 93.5 | 94.9 | 90.7 | 94.6 | 95.3 | 95.3 | 94.9 | 93.4 | 94.8 | 89.7 | 94.3 | 95.2 | 95.1 | 94.7 | 93.4 | 94.6 |  | 2017-12-15
Altenergy Power System Inc. | QS1 [240V] | 1.2 kW, 240 Vac Utility Interactive Microinverter | 1.225 | 240 | 96.5 | N | Y |  | 0.09 |  |  | 27 | 37.5 | 48 | 0.12252 | 0.24503 | 0.36755 | 0.61258 | 0.91887 | 1.2252 | 93.497 | 96.0302 | 96.2918 | 96.5164 | 96.1897 | 95.6368 | 96.1272 | 93.4891 | 96.0102 | 96.472 | 96.7093 | 96.5407 | 96.1255 | 96.3985 | 92.8188 | 95.8573 | 96.4916 | 96.6522 | 96.6297 | 96.2942 | 96.41 | 2018-12-17
Altenergy Power System Inc. | QS1200 [240V] | 1.2 kW, 240 Vac Utility Interactive Microinverter | 1.225 | 240 | 96.5 | N | Y |  | 0.09 |  |  | 27 | 37.5 | 48 | 0.12252 | 0.24503 | 0.36755 | 0.61258 | 0.91887 | 1.2252 | 93.497 | 96.0302 | 96.2918 | 96.5164 | 96.1897 | 95.6368 | 96.1272 | 93.4891 | 96.0102 | 96.472 | 96.7093 | 96.5407 | 96.1255 | 96.3985 | 92.8188 | 95.8573 | 96.4916 | 96.6522 | 96.6297 | 96.2942 | 96.41 | 2018-12-17
American Electric Technologies | ISIS-1000-15000-60 | 1000 kW, 3-phase Utility Interactive Inverter | 1000 |  | 96.5 | Y | N |  | 300 |  |  | 610 | 720 | 1000 | 100 | 200 | 300 | 500 | 750 | 1000 | 93.8 | 95.6 | 96.2 | 96.7 | 97.7 | 97.4 | 97 | 93.3 | 95.2 | 95.7 | 96.3 | 96.6 | 97.1 | 96.2 | 92.1 | 94.2 | 95.2 | 95.6 | 96 | 95.9 | 95.6
American Electric Technologies | ISIS-1000-410-60 | 1000 kW, 3-phase Inverter for 410 Vac applications with TP-1 transformer | 1000 |  | 96 | Y | N |  | 350 |  |  | 610 | 720 | 1000 | 100 | 200 | 300 | 500 | 750 | 1000 | 94.5 | 96.2 | 96.7 | 96.9 | 97.1 | 96.7 | 96.9 | 94 | 95.8 | 96.2 | 96.5 | 96.4 | 96.5 | 96.3 | 92.8 | 94.8 | 95.5 | 95.8 | 95.7 | 95.4 | 95.5
AMETEK Solidstate Control | RECon 30L-100-US | 100 kW, 3-phase Utility Interactive Inverter | 100 |  | 98 | Y | N |  | 59.63 |  |  | 325 | 487 | 650 | 10 | 20 | 30 | 50 | 75 | 100 | 96.5 | 98.1 | 98.4 | 98 | 97.3 | 96.9 | 97.5 | 95.3 | 97.8 | 98.3 | 98.2 | 98.1 | 97.9 | 98 | 96 | 98.2 | 98.8 | 98.7 | 98.3 | 97.7 | 98.3
AMETEK Solidstate Control | RECon 30H-150-US [300V] | 150 kW, 3-phase output 300Vac/LV/MV Utility Interactive Inverter | 150 | 300 | 98 | Y | N |  | 62.53 |  |  | 480 | 615 | 750 | 15 | 30 | 45 | 75 | 112.5 | 150 | 93.6 | 96.3 | 97 | 97.5 | 97.4 | 97.7 | 97.2 | 95.6 | 97.6 | 98.4 | 98.3 | 98 | 98 | 98 | 94.1 | 96.7 | 97.7 | 97.9 | 97.8 | 97.6 | 97.6
Andalay Solar | LW-230-1-AC1-A-B [240V] | 190 W, 240 Vac Inverter | 0.19 | 240 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.03 | 0.19 | 0.03 | 22 | 32.5 | 40 | 0.02 | 0.04 | 0.1 | 0.1 | 0.1 | 0.2 | 93.3 | 94.4 | 94.7 | 95.1 | 94.9 | 94.2 | 94.8 | 93.3 | 94.4 | 94.6 | 95.2 | 95.4 | 95.1 | 95.1 | 93.5 | 94.4 | 94.6 | 94.9 | 95.4 | 95.4 | 95.1
Andalay Solar | LW-230-1-AC3-B-B [208V] | 190 W, 208 Vac Inverter | 0.19 | 208 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.01 | 0.19 | 0.01 | 22 | 32 | 40 | 0.019 | 0.038 | 0.057 | 0.095 | 0.1425 | 0.19 | 93.6 | 94.6 | 94.9 | 95 | 94.6 | 93.7 | 94.6 | 93.4 | 94.6 | 94.7 | 95.2 | 95.2 | 94.8 | 95 | 93.4 | 94.4 | 94.8 | 95.1 | 95.3 | 95.1 | 95.1
Andalay Solar | LW-235-1-AC1-A-B [240V] | 190 W, 240 Vac Inverter | 0.19 | 240 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.03 | 0.19 | 0.03 | 22 | 32.5 | 40 | 0.02 | 0.04 | 0.1 | 0.1 | 0.1 | 0.2 | 93.3 | 94.4 | 94.7 | 95.1 | 94.9 | 94.2 | 94.8 | 93.3 | 94.4 | 94.6 | 95.2 | 95.4 | 95.1 | 95.1 | 93.5 | 94.4 | 94.6 | 94.9 | 95.4 | 95.4 | 95.1
Andalay Solar | LW-235-1-AC3-B-B [208V] | 190 W, 208 Vac Inverter | 0.19 | 208 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.01 | 0.19 | 0.01 | 22 | 32 | 40 | 0.019 | 0.038 | 0.057 | 0.095 | 0.1425 | 0.19 | 93.6 | 94.6 | 94.9 | 95 | 94.6 | 93.7 | 94.6 | 93.4 | 94.6 | 94.7 | 95.2 | 95.2 | 94.8 | 95 | 93.4 | 94.4 | 94.8 | 95.1 | 95.3 | 95.1 | 95.1
Andalay Solar | LW-240-1-AC1-A-B [240V] | 190 W, 240 Vac Inverter | 0.19 | 240 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.03 | 0.19 | 0.03 | 22 | 32.5 | 40 | 0.02 | 0.04 | 0.1 | 0.1 | 0.1 | 0.2 | 93.3 | 94.4 | 94.7 | 95.1 | 94.9 | 94.2 | 94.8 | 93.3 | 94.4 | 94.6 | 95.2 | 95.4 | 95.1 | 95.1 | 93.5 | 94.4 | 94.6 | 94.9 | 95.4 | 95.4 | 95.1
Andalay Solar | LW-240-1-AC3-B-B [208V] | 190 W, 208 Vac Inverter | 0.19 | 208 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.01 | 0.19 | 0.01 | 22 | 32 | 40 | 0.019 | 0.038 | 0.057 | 0.095 | 0.1425 | 0.19 | 93.6 | 94.6 | 94.9 | 95 | 94.6 | 93.7 | 94.6 | 93.4 | 94.6 | 94.7 | 95.2 | 95.2 | 94.8 | 95 | 93.4 | 94.4 | 94.8 | 95.1 | 95.3 | 95.1 | 95.1
Andalay Solar | ST-175-1AC1-A-A [240V] | 190 W, 240 Vac Inverter | 0.19 | 240 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.03 | 0.19 | 0.03 | 22 | 32.5 | 40 | 0.02 | 0.04 | 0.1 | 0.1 | 0.1 | 0.2 | 93.3 | 94.4 | 94.7 | 95.1 | 94.9 | 94.2 | 94.8 | 93.3 | 94.4 | 94.6 | 95.2 | 95.4 | 95.1 | 95.1 | 93.5 | 94.4 | 94.6 | 94.9 | 95.4 | 95.4 | 95.1
Andalay Solar | ST-175-1AC3-B-A [208V] | 190 W, 208 Vac Inverter | 0.19 | 208 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.01 | 0.19 | 0.01 | 22 | 32 | 40 | 0.02 | 0.04 | 0.06 | 0.1 | 0.1 | 0.2 | 93.6 | 94.6 | 94.9 | 95 | 94.6 | 93.7 | 94.6 | 93.4 | 94.6 | 94.7 | 95.2 | 95.2 | 94.8 | 95 | 93.4 | 94.4 | 94.8 | 95.1 | 95.3 | 95.1 | 95.1
Andalay Solar | ST-185-1AC1-A-A [240V] | 190 W, 240 Vac Inverter | 0.19 | 240 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.03 | 0.19 | 0.03 | 22 | 32.5 | 40 | 0.02 | 0.04 | 0.1 | 0.1 | 0.1 | 0.2 | 93.3 | 94.4 | 94.7 | 95.1 | 94.9 | 94.2 | 94.8 | 93.3 | 94.4 | 94.6 | 95.2 | 95.4 | 95.1 | 95.1 | 93.5 | 94.4 | 94.6 | 94.9 | 95.4 | 95.4 | 95.1
Andalay Solar | ST-185-1AC1-A-B [240V] | 190 W, 240 Vac Inverter | 0.19 | 240 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.03 | 0.19 | 0.03 | 22 | 32.5 | 40 | 0.02 | 0.04 | 0.1 | 0.1 | 0.1 | 0.2 | 93.3 | 94.4 | 94.7 | 95.1 | 94.9 | 94.2 | 94.8 | 93.3 | 94.4 | 94.6 | 95.2 | 95.4 | 95.1 | 95.1 | 93.5 | 94.4 | 94.6 | 94.9 | 95.4 | 95.4 | 95.1
Andalay Solar | ST-185-1AC3-B-A [208V] | 190 W, 208 Vac Inverter | 0.19 | 208 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.01 | 0.19 | 0.01 | 22 | 32 | 40 | 0.02 | 0.04 | 0.06 | 0.1 | 0.1 | 0.2 | 93.6 | 94.6 | 94.9 | 95 | 94.6 | 93.7 | 94.6 | 93.4 | 94.6 | 94.7 | 95.2 | 95.2 | 94.8 | 95 | 93.4 | 94.4 | 94.8 | 95.1 | 95.3 | 95.1 | 95.1
Andalay Solar | ST-185-1AC3-B-B [208V] | 190 W, 208 Vac Inverter | 0.19 | 208 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.01 | 0.19 | 0.01 | 22 | 32 | 40 | 0.02 | 0.04 | 0.06 | 0.1 | 0.1 | 0.2 | 93.6 | 94.6 | 94.9 | 95 | 94.6 | 93.7 | 94.6 | 93.4 | 94.6 | 94.7 | 95.2 | 95.2 | 94.8 | 95 | 93.4 | 94.4 | 94.8 | 95.1 | 95.3 | 95.1 | 95.1
Andalay Solar | ST-190-1AC1-A-B [240V] | 190 W, 240 Vac Inverter | 0.19 | 240 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.03 | 0.19 | 0.03 | 22 | 32.5 | 40 | 0.02 | 0.04 | 0.1 | 0.1 | 0.1 | 0.2 | 93.3 | 94.4 | 94.7 | 95.1 | 94.9 | 94.2 | 94.8 | 93.3 | 94.4 | 94.6 | 95.2 | 95.4 | 95.1 | 95.1 | 93.5 | 94.4 | 94.6 | 94.9 | 95.4 | 95.4 | 95.1
Andalay Solar | ST-190-1AC3-B-B [208V] | 190 W, 208 Vac Inverter | 0.19 | 208 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.01 | 0.19 | 0.01 | 22 | 32 | 40 | 0.019 | 0.038 | 0.057 | 0.095 | 0.1425 | 0.19 | 93.6 | 94.6 | 94.9 | 95 | 94.6 | 93.7 | 94.6 | 93.4 | 94.6 | 94.7 | 95.2 | 95.2 | 94.8 | 95 | 93.4 | 94.4 | 94.8 | 95.1 | 95.3 | 95.1 | 95.1
Andalay Solar | ST-195-1AC1-A-B [240V] | 190 W, 240 Vac Inverter | 0.19 | 240 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.03 | 0.19 | 0.03 | 22 | 32.5 | 40 | 0.02 | 0.04 | 0.1 | 0.1 | 0.1 | 0.2 | 93.3 | 94.4 | 94.7 | 95.1 | 94.9 | 94.2 | 94.8 | 93.3 | 94.4 | 94.6 | 95.2 | 95.4 | 95.1 | 95.1 | 93.5 | 94.4 | 94.6 | 94.9 | 95.4 | 95.4 | 95.1
Andalay Solar | ST-195-1AC3-B-B [208V] | 190 W, 208 Vac Inverter | 0.19 | 208 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.01 | 0.19 | 0.01 | 22 | 32 | 40 | 0.019 | 0.038 | 0.057 | 0.095 | 0.1425 | 0.19 | 93.6 | 94.6 | 94.9 | 95 | 94.6 | 93.7 | 94.6 | 93.4 | 94.6 | 94.7 | 95.2 | 95.2 | 94.8 | 95 | 93.4 | 94.4 | 94.8 | 95.1 | 95.3 | 95.1 | 95.1
Andalay Solar | LW-230-1-AC0-D-B [208V] | 215 W, 208 Vac Inverter | 0.215 | 208 | 96 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.04 | 0.215 | 0.04 | 22 | 29 | 36 | 0.02 | 0.04 | 0.06 | 0.11 | 0.16 | 0.22 | 94.5 | 95.5 | 95.9 | 96 | 95.5 | 94.7 | 95.6 | 94.5 | 95.5 | 95.9 | 96.1 | 96 | 95.5 | 95.9 | 94.4 | 95.4 | 95.7 | 96.1 | 96.1 | 95.8 | 95.9
Andalay Solar | LW-230-1-AC0-D-B [240V] | 215 W, 240 Vac Inverter | 0.215 | 240 | 96 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.04 | 0.215 | 0.04 | 22 | 29 | 36 | 0.02 | 0.04 | 0.06 | 0.11 | 0.16 | 0.22 | 94.5 | 95.5 | 95.9 | 96 | 95.5 | 94.7 | 95.6 | 94.5 | 95.5 | 95.9 | 96.1 | 96 | 95.5 | 95.9 | 94.4 | 95.4 | 95.7 | 96.1 | 96.1 | 95.8 | 95.9
Andalay Solar | LW-230-1-AC2-D-B [208V] | 215 W, 208 Vac Inverter | 0.215 | 208 | 96 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.04 | 0.215 | 0.04 | 22 | 29 | 36 | 0.02 | 0.04 | 0.06 | 0.11 | 0.16 | 0.22 | 94.5 | 95.5 | 95.9 | 96 | 95.5 | 94.7 | 95.6 | 94.5 | 95.5 | 95.9 | 96.1 | 96 | 95.5 | 95.9 | 94.4 | 95.4 | 95.7 | 96.1 | 96.1 | 95.8 | 95.9
Andalay Solar | LW-230-1-AC2-D-B [240V] | 215 W, 240 Vac Inverter | 0.215 | 240 | 96 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.04 | 0.215 | 0.04 | 22 | 29 | 36 | 0.02 | 0.04 | 0.06 | 0.11 | 0.16 | 0.22 | 94.5 | 95.5 | 95.9 | 96 | 95.5 | 94.7 | 95.6 | 94.5 | 95.5 | 95.9 | 96.1 | 96 | 95.5 | 95.9 | 94.4 | 95.4 | 95.7 | 96.1 | 96.1 | 95.8 | 95.9
Andalay Solar | LW-235-1-AC0-D-B [208V] | 215 W, 208 Vac Inverter | 0.215 | 208 | 96 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.04 | 0.215 | 0.04 | 22 | 29 | 36 | 0.02 | 0.04 | 0.06 | 0.11 | 0.16 | 0.22 | 94.5 | 95.5 | 95.9 | 96 | 95.5 | 94.7 | 95.6 | 94.5 | 95.5 | 95.9 | 96.1 | 96 | 95.5 | 95.9 | 94.4 | 95.4 | 95.7 | 96.1 | 96.1 | 95.8 | 95.9
Andalay Solar | LW-235-1-AC0-D-B [240V] | 215 W, 240 Vac Inverter | 0.215 | 240 | 96 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.04 | 0.215 | 0.04 | 22 | 29 | 36 | 0.02 | 0.04 | 0.06 | 0.11 | 0.16 | 0.22 | 94.5 | 95.5 | 95.9 | 96 | 95.5 | 94.7 | 95.6 | 94.5 | 95.5 | 95.9 | 96.1 | 96 | 95.5 | 95.9 | 94.4 | 95.4 | 95.7 | 96.1 | 96.1 | 95.8 | 95.9
Andalay Solar | LW-235-1-AC2-D-B [208V] | 215 W, 208 Vac Inverter | 0.215 | 208 | 96 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.04 | 0.215 | 0.04 | 22 | 29 | 36 | 0.02 | 0.04 | 0.06 | 0.11 | 0.16 | 0.22 | 94.5 | 95.5 | 95.9 | 96 | 95.5 | 94.7 | 95.6 | 94.5 | 95.5 | 95.9 | 96.1 | 96 | 95.5 | 95.9 | 94.4 | 95.4 | 95.7 | 96.1 | 96.1 | 95.8 | 95.9
Andalay Solar | LW-235-1-AC2-D-B [240V] | 215 W, 240 Vac Inverter | 0.215 | 240 | 96 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.04 | 0.215 | 0.04 | 22 | 29 | 36 | 0.02 | 0.04 | 0.06 | 0.11 | 0.16 | 0.22 | 94.5 | 95.5 | 95.9 | 96 | 95.5 | 94.7 | 95.6 | 94.5 | 95.5 | 95.9 | 96.1 | 96 | 95.5 | 95.9 | 94.4 | 95.4 | 95.7 | 96.1 | 96.1 | 95.8 | 95.9
Andalay Solar | LW-240-1-AC0-D-B [208V] | 215 W, 208 Vac Inverter | 0.215 | 208 | 96 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.04 | 0.215 | 0.04 | 22 | 29 | 36 | 0.02 | 0.04 | 0.06 | 0.11 | 0.16 | 0.22 | 94.5 | 95.5 | 95.9 | 96 | 95.5 | 94.7 | 95.6 | 94.5 | 95.5 | 95.9 | 96.1 | 96 | 95.5 | 95.9 | 94.4 | 95.4 | 95.7 | 96.1 | 96.1 | 95.8 | 95.9
Andalay Solar | LW-240-1-AC0-D-B [240V] | 215 W, 240 Vac Inverter | 0.215 | 240 | 96 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.04 | 0.215 | 0.04 | 22 | 29 | 36 | 0.02 | 0.04 | 0.06 | 0.11 | 0.16 | 0.22 | 94.5 | 95.5 | 95.9 | 96 | 95.5 | 94.7 | 95.6 | 94.5 | 95.5 | 95.9 | 96.1 | 96 | 95.5 | 95.9 | 94.4 | 95.4 | 95.7 | 96.1 | 96.1 | 95.8 | 95.9
Andalay Solar | LW-240-1-AC2-D-B [208V] | 215 W, 208 Vac Inverter | 0.215 | 208 | 96 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.04 | 0.215 | 0.04 | 22 | 29 | 36 | 0.02 | 0.04 | 0.06 | 0.11 | 0.16 | 0.22 | 94.5 | 95.5 | 95.9 | 96 | 95.5 | 94.7 | 95.6 | 94.5 | 95.5 | 95.9 | 96.1 | 96 | 95.5 | 95.9 | 94.4 | 95.4 | 95.7 | 96.1 | 96.1 | 95.8 | 95.9
Andalay Solar | LW-240-1-AC2-D-B [240V] | 215 W, 240 Vac Inverter | 0.215 | 240 | 96 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.04 | 0.215 | 0.04 | 22 | 29 | 36 | 0.02 | 0.04 | 0.06 | 0.11 | 0.16 | 0.22 | 94.5 | 95.5 | 95.9 | 96 | 95.5 | 94.7 | 95.6 | 94.5 | 95.5 | 95.9 | 96.1 | 96 | 95.5 | 95.9 | 94.4 | 95.4 | 95.7 | 96.1 | 96.1 | 95.8 | 95.9
Andalay Solar | TW-240-1-AC2-D-B [208V] | 215 W, 208 Vac Inverter | 0.215 | 208 | 96 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.04 |  |  | 22 | 29 | 36 | 0.02 | 0.04 | 0.06 | 0.11 | 0.16 | 0.22 | 94.5 | 95.5 | 95.9 | 96 | 95.5 | 94.7 | 95.6 | 94.5 | 95.5 | 95.9 | 96.1 | 96 | 95.5 | 95.9 | 94.4 | 95.4 | 95.7 | 96.1 | 96.1 | 95.8 | 95.9
Andalay Solar | TW-240-1-AC2-D-B [240V] | 215 W, 240 Vac Inverter | 0.215 | 240 | 96 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.04 |  |  | 22 | 29 | 36 | 0.02 | 0.04 | 0.06 | 0.11 | 0.16 | 0.22 | 94.5 | 95.5 | 95.9 | 96 | 95.5 | 94.7 | 95.6 | 94.5 | 95.5 | 95.9 | 96.1 | 96 | 95.5 | 95.9 | 94.4 | 95.4 | 95.7 | 96.1 | 96.1 | 95.8 | 95.9
Andalay Solar | TW-245-1-AC2-D-B [208V] | 215 W, 208 Vac Inverter | 0.215 | 208 | 96 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.04 |  |  | 22 | 29 | 36 | 0.02 | 0.04 | 0.06 | 0.11 | 0.16 | 0.22 | 94.5 | 95.5 | 95.9 | 96 | 95.5 | 94.7 | 95.6 | 94.5 | 95.5 | 95.9 | 96.1 | 96 | 95.5 | 95.9 | 94.4 | 95.4 | 95.7 | 96.1 | 96.1 | 95.8 | 95.9
Andalay Solar | TW-245-1-AC2-D-B [240V] | 215 W, 240 Vac Inverter | 0.215 | 240 | 96 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.04 |  |  | 22 | 29 | 36 | 0.02 | 0.04 | 0.06 | 0.11 | 0.16 | 0.22 | 94.5 | 95.5 | 95.9 | 96 | 95.5 | 94.7 | 95.6 | 94.5 | 95.5 | 95.9 | 96.1 | 96 | 95.5 | 95.9 | 94.4 | 95.4 | 95.7 | 96.1 | 96.1 | 95.8 | 95.9
Andalay Solar | TW-250-1-AC2-D-B [208V] | 215 W, 208 Vac Inverter | 0.215 | 208 | 96 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.04 |  |  | 22 | 29 | 36 | 0.02 | 0.04 | 0.06 | 0.11 | 0.16 | 0.22 | 94.5 | 95.5 | 95.9 | 96 | 95.5 | 94.7 | 95.6 | 94.5 | 95.5 | 95.9 | 96.1 | 96 | 95.5 | 95.9 | 94.4 | 95.4 | 95.7 | 96.1 | 96.1 | 95.8 | 95.9
Andalay Solar | TW-250-1-AC2-D-B [240V] | 215 W, 240 Vac Inverter | 0.215 | 240 | 96 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.04 |  |  | 22 | 29 | 36 | 0.02 | 0.04 | 0.06 | 0.11 | 0.16 | 0.22 | 94.5 | 95.5 | 95.9 | 96 | 95.5 | 94.7 | 95.6 | 94.5 | 95.5 | 95.9 | 96.1 | 96 | 95.5 | 95.9 | 94.4 | 95.4 | 95.7 | 96.1 | 96.1 | 95.8 | 95.9
Apparent Inc. | MGI220-xxx [240V] | 180 W, 240 Vac Inverter, where xxx are connector types | 0.18 | 240 | 90 | N | Y |  | 0.4 |  |  | 23 | 28 | 36 | 0.02 | 0.04 | 0.05 | 0.09 | 0.14 | 0.18 | 80.5 | 87 | 88.4 | 90.6 | 91.2 | 91.2 | 90.1 | 81.6 | 86.8 | 89 | 90.2 | 91.2 | 91.4 | 90.1 | 79.7 | 85.7 | 88.2 | 89.7 | 90.7 | 91.2 | 89.5 |  | 2019-04-02
Apparent Inc. | SG424-120V [120V] | 230 W, Utility Interactive Inverter, 120V Split Phase | 0.23 | 120 | 91.5 | N | Y |  | 0.45 |  |  | 29 | 36 | 48 | 0.02 | 0.05 | 0.07 | 0.12 | 0.17 | 0.23 | 85.6 | 89.7 | 91.5 | 92.1 | 91.8 | 91.1 | 91.5 | 85.3 | 90.2 | 91.4 | 92.2 | 92.2 | 91.6 | 91.7 | 84.2 | 89.9 | 90.8 | 92.4 | 92.4 | 91.9 | 91.7 |  | 2019-04-02
Apparent Inc. | SG424U CA, 120VAC, 60Hz [120V] | 250 W, 120 Vac Utility Interactive Microinverter | 0.25 | 120 | 91.5 | N | Y |  |  |  |  | 31.2 | 36.4 | 48.9 | 0.03 | 0.05 | 0.08 | 0.13 | 0.19 | 0.25 | 85.4 | 91.1 | 91.5 | 92.1 | 91.8 | 90.6 | 91.5 | 87 | 90.8 | 91.5 | 92.4 | 92.2 | 91.2 | 91.8 | 86.1 | 90.9 | 92 | 92.2 | 92.4 | 92 | 92 | 2019-04-02
AU Optronics | PM060MA0_240 [240V] | 225 W, 240 Vac Inverter | 0.225 | 240 | 94.5 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.02 |  |  | 21 | 31.5 | 35 | 0.02 | 0.05 | 0.07 | 0.11 | 0.17 | 0.23 | 87 | 92 | 93.4 | 94.5 | 94.5 | 94.1 | 93.9 | 85.8 | 91.5 | 93.5 | 95.1 | 96.1 | 95.3 | 94.9 | 85.4 | 91.3 | 93.3 | 94.9 | 95.3 | 95.5 | 94.4
AU Optronics | PM060MA0_245 [240V] | 225 W, 240 Vac Inverter | 0.225 | 240 | 94.5 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.02 |  |  | 21 | 31.5 | 35 | 0.02 | 0.05 | 0.07 | 0.11 | 0.17 | 0.23 | 87 | 92 | 93.4 | 94.5 | 94.5 | 94.1 | 93.9 | 85.8 | 91.5 | 93.5 | 95.1 | 96.1 | 95.3 | 94.9 | 85.4 | 91.3 | 93.3 | 94.9 | 95.3 | 95.5 | 94.4
AU Optronics | PM060MA0_250 [240V] | 225 W, 240 Vac Inverter | 0.225 | 240 | 94.5 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.02 |  |  | 21 | 31.5 | 35 | 0.02 | 0.05 | 0.07 | 0.11 | 0.17 | 0.23 | 87 | 92 | 93.4 | 94.5 | 94.5 | 94.1 | 93.9 | 85.8 | 91.5 | 93.5 | 95.1 | 96.1 | 95.3 | 94.9 | 85.4 | 91.3 | 93.3 | 94.9 | 95.3 | 95.5 | 94.4
AU Optronics | PM060MA0_255 [240V] | 225 W, 240 Vac Inverter | 0.225 | 240 | 94.5 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.02 |  |  | 21 | 31.5 | 35 | 0.02 | 0.05 | 0.07 | 0.11 | 0.17 | 0.23 | 87 | 92 | 93.4 | 94.5 | 94.5 | 94.1 | 93.9 | 85.8 | 91.5 | 93.5 | 95.1 | 96.1 | 95.3 | 94.9 | 85.4 | 91.3 | 93.3 | 94.9 | 95.3 | 95.5 | 94.4
AU Optronics | PM060MA0_260 [240V] | 225 W, 240 Vac Inverter | 0.225 | 240 | 94.5 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.02 |  |  | 21 | 31.5 | 35 | 0.02 | 0.05 | 0.07 | 0.11 | 0.17 | 0.23 | 87 | 92 | 93.4 | 94.5 | 94.5 | 94.1 | 93.9 | 85.8 | 91.5 | 93.5 | 95.1 | 96.1 | 95.3 | 94.9 | 85.4 | 91.3 | 93.3 | 94.9 | 95.3 | 95.5 | 94.4
AU Optronics | PM060MA0_265 [240V] | 225 W, 240 Vac Inverter | 0.225 | 240 | 94.5 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.02 |  |  | 21 | 31.5 | 35 | 0.02 | 0.05 | 0.07 | 0.11 | 0.17 | 0.23 | 87 | 92 | 93.4 | 94.5 | 94.5 | 94.1 | 93.9 | 85.8 | 91.5 | 93.5 | 95.1 | 96.1 | 95.3 | 94.9 | 85.4 | 91.3 | 93.3 | 94.9 | 95.3 | 95.5 | 94.4
AU Optronics | PM060MA0_270 [240V] | 225 W, 240 Vac Inverter | 0.225 | 240 | 94.5 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.02 |  |  | 21 | 31.5 | 35 | 0.02 | 0.05 | 0.07 | 0.11 | 0.17 | 0.23 | 87 | 92 | 93.4 | 94.5 | 94.5 | 94.1 | 93.9 | 85.8 | 91.5 | 93.5 | 95.1 | 96.1 | 95.3 | 94.9 | 85.4 | 91.3 | 93.3 | 94.9 | 95.3 | 95.5 | 94.4
AU Optronics | PM060MA0_275 [240V] | 225 W, 240 Vac Inverter | 0.225 | 240 | 94.5 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.02 |  |  | 21 | 31.5 | 35 | 0.023 | 0.045 | 0.068 | 0.113 | 0.169 | 0.225 | 87 | 92 | 93.4 | 94.5 | 94.5 | 94.1 | 93.9 | 85.8 | 91.5 | 93.5 | 95.1 | 96.1 | 95.3 | 94.9 | 85.4 | 91.3 | 93.3 | 94.9 | 95.3 | 95.5 | 94.4
AU Optronics | PM060MA1_275 [240V] | 225 W, 240 Vac Inverter | 0.225 | 240 | 94.5 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.02 |  |  | 21 | 31.5 | 35 | 0.023 | 0.045 | 0.068 | 0.113 | 0.169 | 0.225 | 87 | 92 | 93.4 | 94.5 | 94.5 | 94.1 | 93.9 | 85.8 | 91.5 | 93.5 | 95.1 | 96.1 | 95.3 | 94.9 | 85.4 | 91.3 | 93.3 | 94.9 | 95.3 | 95.5 | 94.4
AU Optronics | PM060MA2_275 [240V] | 225 W, 240 Vac Inverter | 0.225 | 240 | 94.5 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.02 |  |  | 21 | 31.5 | 35 | 0.023 | 0.045 | 0.068 | 0.113 | 0.169 | 0.225 | 87 | 92 | 93.4 | 94.5 | 94.5 | 94.1 | 93.9 | 85.8 | 91.5 | 93.5 | 95.1 | 96.1 | 95.3 | 94.9 | 85.4 | 91.3 | 93.3 | 94.9 | 95.3 | 95.5 | 94.4
AU Optronics | PM060PA0_235 [240V] | 225 W, 240 Vac Inverter | 0.225 | 240 | 94.5 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.02 |  |  | 21 | 31.5 | 35 | 0.02 | 0.05 | 0.07 | 0.11 | 0.17 | 0.23 | 87 | 92 | 93.4 | 94.5 | 94.5 | 94.1 | 93.9 | 85.8 | 91.5 | 93.5 | 95.1 | 96.1 | 95.3 | 94.9 | 85.4 | 91.3 | 93.3 | 94.9 | 95.3 | 95.5 | 94.4
AU Optronics | PM060PA0_240 [240V] | 225 W, 240 Vac Inverter | 0.225 | 240 | 94.5 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.02 |  |  | 21 | 31.5 | 35 | 0.02 | 0.05 | 0.07 | 0.11 | 0.17 | 0.23 | 87 | 92 | 93.4 | 94.5 | 94.5 | 94.1 | 93.9 | 85.8 | 91.5 | 93.5 | 95.1 | 96.1 | 95.3 | 94.9 | 85.4 | 91.3 | 93.3 | 94.9 | 95.3 | 95.5 | 94.4
AU Optronics | PM060PA0_250 [240V] | 225 W, 240 Vac Inverter | 0.225 | 240 | 94.5 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.02 |  |  | 21 | 31.5 | 35 | 0.02 | 0.05 | 0.07 | 0.11 | 0.17 | 0.23 | 87 | 92 | 93.4 | 94.5 | 94.5 | 94.1 | 93.9 | 85.8 | 91.5 | 93.5 | 95.1 | 96.1 | 95.3 | 94.9 | 85.4 | 91.3 | 93.3 | 94.9 | 95.3 | 95.5 | 94.4
AU Optronics | PM060PA0_255 [240V] | 225 W, 240 Vac Inverter | 0.225 | 240 | 94.5 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.02 |  |  | 21 | 31.5 | 35 | 0.02 | 0.05 | 0.07 | 0.11 | 0.17 | 0.23 | 87 | 92 | 93.4 | 94.5 | 94.5 | 94.1 | 93.9 | 85.8 | 91.5 | 93.5 | 95.1 | 96.1 | 95.3 | 94.9 | 85.4 | 91.3 | 93.3 | 94.9 | 95.3 | 95.5 | 94.4
AU Optronics | PM060PA0_260 [240V] | 225 W, 240 Vac Inverter | 0.225 | 240 | 94.5 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.02 |  |  | 21 | 31.5 | 35 | 0.02 | 0.05 | 0.07 | 0.11 | 0.17 | 0.23 | 87 | 92 | 93.4 | 94.5 | 94.5 | 94.1 | 93.9 | 85.8 | 91.5 | 93.5 | 95.1 | 96.1 | 95.3 | 94.9 | 85.4 | 91.3 | 93.3 | 94.9 | 95.3 | 95.5 | 94.4
AU Optronics | PM240PA0_235 [240V] | 225 W, 240 Vac Inverter | 0.225 | 240 | 94.5 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.02 |  |  | 21 | 31.5 | 35 | 0.0225 | 0.045 | 0.0675 | 0.1125 | 0.1688 | 0.225 | 86.98 | 91.98 | 93.37 | 94.53 | 94.52 | 94.11 | 93.93 | 85.82 | 91.51 | 93.51 | 95.05 | 96.08 | 95.32 | 94.88 | 85.39 | 91.3 | 93.34 | 94.9 | 95.33 | 95.5 | 94.41
AU Optronics | PM240PA0_240 [240V] | 225 W, 240 Vac Inverter | 0.225 | 240 | 94.5 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.02 |  |  | 21 | 31.5 | 35 | 0.0225 | 0.045 | 0.0675 | 0.1125 | 0.1688 | 0.225 | 86.98 | 91.98 | 93.37 | 94.53 | 94.52 | 94.11 | 93.93 | 85.82 | 91.51 | 93.51 | 95.05 | 96.08 | 95.32 | 94.88 | 85.39 | 91.3 | 93.34 | 94.9 | 95.33 | 95.5 | 94.41
AU Optronics | PM240PA0_245 [240V] | 225 W, 240 Vac Inverter | 0.225 | 240 | 94.5 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.02 |  |  | 21 | 31.5 | 35 | 0.0225 | 0.045 | 0.0675 | 0.1125 | 0.1688 | 0.225 | 86.98 | 91.98 | 93.37 | 94.53 | 94.52 | 94.11 | 93.93 | 85.82 | 91.51 | 93.51 | 95.05 | 96.08 | 95.32 | 94.88 | 85.39 | 91.3 | 93.34 | 94.9 | 95.33 | 95.5 | 94.41
AU Optronics | PM245PA0_235 [240V] | 225 W, 240 Vac Inverter | 0.225 | 240 | 94.5 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.02 |  |  | 21 | 31.5 | 35 | 0.0225 | 0.045 | 0.0675 | 0.1125 | 0.1688 | 0.225 | 86.98 | 91.98 | 93.37 | 94.53 | 94.52 | 94.11 | 93.93 | 85.82 | 91.51 | 93.51 | 95.05 | 96.08 | 95.32 | 94.88 | 85.39 | 91.3 | 93.34 | 94.9 | 95.33 | 95.5 | 94.41
AU Optronics | PM245PA0_240 [240V] | 225 W, 240 Vac Inverter | 0.225 | 240 | 94.5 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.02 |  |  | 21 | 31.5 | 35 | 0.0225 | 0.045 | 0.0675 | 0.1125 | 0.1688 | 0.225 | 86.98 | 91.98 | 93.37 | 94.53 | 94.52 | 94.11 | 93.93 | 85.82 | 91.51 | 93.51 | 95.05 | 96.08 | 95.32 | 94.88 | 85.39 | 91.3 | 93.34 | 94.9 | 95.33 | 95.5 | 94.41
AU Optronics | PM245PA0_245 [240V] | 225 W, 240 Vac Inverter | 0.225 | 240 | 94.5 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.02 |  |  | 21 | 31.5 | 35 | 0.0225 | 0.045 | 0.0675 | 0.1125 | 0.1688 | 0.225 | 86.98 | 91.98 | 93.37 | 94.53 | 94.52 | 94.11 | 93.93 | 85.82 | 91.51 | 93.51 | 95.05 | 96.08 | 95.32 | 94.88 | 85.39 | 91.3 | 93.34 | 94.9 | 95.33 | 95.5 | 94.41
AU Optronics | PM245PA0_250 [240V] | 225 W, 240 Vac Inverter | 0.225 | 240 | 94.5 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.02 |  |  | 21 | 31.5 | 35 | 0.0225 | 0.045 | 0.0675 | 0.1125 | 0.1688 | 0.225 | 86.98 | 91.98 | 93.37 | 94.53 | 94.52 | 94.11 | 93.93 | 85.82 | 91.51 | 93.51 | 95.05 | 96.08 | 95.32 | 94.88 | 85.39 | 91.3 | 93.34 | 94.9 | 95.33 | 95.5 | 94.41
AU Optronics | PM245PA0_255 [240V] | 225 W, 240 Vac Inverter | 0.225 | 240 | 94.5 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.02 |  |  | 21 | 31.5 | 35 | 0.02 | 0.05 | 0.07 | 0.11 | 0.17 | 0.23 | 87 | 92 | 93.4 | 94.5 | 94.5 | 94.1 | 93.9 | 85.8 | 91.5 | 93.5 | 95.1 | 96.1 | 95.3 | 94.9 | 85.4 | 91.3 | 93.3 | 94.9 | 95.3 | 95.5 | 94.4
AU Optronics | PM245PA0_260 [240V] | 225 W, 240 Vac Inverter | 0.225 | 240 | 94.5 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.02 |  |  | 21 | 31.5 | 35 | 0.02 | 0.05 | 0.07 | 0.11 | 0.17 | 0.23 | 87 | 92 | 93.4 | 94.5 | 94.5 | 94.1 | 93.9 | 85.8 | 91.5 | 93.5 | 95.1 | 96.1 | 95.3 | 94.9 | 85.4 | 91.3 | 93.3 | 94.9 | 95.3 | 95.5 | 94.4
AU Optronics | PM250MA0_240 [240V] | 225 W, 240 Vac Inverter | 0.225 | 240 | 94.5 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.02 |  |  | 21 | 31.5 | 35 | 0.02 | 0.05 | 0.07 | 0.11 | 0.17 | 0.23 | 87 | 92 | 93.4 | 94.5 | 94.5 | 94.1 | 93.9 | 85.8 | 91.5 | 93.5 | 95.1 | 96.1 | 95.3 | 94.9 | 85.4 | 91.3 | 93.3 | 94.9 | 95.3 | 95.5 | 94.4
AU Optronics | PM250MA0_245 [240V] | 225 W, 240 Vac Inverter | 0.225 | 240 | 94.5 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.02 |  |  | 21 | 31.5 | 35 | 0.0225 | 0.045 | 0.0675 | 0.1125 | 0.1688 | 0.225 | 86.98 | 91.98 | 93.37 | 94.53 | 94.52 | 94.11 | 93.93 | 85.82 | 91.51 | 93.51 | 95.05 | 96.08 | 95.32 | 94.88 | 85.39 | 91.3 | 93.34 | 94.9 | 95.33 | 95.5 | 94.41
AU Optronics | PM250MA0_250 [240V] | 225 W, 240 Vac Inverter | 0.225 | 240 | 94.5 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.02 |  |  | 21 | 31.5 | 35 | 0.0225 | 0.045 | 0.0675 | 0.1125 | 0.1688 | 0.225 | 86.98 | 91.98 | 93.37 | 94.53 | 94.52 | 94.11 | 93.93 | 85.82 | 91.51 | 93.51 | 95.05 | 96.08 | 95.32 | 94.88 | 85.39 | 91.3 | 93.34 | 94.9 | 95.33 | 95.5 | 94.41
AU Optronics | PM250MA0_255 [240V] | 225 W, 240 Vac Inverter | 0.225 | 240 | 94.5 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.02 |  |  | 21 | 31.5 | 35 | 0.0225 | 0.045 | 0.0675 | 0.1125 | 0.1688 | 0.225 | 86.98 | 91.98 | 93.37 | 94.53 | 94.52 | 94.11 | 93.93 | 85.82 | 91.51 | 93.51 | 95.05 | 96.08 | 95.32 | 94.88 | 85.39 | 91.3 | 93.34 | 94.9 | 95.33 | 95.5 | 94.41
AU Optronics | PM250MA0_260 [240V] | 225 W, 240 Vac Inverter | 0.225 | 240 | 94.5 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.02 |  |  | 21 | 31.5 | 35 | 0.0225 | 0.045 | 0.0675 | 0.1125 | 0.1688 | 0.225 | 86.98 | 91.98 | 93.37 | 94.53 | 94.52 | 94.11 | 93.93 | 85.82 | 91.51 | 93.51 | 95.05 | 96.08 | 95.32 | 94.88 | 85.39 | 91.3 | 93.34 | 94.9 | 95.33 | 95.5 | 94.41
AU Optronics | PM250MA0_265 [240V] | 225 W, 240 Vac Inverter | 0.225 | 240 | 94.5 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.02 |  |  | 21 | 31.5 | 35 | 0.0225 | 0.045 | 0.0675 | 0.1125 | 0.1688 | 0.225 | 86.98 | 91.98 | 93.37 | 94.53 | 94.52 | 94.11 | 93.93 | 85.82 | 91.51 | 93.51 | 95.05 | 96.08 | 95.32 | 94.88 | 85.39 | 91.3 | 93.34 | 94.9 | 95.33 | 95.5 | 94.41
AU Optronics | PM250MA0_270 [240V] | 225 W, 240 Vac Inverter | 0.225 | 240 | 94.5 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.02 |  |  | 21 | 31.5 | 35 | 0.02 | 0.05 | 0.07 | 0.11 | 0.17 | 0.23 | 87 | 92 | 93.4 | 94.5 | 94.5 | 94.1 | 93.9 | 85.8 | 91.5 | 93.5 | 95.1 | 96.1 | 95.3 | 94.9 | 85.4 | 91.3 | 93.3 | 94.9 | 95.3 | 95.5 | 94.4
AU Optronics | PM250MA0_275 [240V] | 225 W, 240 Vac Inverter | 0.225 | 240 | 94.5 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.02 |  |  | 21 | 31.5 | 35 | 0.023 | 0.045 | 0.068 | 0.113 | 0.169 | 0.225 | 87 | 92 | 93.4 | 94.5 | 94.5 | 94.1 | 93.9 | 85.8 | 91.5 | 93.5 | 95.1 | 96.1 | 95.3 | 94.9 | 85.4 | 91.3 | 93.3 | 94.9 | 95.3 | 95.5 | 94.4
AU Optronics | PM250MA1_275 [240V] | 225 W, 240 Vac Inverter | 0.225 | 240 | 94.5 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.02 |  |  | 21 | 31.5 | 35 | 0.023 | 0.045 | 0.068 | 0.113 | 0.169 | 0.225 | 87 | 92 | 93.4 | 94.5 | 94.5 | 94.1 | 93.9 | 85.8 | 91.5 | 93.5 | 95.1 | 96.1 | 95.3 | 94.9 | 85.4 | 91.3 | 93.3 | 94.9 | 95.3 | 95.5 | 94.4
AU Optronics | PM250MA2_275 [240V] | 225 W, 240 Vac Inverter | 0.225 | 240 | 94.5 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.02 |  |  | 21 | 31.5 | 35 | 0.023 | 0.045 | 0.068 | 0.113 | 0.169 | 0.225 | 87 | 92 | 93.4 | 94.5 | 94.5 | 94.1 | 93.9 | 85.8 | 91.5 | 93.5 | 95.1 | 96.1 | 95.3 | 94.9 | 85.4 | 91.3 | 93.3 | 94.9 | 95.3 | 95.5 | 94.4
AU Optronics | PM060MA1_240 [208V] | 240 W, 208 Vac Inverter | 0.24 | 208 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6
AU Optronics | PM060MA1_240 [240V] | 240 W, 240 Vac Inverter | 0.24 | 240 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6
AU Optronics | PM060MA1_245 [208V] | 240 W, 208 Vac Inverter | 0.24 | 208 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6
AU Optronics | PM060MA1_245 [240V] | 240 W, 240 Vac Inverter | 0.24 | 240 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6
AU Optronics | PM060MA1_250 [208V] | 240 W, 208 Vac Inverter | 0.24 | 208 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6
AU Optronics | PM060MA1_250 [240V] | 240 W, 240 Vac Inverter | 0.24 | 240 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6
AU Optronics | PM060MA1_255 [208V] | 240 W, 208 Vac Inverter | 0.24 | 208 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6
AU Optronics | PM060MA1_255 [240V] | 240 W, 240 Vac Inverter | 0.24 | 240 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6
AU Optronics | PM060MA1_260 [208V] | 240 W, 208 Vac Inverter | 0.24 | 208 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6
AU Optronics | PM060MA1_260 [240V] | 240 W, 240 Vac Inverter | 0.24 | 240 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6
AU Optronics | PM060MA1_265 [208V] | 240 W, 208 Vac Inverter | 0.24 | 208 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6
AU Optronics | PM060MA1_265 [240V] | 240 W, 240 Vac Inverter | 0.24 | 240 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6
AU Optronics | PM060MA1_270 [208V] | 240 W, 208 Vac Inverter | 0.24 | 208 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6
AU Optronics | PM060MA1_270 [240V] | 240 W, 240 Vac Inverter | 0.24 | 240 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6
AU Optronics | PM060MA2_240 [208V] | 240 W, 208 Vac Inverter | 0.24 | 208 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6
AU Optronics | PM060MA2_240 [240V] | 240 W, 240 Vac Inverter | 0.24 | 240 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6
AU Optronics | PM060MA2_245 [208V] | 240 W, 208 Vac Inverter | 0.24 | 208 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6
AU Optronics | PM060MA2_245 [240V] | 240 W, 240 Vac Inverter | 0.24 | 240 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6
AU Optronics | PM060MA2_250 [208V] | 240 W, 208 Vac Inverter | 0.24 | 208 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6
AU Optronics | PM060MA2_250 [240V] | 240 W, 240 Vac Inverter | 0.24 | 240 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6
AU Optronics | PM060MA2_255 [208V] | 240 W, 208 Vac Inverter | 0.24 | 208 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6
AU Optronics | PM060MA2_255 [240V] | 240 W, 240 Vac Inverter | 0.24 | 240 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6
AU Optronics | PM060MA2_260 [208V] | 240 W, 208 Vac Inverter | 0.24 | 208 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6
AU Optronics | PM060MA2_260 [240V] | 240 W, 240 Vac Inverter | 0.24 | 240 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6
AU Optronics | PM060MA2_265 [208V] | 240 W, 208 Vac Inverter | 0.24 | 208 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6
AU Optronics | PM060MA2_265 [240V] | 240 W, 240 Vac Inverter | 0.24 | 240 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6
AU Optronics | PM060MA2_270 [208V] | 240 W, 208 Vac Inverter | 0.24 | 208 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6
AU Optronics | PM060MA2_270 [240V] | 240 W, 240 Vac Inverter | 0.24 | 240 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6
AU Optronics | PM060PA0_245 [240V] | 225 W, 240 Vac Inverter | 0.24 | 240 | 94.5 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6
AU Optronics | PM060PA1_235 [208V] | 240 W, 208 Vac Inverter | 0.24 | 208 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6
AU Optronics | PM060PA1_235 [240V] | 240 W, 240 Vac Inverter | 0.24 | 240 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6
AU Optronics | PM060PA1_240 [208V] | 240 W, 208 Vac Inverter | 0.24 | 208 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6
AU Optronics | PM060PA1_240 [240V] | 240 W, 240 Vac Inverter | 0.24 | 240 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6
AU Optronics | PM060PA1_245 [208V] | 240 W, 208/Vac Inverter | 0.24 | 208 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6
AU Optronics | PM060PA1_245 [240V] | 240 W, 240 Vac Inverter | 0.24 | 240 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6
AU Optronics | PM060PA1_250 [208V] | 240 W, 208 Vac Inverter | 0.24 | 208 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6
AU Optronics | PM060PA1_250 [240V] | 240 W, 240 Vac Inverter | 0.24 | 240 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6
AU Optronics | PM060PA1_255 [208V] | 240 W, 208/Vac Inverter | 0.24 | 208 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6
AU Optronics | PM060PA1_255 [240V] | 240 W, 240 Vac Inverter | 0.24 | 240 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6
AU Optronics | PM060PA1_260 [208V] | 240 W, 208 Vac Inverter | 0.24 | 208 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6
AU Optronics | PM060PA1_260 [240V] | 240 W, 240 Vac Inverter | 0.24 | 240 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6
AU Optronics | PM060PA2_235 [208V] | 240 W, 208 Vac Inverter | 0.24 | 208 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6
AU Optronics | PM060PA2_235 [240V] | 240 W, 240 Vac Inverter | 0.24 | 240 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6
AU Optronics | PM060PA2_240 [208V] | 240 W, 208 Vac Inverter | 0.24 | 208 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6
AU Optronics | PM060PA2_240 [240V] | 240 W, 240 Vac Inverter | 0.24 | 240 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6
AU Optronics | PM060PA2_245 [208V] | 240 W, 208 Vac Inverter | 0.24 | 208 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6
AU Optronics | PM060PA2_245 [240V] | 240 W, 240 Vac Inverter | 0.24 | 240 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6
AU Optronics | PM060PA2_250 [208V] | 240 W, 208 Vac Inverter | 0.24 | 208 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6
AU Optronics | PM060PA2_250 [240V] | 240 W, 240 Vac Inverter | 0.24 | 240 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6
AU Optronics | PM060PA2_255 [208V] | 240 W, 208 Vac Inverter | 0.24 | 208 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6
AU Optronics | PM060PA2_255 [240V] | 240 W, 240 Vac Inverter | 0.24 | 240 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6
AU Optronics | PM060PA2_260 [208V] | 240 W, 208 Vac Inverter | 0.24 | 208 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6
AU Optronics | PM060PA2_260 [240V] | 240 W, 240 Vac Inverter | 0.24 | 240 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6
AU Optronics | PM245PA1_235 [240V] | 240 W, 240 Vac Inverter | 0.24 | 240 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.0238 | 0.0476 | 0.0714 | 0.119 | 0.1785 | 0.238 | 88.74 | 93.68 | 94.03 | 94.87 | 94.98 | 94.74 | 94.52 | 87.73 | 93.5 | 94.82 | 95.13 | 95.52 | 95.46 | 94.94 | 86.91 | 93.18 | 94.64 | 95.08 | 95.65 | 95.69 | 94.94
AU Optronics | PM245PA1_240 [240V] | 240 W, 240 Vac Inverter | 0.24 | 240 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.0238 | 0.0476 | 0.0714 | 0.119 | 0.1785 | 0.238 | 88.74 | 93.68 | 94.03 | 94.87 | 94.98 | 94.74 | 94.52 | 87.73 | 93.5 | 94.82 | 95.13 | 95.52 | 95.46 | 94.94 | 86.91 | 93.18 | 94.64 | 95.08 | 95.65 | 95.69 | 94.94
AU Optronics | PM245PA1_245 [240V] | 240 W, 240 Vac Inverter | 0.24 | 240 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.0238 | 0.0476 | 0.0714 | 0.119 | 0.1785 | 0.238 | 88.74 | 93.68 | 94.03 | 94.87 | 94.98 | 94.74 | 94.52 | 87.73 | 93.5 | 94.82 | 95.13 | 95.52 | 95.46 | 94.94 | 86.91 | 93.18 | 94.64 | 95.08 | 95.65 | 95.69 | 94.94
AU Optronics | PM245PA1_250 [240V] | 240 W, 240 Vac Inverter | 0.24 | 240 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.0238 | 0.0476 | 0.0714 | 0.119 | 0.1785 | 0.238 | 88.74 | 93.68 | 94.03 | 94.87 | 94.98 | 94.74 | 94.52 | 87.73 | 93.5 | 94.82 | 95.13 | 95.52 | 95.46 | 94.94 | 86.91 | 93.18 | 94.64 | 95.08 | 95.65 | 95.69 | 94.94
AU Optronics | PM245PA1_255 [208V] | 240 W, 208 Vac Inverter | 0.24 | 208 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6
AU Optronics | PM245PA1_255 [240V] | 240 W, 240 Vac Inverter | 0.24 | 240 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6
AU Optronics | PM245PA1_260 [208V] | 240 W, 208 Vac Inverter | 0.24 | 208 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6
AU Optronics | PM245PA1_260 [240V] | 240 W, 240 Vac Inverter | 0.24 | 240 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6
AU Optronics | PM245PA2_235 [208V] | 240 W, 208 Vac Inverter | 0.24 | 208 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6
AU Optronics | PM245PA2_235 [240V] | 240 W, 240 Vac Inverter | 0.24 | 240 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6
AU Optronics | PM245PA2_240 [208V] | 240 W, 208 Vac Inverter | 0.24 | 208 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6
AU Optronics | PM245PA2_240 [240V] | 240 W, 240 Vac Inverter | 0.24 | 240 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6
AU Optronics | PM245PA2_245 [208V] | 240 W, 208 Vac Inverter | 0.24 | 208 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6
AU Optronics | PM245PA2_245 [240V] | 240 W, 240 Vac Inverter | 0.24 | 240 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6
AU Optronics | PM245PA2_250 [208V] | 240 W, 208 Vac Inverter | 0.24 | 208 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6
AU Optronics | PM245PA2_250 [240V] | 240 W, 240 Vac Inverter | 0.24 | 240 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6
AU Optronics | PM245PA2_255 [208V] | 240 W, 208 Vac Inverter | 0.24 | 208 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6
AU Optronics | PM245PA2_255 [240V] | 240 W, 240 Vac Inverter | 0.24 | 240 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6
AU Optronics | PM245PA2_260 [208V] | 240 W, 208 Vac Inverter | 0.24 | 208 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6
AU Optronics | PM245PA2_260 [240V] | 240 W, 240 Vac Inverter | 0.24 | 240 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6
AU Optronics | PM250MA1_240 [240V] | 240 W, 240 Vac Inverter | 0.24 | 240 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6
AU Optronics | PM250MA1_245 [240V] | 240 W, 240 Vac Inverter | 0.24 | 240 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.0238 | 0.0476 | 0.0714 | 0.119 | 0.1785 | 0.238 | 88.74 | 93.68 | 94.03 | 94.87 | 94.98 | 94.74 | 94.52 | 87.73 | 93.5 | 94.82 | 95.13 | 95.52 | 95.46 | 94.94 | 86.91 | 93.18 | 94.64 | 95.08 | 95.65 | 95.69 | 94.94
AU Optronics | PM250MA1_250 [240V] | 240 W, 240 Vac Inverter | 0.24 | 240 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.0238 | 0.0476 | 0.0714 | 0.119 | 0.1785 | 0.238 | 88.74 | 93.68 | 94.03 | 94.87 | 94.98 | 94.74 | 94.52 | 87.73 | 93.5 | 94.82 | 95.13 | 95.52 | 95.46 | 94.94 | 86.91 | 93.18 | 94.64 | 95.08 | 95.65 | 95.69 | 94.94
AU Optronics | PM250MA1_255 [240V] | 240 W, 240 Vac Inverter | 0.24 | 240 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.0238 | 0.0476 | 0.0714 | 0.119 | 0.1785 | 0.238 | 88.74 | 93.68 | 94.03 | 94.87 | 94.98 | 94.74 | 94.52 | 87.73 | 93.5 | 94.82 | 95.13 | 95.52 | 95.46 | 94.94 | 86.91 | 93.18 | 94.64 | 95.08 | 95.65 | 95.69 | 94.94
AU Optronics | PM250MA1_260 [240V] | 240 W, 240 Vac Inverter | 0.24 | 240 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.0238 | 0.0476 | 0.0714 | 0.119 | 0.1785 | 0.238 | 88.74 | 93.68 | 94.03 | 94.87 | 94.98 | 94.74 | 94.52 | 87.73 | 93.5 | 94.82 | 95.13 | 95.52 | 95.46 | 94.94 | 86.91 | 93.18 | 94.64 | 95.08 | 95.65 | 95.69 | 94.94
AU Optronics | PM250MA1_265 [208V] | 240 W, 208 Vac Inverter | 0.24 | 208 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.0238 | 0.0476 | 0.0714 | 0.119 | 0.1785 | 0.238 | 88.74 | 93.68 | 94.03 | 94.87 | 94.98 | 94.74 | 94.52 | 87.73 | 93.5 | 94.82 | 95.13 | 95.52 | 95.46 | 94.94 | 86.91 | 93.18 | 94.64 | 95.08 | 95.65 | 95.69 | 94.94
AU Optronics | PM250MA1_265 [240V] | 240 W, 240 Vac Inverter | 0.24 | 240 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.0238 | 0.0476 | 0.0714 | 0.119 | 0.1785 | 0.238 | 88.74 | 93.68 | 94.03 | 94.87 | 94.98 | 94.74 | 94.52 | 87.73 | 93.5 | 94.82 | 95.13 | 95.52 | 95.46 | 94.94 | 86.91 | 93.18 | 94.64 | 95.08 | 95.65 | 95.69 | 94.94
AU Optronics | PM250MA1_270 [208V] | 240 W, 208 Vac Inverter | 0.24 | 208 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6
AU Optronics | PM250MA1_270 [240V] | 240 W, 240 Vac Inverter | 0.24 | 240 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6
AU Optronics | PM250MA2_240 [208V] | 240 W, 208 Vac Inverter | 0.24 | 208 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6
AU Optronics | PM250MA2_240 [240V] | 240 W, 240 Vac Inverter | 0.24 | 240 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6
AU Optronics | PM250MA2_245 [208V] | 240 W, 208 Vac Inverter | 0.24 | 208 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6
AU Optronics | PM250MA2_245 [240V] | 240 W, 240 Vac Inverter | 0.24 | 240 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6
AU Optronics | PM250MA2_250 [208V] | 240 W, 208 Vac Inverter | 0.24 | 208 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6
AU Optronics | PM250MA2_250 [240V] | 240 W, 240 Vac Inverter | 0.24 | 240 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6
AU Optronics | PM250MA2_255 [208V] | 240 W, 208 Vac Inverter | 0.24 | 208 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6
AU Optronics | PM250MA2_255 [240V] | 240 W, 240 Vac Inverter | 0.24 | 240 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6
AU Optronics | PM250MA2_260 [208V] | 240 W, 208/Vac Inverter | 0.24 | 208 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6
AU Optronics | PM250MA2_260 [240V] | 240 W, 240 Vac Inverter | 0.24 | 240 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6
AU Optronics | PM250MA2_265 [208V] | 240 W, 208 Vac Inverter | 0.24 | 208 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6
AU Optronics | PM250MA2_265 [240V] | 240 W, 240 Vac Inverter | 0.24 | 240 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6
AU Optronics | PM250MA2_270 [208V] | 240 W, 208 Vac Inverter | 0.24 | 208 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6
AU Optronics | PM250MA2_270 [240V] | 240 W, 240 Vac Inverter | 0.24 | 240 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6
Auxin Solar | AXU-PV1500U [208V] | 1.5 kW, 208 Vac Utility Interactive Inverter | 1.55 | 208 | 94.5 | Y | N |  | 0.21 |  |  | 100 | 325 | 360 | 0.155 | 0.31 | 0.465 | 0.775 | 1.163 | 1.55 | 84.46 | 90.49 | 92.52 | 94.25 | 94.92 | 95.02 | 93.86 | 85.04 | 91.04 | 93.19 | 94.79 | 95.41 | 95.53 | 94.38 | 85.31 | 91.19 | 93.54 | 95.02 | 95.55 | 95.76 | 94.58
Auxin Solar | AXU-PV1500U [240V] | 1.5 kW, 240 Vac Utility Interactive Inverter | 1.55 | 240 | 94.5 | Y | N |  | 0.32 |  |  | 100 | 325 | 360 | 0.155 | 0.31 | 0.465 | 0.775 | 1.163 | 1.55 | 84.62 | 90.46 | 92.57 | 94.42 | 95.07 | 95.25 | 93.99 | 84.89 | 90.97 | 93.04 | 94.81 | 95.51 | 95.73 | 94.42 | 85.22 | 91.38 | 93.44 | 95.12 | 95.65 | 95.93 | 94.66
Auxin Solar | AXU-PV2000U [208V] | 2 kW, 208 Vac Utility Interactive Inverter | 2.06 | 208 | 95.5 | Y | N |  | 0.29 |  |  | 100 | 325 | 360 | 0.206 | 0.412 | 0.618 | 1.03 | 1.545 | 2.06 | 88.28 | 93.12 | 94.41 | 95.27 | 95.43 | 95.37 | 94.87 | 89.63 | 93.68 | 94.91 | 95.73 | 95.84 | 95.8 | 95.34 | 89.74 | 94.01 | 95.11 | 96.13 | 96.38 | 96.07 | 95.77
Auxin Solar | AXU-PV2000U [240V] | 2 kW, 240 Vac Utility Interactive Inverter | 2.06 | 240 | 95 | Y | N |  | 0.36 |  |  | 100 | 325 | 360 | 0.206 | 0.412 | 0.618 | 1.03 | 1.545 | 2.06 | 86.91 | 92.14 | 93.78 | 94.94 | 95.3 | 95.37 | 94.55 | 87.84 | 92.87 | 94.26 | 95.56 | 95.79 | 95.73 | 95.09 | 88.1 | 93.05 | 94.37 | 95.71 | 96 | 95.94 | 95.28
Auxin Solar | AXU-PV3000U [208V] | 3 kW, 208 Vac Utility Interactive Inverter | 3 | 208 | 95.5 | Y | N |  | 0.18 |  |  | 100 | 325 | 360 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 91.57 | 94.41 | 95.16 | 95.47 | 95.31 | 94.62 | 95.1 | 92.05 | 94.92 | 95.58 | 95.89 | 95.76 | 95.37 | 95.56 | 92.22 | 95.17 | 95.79 | 96.25 | 95.93 | 95.8 | 95.78
Auxin Solar | AXU-PV3000U [240V] | 3 kW, 240 Vac Utility Interactive Inverter | 3.01 | 240 | 95.5 | Y | N |  | 0.25 |  |  | 100 | 325 | 360 | 0.301 | 0.602 | 0.903 | 1.505 | 2.258 | 3.01 | 90 | 93.9 | 94.85 | 95.4 | 95.31 | 94.83 | 94.97 | 90.64 | 94.34 | 95.34 | 95.79 | 95.87 | 95.6 | 95.49 | 91 | 94.59 | 95.44 | 95.97 | 96.01 | 95.77 | 95.65
Auxin Solar | AXN-PV4000U [208V] | 4 kW, 208 Vac Utility Interactive Inverter | 3.98 | 208 | 95.5 | Y | N |  | 0.18 |  |  | 100 | 325 | 360 | 0.398 | 0.796 | 1.194 | 1.99 | 2.985 | 3.98 | 90.53 | 94.32 | 95.17 | 95.44 | 95.41 | 95.16 | 95.13 | 91.58 | 94.87 | 95.63 | 96.05 | 96 | 95.45 | 95.7 | 91.82 | 95.03 | 95.8 | 96.45 | 96.31 | 95.76 | 96.01
Auxin Solar | AXN-PV4000U [240V] | 4 kW, 240 Vac Utility Interactive Inverter | 3.99 | 240 | 96 | Y | N |  | 0.25 |  |  | 100 | 325 | 360 | 0.399 | 0.798 | 1.197 | 1.995 | 2.993 | 3.99 | 90.55 | 94.3 | 95.24 | 95.69 | 95.74 | 95.56 | 95.38 | 91.53 | 94.95 | 95.81 | 96.33 | 96.33 | 96.05 | 95.99 | 91.95 | 95.23 | 95.96 | 96.4 | 96.48 | 96.25 | 96.15
Ballard Power Systems | EPC-PV-208-30KW [208V] | Utility Interactive 208 Vac , 30 kW PV Power Converter System | 30 | 208 | 93 | Y | N |  | 32 |  |  | 290 | 322 | 420 | 3 | 6 | 9 | 15 | 22.5 | 30 | 83.72 | 90.23 | 92.39 | 93.75 | 94.13 | 93.87 | 93.22 | 83.3 | 89.7 | 92.12 | 93.58 | 94 | 93.77 | 93.03 | 81.74 | 89.02 | 91.17 | 93 | 93.45 | 93.37 | 92.39
Ballard Power Systems | EPC-PV-480-30KW [480V] | Utility Interactive 480 Vac, 30 kW PV Power Converter System | 30 | 480 | 93 | Y | N |  | 27 |  |  | 290 | 322 | 420 | 3 | 6 | 9 | 15 | 22.5 | 30 | 83.8 | 90.14 | 92.4 | 93.85 | 94.24 | 93.93 | 93.3 | 83.23 | 89.86 | 92.1 | 93.66 | 94.07 | 93.8 | 93.09 | 81.53 | 88.67 | 91.17 | 93.05 | 93.5 | 93.3 | 92.39
Ballard Power Systems | EPC-PV-208-75KW | Utility Interactive 75 kW PV Power Converter System | 75 |  | 91.5 | Y | N |  | 107 |  |  | 330 | 352 | 420 | 7.5 | 15 | 22.5 | 37.5 | 56.25 | 75 | 81.8 | 88.6 | 91 | 92.6 | 93 | 92.8 | 92 | 81.2 | 88.3 | 90.7 | 92.4 | 92.9 | 92.7 | 91.8 | 79.9 | 87.5 | 90 | 91.9 | 92.4 | 92.2 | 91.2
Ballard Power Systems | EPC-PV-480-75KW [480V] | Utility Interactive 480 Vac, 75 kW PV Power Converter System | 75 | 480 | 91.5 | Y | N |  | 110 |  |  | 330 | 352 | 420 | 7.5 | 15 | 22.5 | 37.5 | 56.25 | 75 | 81.4 | 88.5 | 90.9 | 92.6 | 93.1 | 93 | 92 | 81.1 | 88.2 | 90.7 | 92.4 | 92.9 | 92.8 | 91.9 | 79.7 | 87.5 | 90.1 | 92 | 92.5 | 92.3 | 91.3
Beacon Power | M4 | 4 kW Power Conversion System | 4 |  | 90 | N | N |  | 14 |  |  | 46.5 | 54.5 | 58 | 0.4 | 0.8 | 1.2 | 2 | 3 | 4 | 88.63 | 92.11 | 92.88 | 92.82 | 91.6 | 89.17 | 91.79 | 86.23 | 90.4 | 91.55 | 91.38 | 89.29 | 87.38 | 89.84 | 84.47 | 89.04 | 90.58 | 90.79 | 88.45 | 86.39 | 88.97
Beacon Power | M4 Plus | 4 kW Power Conversion System with Meter | 4 |  | 91.5 | Y | N |  | 14 |  |  | 46.5 | 54.5 | 58 | 0.4 | 0.8 | 1.2 | 2 | 3 | 4 | 89.16 | 92.55 | 93.39 | 93.49 | 92.37 | 89.68 | 92.48 | 86.23 | 90.71 | 91.58 | 91.8 | 90.08 | 87.97 | 90.39 | 85.9 | 90.28 | 91.4 | 93.28 | 91.68 | 88.3 | 91.51
Beacon Power | M5 | 5 kW Power Conversion System | 5 |  | 89 | N | N |  | 14 |  |  | 46.5 | 54.5 | 58 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 89.99 | 92.65 | 93.04 | 92.33 | 89.68 | 87.6 | 90.7 | 87.66 | 91.12 | 91.61 | 90.41 | 87.83 | 85.17 | 88.85 | 86.14 | 90.07 | 90.87 | 90.27 | 87.18 | 83.21 | 88.18
Beacon Power | M5 Plus | 5 kW Power Conversion System with Meter | 5 |  | 90 | Y | N |  | 14 |  |  | 46.5 | 54.5 | 58 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 90.49 | 93.1 | 93.64 | 92.85 | 90.35 | 88.11 | 91.3 | 87.93 | 91.36 | 91.96 | 90.96 | 88.65 | 85.7 | 89.49 | 87.48 | 91.09 | 91.81 | 91.38 | 88.89 | 85.33 | 89.64
Beijing Kinglong New Energy Technology | Sunteams 1500 [208V] | 1500 W, 208 Vac Utility Interactive Inverter | 1.5 | 208 | 95 | Y | N |  | 0.1 |  |  | 100 | 300 | 360 | 0.15 | 0.3 | 0.45 | 0.75 | 1.13 | 1.5 | 86.5 | 91.8 | 93.5 | 95 | 94.9 | 95.1 | 94.3 | 88.8 | 93.4 | 94.7 | 95.7 | 95.9 | 95.8 | 95.3 | 90.7 | 94.2 | 95.6 | 96.4 | 96.3 | 96.4 | 95.9
Beijing Kinglong New Energy Technology | Sunteams 1500 [240V] | 1500 W, 240 Vac Utility Interactive Inverter | 1.5 | 240 | 95 | Y | N |  | 0.13 |  |  | 100 | 300 | 360 | 0.15 | 0.3 | 0.45 | 0.75 | 1.13 | 1.5 | 85.9 | 91.4 | 93.2 | 94.8 | 95 | 95.2 | 94.2 | 87.5 | 92.8 | 94.3 | 95.6 | 96 | 96 | 95.2 | 90.4 | 94 | 95 | 96 | 96.4 | 96.4 | 95.8
Beijing Kinglong New Energy Technology | Sunteams 2000 [208V] | 2000 W, 208 Vac Utility Interactive Inverter | 2 | 208 | 95.5 | Y | N |  | 0.13 |  |  | 100 | 350 | 400 | 0.2 | 0.4 | 0.6 | 1 | 1.5 | 2 | 90.1 | 93.6 | 94.7 | 95.3 | 95.4 | 95.2 | 95 | 92.6 | 95 | 96 | 96.1 | 96.2 | 96 | 95.9 | 91.6 | 94.7 | 95.4 | 95.9 | 96.2 | 95.8 | 95.7
Beijing Kinglong New Energy Technology | Sunteams 2000 [240V] | 2000 W, 240 Vac Utility Interactive Inverter | 2 | 240 | 96 | Y | N |  | 0.17 |  |  | 100 | 380 | 400 | 0.2 | 0.4 | 0.6 | 1 | 1.5 | 2 | 89.6 | 93.2 | 94.5 | 95.3 | 95.6 | 95.5 | 95 | 92.2 | 94.7 | 96 | 96.5 | 96.7 | 96.4 | 96.3 | 94.1 | 95.4 | 96.2 | 96.5 | 96.5 | 96.4 | 96.3
Beijing Kinglong New Energy Technology | Sunteams 3000 [208V] | 2800 W, 208 Vac Utility Interactive Inverter | 2.8 | 208 | 96 | Y | N |  | 0.11 |  |  | 100 | 350 | 400 | 0.28 | 0.56 | 0.84 | 1.4 | 2.1 | 2.8 | 90.3 | 93.4 | 94.8 | 95.6 | 95.6 | 95.6 | 95.2 | 93.1 | 95.7 | 96.3 | 96.7 | 96.5 | 95.9 | 96.3 | 92 | 95 | 95.9 | 96.5 | 96.4 | 96 | 96.1
Beijing Kinglong New Energy Technology | Sunteams 3000 [240V] | 2800 W, 240 Vac Utility Interactive Inverter | 2.8 | 240 | 96 | Y | N |  | 0.15 |  |  | 100 | 380 | 440 | 0.28 | 0.56 | 0.84 | 1.4 | 2.1 | 2.8 | 89.1 | 93 | 94.5 | 95.5 | 95.8 | 95.8 | 95.2 | 93.1 | 95.9 | 96.3 | 96.9 | 96.9 | 96.9 | 96.7 | 92.7 | 95.6 | 96.7 | 96.9 | 96.9 | 96.9 | 96.6
Beijing Kinglong New Energy Technology | Sunteams 4000 [208V] | 4000 W, 208 Vac Utility Interactive Inverter | 4 | 208 | 97 | Y | N |  | 0.07 |  |  | 100 | 350 | 440 | 0.4 | 0.8 | 1.2 | 2 | 3 | 4 | 93.7 | 96.1 | 96.8 | 97.2 | 97.1 | 96.8 | 96.9 | 95.4 | 97.1 | 97.5 | 97.6 | 97.4 | 97.2 | 97.4 | 94 | 96.3 | 97 | 97.4 | 97.3 | 97.1 | 97.1
Beijing Kinglong New Energy Technology | Sunteams 4000 [240V] | 4000 W, 240 Vac Utility Interactive Inverter | 4 | 240 | 97.5 | Y | N |  | 0.11 |  |  | 100 | 380 | 440 | 0.4 | 0.8 | 1.2 | 2 | 3 | 4 | 93.1 | 95.8 | 96.6 | 97.3 | 97.4 | 97.2 | 97 | 95.5 | 97.1 | 97.6 | 97.9 | 97.8 | 97.5 | 97.6 | 94.6 | 96.7 | 97.4 | 97.6 | 97.6 | 97.4 | 97.4
Beijing Kinglong New Energy Technology | Sunteams 5000 [208V] | 4600 W, 208 Vac Utility Interactive Inverter | 4.6 | 208 | 97 | Y | N |  | 0.07 |  |  | 100 | 350 | 440 | 0.46 | 0.92 | 1.38 | 2.3 | 3.45 | 4.6 | 93.8 | 96.1 | 96.8 | 97.1 | 96.9 | 96.4 | 96.7 | 95.3 | 97 | 97.5 | 97.5 | 97.3 | 96.8 | 97.2 | 94 | 96.3 | 96.9 | 97.2 | 97.1 | 96.7 | 96.9
Beijing Kinglong New Energy Technology | Sunteams 5000 [240V] | 4600 W, 240 Vac Utility Interactive Inverter | 4.6 | 240 | 97.5 | Y | N |  | 0.1 |  |  | 100 | 380 | 440 | 0.46 | 0.92 | 1.38 | 2.3 | 3.45 | 4.6 | 93.3 | 95.8 | 96.7 | 97.2 | 97.2 | 96.9 | 96.9 | 95.4 | 96.9 | 97.6 | 97.9 | 97.8 | 97.5 | 97.6 | 94.6 | 96.7 | 97.2 | 97.6 | 97.6 | 97.4 | 97.4
Beyond Building Group | SR1500TLI [208V] | 1.5 kW, 208 Vac Utility Interactive Inverter | 1.55 | 208 | 94.5 | Y | N |  | 0.21 |  |  | 100 | 325 | 360 | 0.155 | 0.31 | 0.465 | 0.775 | 1.163 | 1.55 | 84.46 | 90.49 | 92.52 | 94.25 | 94.92 | 95.02 | 93.86 | 85.04 | 91.04 | 93.19 | 94.79 | 95.41 | 95.53 | 94.38 | 85.31 | 91.19 | 93.54 | 95.02 | 95.55 | 95.76 | 94.58
Beyond Building Group | SR1500TLI [240V] | 1.5 kW, 240 Vac Utility Interactive Inverter | 1.55 | 240 | 94.5 | Y | N |  | 0.32 |  |  | 100 | 325 | 360 | 0.155 | 0.31 | 0.465 | 0.775 | 1.163 | 1.55 | 84.62 | 90.46 | 92.57 | 94.42 | 95.07 | 95.25 | 93.99 | 84.89 | 90.97 | 93.04 | 94.81 | 95.51 | 95.73 | 94.42 | 85.22 | 91.38 | 93.44 | 95.12 | 95.65 | 95.93 | 94.66
Beyond Building Group | SR2000TLI [208V] | 2 kW, 208 Vac Utility Interactive Inverter | 2.06 | 208 | 95.5 | Y | N |  | 0.29 |  |  | 100 | 325 | 360 | 0.206 | 0.412 | 0.618 | 1.03 | 1.545 | 2.06 | 88.28 | 93.12 | 94.41 | 95.27 | 95.43 | 95.37 | 94.87 | 89.63 | 93.68 | 94.91 | 95.73 | 95.84 | 95.8 | 95.34 | 89.74 | 94.01 | 95.11 | 96.13 | 96.38 | 96.07 | 95.77
Beyond Building Group | SR2000TLI [240V] | 2 kW, 240 Vac Utility Interactive Inverter | 2.06 | 240 | 95 | Y | N |  | 0.36 |  |  | 100 | 325 | 360 | 0.206 | 0.412 | 0.618 | 1.03 | 1.545 | 2.06 | 86.91 | 92.14 | 93.78 | 94.94 | 95.3 | 95.37 | 94.55 | 87.84 | 92.87 | 94.26 | 95.56 | 95.79 | 95.73 | 95.09 | 88.1 | 93.05 | 94.37 | 95.71 | 96 | 95.94 | 95.28
Beyond Building Group | SR3000TLI [208V] | 3 kW, 208 Vac Utility Interactive Inverter | 3 | 208 | 95.5 | Y | N |  | 0.18 |  |  | 100 | 325 | 360 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 91.57 | 94.41 | 95.16 | 95.47 | 95.31 | 94.62 | 95.1 | 92.05 | 94.92 | 95.58 | 95.89 | 95.76 | 95.37 | 95.56 | 92.22 | 95.17 | 95.79 | 96.25 | 95.93 | 95.8 | 95.78
Beyond Building Group | SR3000TLI [240V] | 2 kW, 240 Vac Utility Interactive Inverter | 3.01 | 240 | 95.5 | Y | N |  | 0.25 |  |  | 100 | 325 | 360 | 0.301 | 0.602 | 0.903 | 1.505 | 2.258 | 3.01 | 90 | 93.9 | 94.85 | 95.4 | 95.31 | 94.83 | 94.97 | 90.64 | 94.34 | 95.34 | 95.79 | 95.87 | 95.6 | 95.49 | 91 | 94.59 | 95.44 | 95.97 | 96.01 | 95.77 | 95.65
Beyond Building Group | SR4000TLI [208V] | 4 kW, 208 Vac Utility Interactive Inverter | 3.98 | 208 | 95.5 | Y | N |  | 0.18 |  |  | 100 | 325 | 360 | 0.398 | 0.796 | 1.194 | 1.99 | 2.985 | 3.98 | 90.53 | 94.32 | 95.17 | 95.44 | 95.41 | 95.16 | 95.13 | 91.58 | 94.87 | 95.63 | 96.05 | 96 | 95.45 | 95.7 | 91.82 | 95.03 | 95.8 | 96.45 | 96.31 | 95.76 | 96.01
Beyond Building Group | SR4000TLI [240V] | 4 kW, 240 Vac Utility Interactive Inverter | 3.99 | 240 | 96 | Y | N |  | 0.25 |  |  | 100 | 325 | 360 | 0.399 | 0.798 | 1.197 | 1.995 | 2.993 | 3.99 | 90.55 | 94.3 | 95.24 | 95.69 | 95.74 | 95.56 | 95.38 | 91.53 | 94.95 | 95.81 | 96.33 | 96.33 | 96.05 | 95.99 | 91.95 | 95.23 | 95.96 | 96.4 | 96.48 | 96.25 | 96.15
Beyond Building Systems | SR2000TL-US-240 [240V] | 2110 W, 240 Vac Utility Interactive Inverter | 2.11 | 240 | 94.5 | Y | N |  | 0.25 |  |  | 100 | 375 | 400 | 0.21 | 0.42 | 0.63 | 1.06 | 1.58 | 2.11 | 85.3 | 91.6 | 92.9 | 94.3 | 94.6 | 94.5 | 93.8 | 82.1 | 91.9 | 94.2 | 95.6 | 96.1 | 96.4 | 95 | 82.2 | 91.5 | 93.8 | 95.6 | 96.1 | 96.3 | 95
Beyond Building Systems | SR3000TL-US-240 [240V] | 3180 W, 240 Vac Utility Interactive Inverter | 3.18 | 240 | 95 | Y | N |  | 0.25 |  |  | 100 | 375 | 400 | 0.32 | 0.64 | 0.95 | 1.59 | 2.39 | 3.18 | 88.8 | 92.9 | 94.1 | 94.6 | 94.3 | 94 | 94 | 88.8 | 94.4 | 95.3 | 96.2 | 96.3 | 95.9 | 95.7 | 89.5 | 93.7 | 95.3 | 96.2 | 96.3 | 96.1 | 95.7
Beyond Building Systems | SR4200TL-US-240 [240V] | 4100 W, 240 Vac Utility Interactive Inverter | 4.16 | 240 | 95.5 | Y | N |  | 0.2 |  |  | 100 | 380 | 400 | 0.42 | 0.83 | 1.25 | 2.08 | 3.12 | 4.16 | 90.6 | 93.8 | 94.5 | 94.8 | 94.6 | 94.2 | 94.4 | 91.4 | 95 | 95.7 | 96.1 | 96.2 | 95.9 | 95.9 | 90.7 | 94.7 | 95.5 | 96.1 | 96.1 | 95.9 | 95.7
Beyond Building Systems | SR5000TL-US-240 [240V] | 5000 W, 240 Vac Utility Interactive Inverter | 5.24 | 240 | 95.5 | Y | N |  | 0.2 |  |  | 100 | 380 | 400 | 0.52 | 1.05 | 1.57 | 2.62 | 3.93 | 5.24 | 91.8 | 94.1 | 94.6 | 94.7 | 94.3 | 93.5 | 94.3 | 92.5 | 95.1 | 96.1 | 96.2 | 95.9 | 95.6 | 95.8 | 92.3 | 95.3 | 95.8 | 96.1 | 95.9 | 95.5 | 95.8
Canadian Solar Inc. | CM-240-EC | 1-phase Microinverter | 0.24 |  | 96 | N | Y |  | 0.03 |  |  | 24 | 29 | 35 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 92.6 | 95 | 95.6 | 96.4 | 96.3 | 95.9 | 96 | 90.7 | 94.3 | 95.3 | 96.1 | 96.4 | 96.2 | 95.8 | 89.6 | 93.5 | 94.7 | 95.6 | 96.2 | 96.2 | 95.5 |  | 2017-10-03
Canadian Solar Inc. | CS6P-245M-EA | 1-phase Microinverter | 0.24 |  | 96 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.03 |  |  | 24 | 29 | 35 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 92.6 | 95 | 95.6 | 96.4 | 96.3 | 95.9 | 96 | 90.7 | 94.3 | 95.3 | 96.1 | 96.4 | 96.2 | 95.8 | 89.6 | 93.5 | 94.7 | 95.6 | 96.2 | 96.2 | 95.5 |  | 2017-10-03
Canadian Solar Inc. | CS6P-245P-EA | 1-phase Microinverter | 0.24 |  | 96 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.03 |  |  | 24 | 29 | 35 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 92.6 | 95 | 95.6 | 96.4 | 96.3 | 95.9 | 96 | 90.7 | 94.3 | 95.3 | 96.1 | 96.4 | 96.2 | 95.8 | 89.6 | 93.5 | 94.7 | 95.6 | 96.2 | 96.2 | 95.5 |  | 2017-10-03
Canadian Solar Inc. | CS6P-250M-EA | 1-phase Microinverter | 0.24 |  | 96 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.03 |  |  | 24 | 29 | 35 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 92.6 | 95 | 95.6 | 96.4 | 96.3 | 95.9 | 96 | 90.7 | 94.3 | 95.3 | 96.1 | 96.4 | 96.2 | 95.8 | 89.6 | 93.5 | 94.7 | 95.6 | 96.2 | 96.2 | 95.5 |  | 2017-10-03
Canadian Solar Inc. | CS6P-250P-EA | 1-phase Microinverter | 0.24 |  | 96 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.03 |  |  | 24 | 29 | 35 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 92.6 | 95 | 95.6 | 96.4 | 96.3 | 95.9 | 96 | 90.7 | 94.3 | 95.3 | 96.1 | 96.4 | 96.2 | 95.8 | 89.6 | 93.5 | 94.7 | 95.6 | 96.2 | 96.2 | 95.5 |  | 2017-10-03
Canadian Solar Inc. | CS6P-255M-EA | 1-phase Microinverter | 0.24 |  | 96 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.03 |  |  | 24 | 29 | 35 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 92.6 | 95 | 95.6 | 96.4 | 96.3 | 95.9 | 96 | 90.7 | 94.3 | 95.3 | 96.1 | 96.4 | 96.2 | 95.8 | 89.6 | 93.5 | 94.7 | 95.6 | 96.2 | 96.2 | 95.5 |  | 2017-10-03
Canadian Solar Inc. | CS6P-255P-EA | 1-phase Microinverter | 0.24 |  | 96 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.03 |  |  | 24 | 29 | 35 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 92.6 | 95 | 95.6 | 96.4 | 96.3 | 95.9 | 96 | 90.7 | 94.3 | 95.3 | 96.1 | 96.4 | 96.2 | 95.8 | 89.6 | 93.5 | 94.7 | 95.6 | 96.2 | 96.2 | 95.5 |  | 2017-10-03
Canadian Solar Inc. | CS6P-260M-EA | 1-phase Microinverter | 0.24 |  | 96 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.03 |  |  | 24 | 29 | 35 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 92.6 | 95 | 95.6 | 96.4 | 96.3 | 95.9 | 96 | 90.7 | 94.3 | 95.3 | 96.1 | 96.4 | 96.2 | 95.8 | 89.6 | 93.5 | 94.7 | 95.6 | 96.2 | 96.2 | 95.5 |  | 2017-10-03
Canadian Solar Inc. | CS6P-260P-EA | 240 W, 1-phase Microinverter | 0.24 |  | 96 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.03 |  |  | 24 | 29 | 35 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 92.6 | 95 | 95.6 | 96.4 | 96.3 | 95.9 | 96 | 90.7 | 94.3 | 95.3 | 96.1 | 96.4 | 96.2 | 95.8 | 89.6 | 93.5 | 94.7 | 95.6 | 96.2 | 96.2 | 95.5 |  | 2017-10-03
Canadian Solar Inc. | CM-260-EC | 1-phase Microinverter | 0.26 |  | 96 | N | Y |  | 0.03 |  |  | 24 | 29 | 35 | 0.03 | 0.05 | 0.08 | 0.13 | 0.2 | 0.26 | 93 | 95.2 | 95.6 | 96.4 | 96.2 | 95.7 | 96 | 91.2 | 94.6 | 95.3 | 96.2 | 96.3 | 96 | 95.9 | 90.2 | 93.6 | 94.8 | 95.7 | 96.2 | 96.1 | 95.5 |  | 2017-10-03
Canadian Solar Inc. | CM-280-EC | 1-phase Microinverter | 0.28 |  | 96 | N | Y |  | 0.03 |  |  | 24 | 29 | 35 | 0.03 | 0.06 | 0.08 | 0.14 | 0.21 | 0.28 | 93.3 | 95.3 | 95.6 | 96.4 | 96.1 | 95.5 | 95.9 | 91.4 | 94.7 | 95.4 | 96.4 | 96.3 | 95.9 | 95.9 | 90.5 | 93.9 | 94.8 | 95.8 | 96.1 | 96 | 95.6 |  | 2017-10-03
Canadian Solar Inc. | CM-300-EC | 1-phase Microinverter | 0.3 |  | 96 | N | Y |  | 0.03 |  |  | 24 | 29 | 35 | 0.03 | 0.06 | 0.09 | 0.15 | 0.23 | 0.3 | 93.6 | 95.4 | 95.7 | 96.4 | 95.9 | 95.3 | 95.9 | 91.9 | 94.8 | 95.4 | 96.4 | 96.2 | 95.8 | 95.9 | 91.1 | 94.1 | 95 | 96 | 96.1 | 96 | 95.7 |  | 2017-10-03
Canadian Solar Inc. | CSI-3000TL-CT [208V] | Utility Interactive Inverter | 2.86 | 208 | 96 | Y | N |  | 1 |  |  | 100 | 390 | 470 | 0.29 | 0.57 | 0.86 | 1.43 | 2.15 | 2.86 | 91.1 | 94.1 | 95.1 | 95.6 | 95.6 | 95 | 95.3 | 93.4 | 95.7 | 96.7 | 97.1 | 97 | 96.6 | 96.8 | 93 | 95.4 | 96.4 | 96.9 | 96.8 | 96.4 | 96.6 |  | 2017-10-03
Canadian Solar Inc. | CSI-3000TL-CT [240V] | Utility Interactive Inverter | 3 | 240 | 96.5 | Y | N |  | 1 |  |  | 100 | 390 | 470 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 91.5 | 94.5 | 95.5 | 96 | 96 | 95.6 | 95.7 | 94.1 | 96.2 | 97.1 | 97.5 | 97.4 | 97.1 | 97.2 | 93.8 | 95.8 | 96.8 | 97.3 | 97.3 | 97 | 97 |  | 2017-10-03
Canadian Solar Inc. | CSI-4000TL-CT [208V] | Utility Interactive Inverter | 3.81 | 208 | 96.5 | Y | N |  | 1 |  |  | 100 | 390 | 470 | 0.38 | 0.76 | 1.14 | 1.91 | 2.86 | 3.81 | 91.4 | 94.6 | 95.4 | 96 | 95.8 | 95.2 | 95.5 | 93.7 | 96.2 | 97 | 97.3 | 97.2 | 96.8 | 97 | 93.1 | 95.6 | 96.5 | 97.1 | 97 | 96.6 | 96.7 |  | 2017-10-03
Canadian Solar Inc. | CSI-4000TL-CT [240V] | Utility Interactive Inverter | 4.02 | 240 | 97 | Y | N |  | 1 |  |  | 100 | 390 | 470 | 0.4 | 0.8 | 1.21 | 2.01 | 3.02 | 4.02 | 92.1 | 94.9 | 95.8 | 96.3 | 96.2 | 95.8 | 95.9 | 94.2 | 96.6 | 97.2 | 97.7 | 97.6 | 97.4 | 97.4 | 93.4 | 95.9 | 96.8 | 97.4 | 97.5 | 97.1 | 97.1 |  | 2017-10-03
Canadian Solar Inc. | CSI-5000TL-CT [208V] | Utility Interactive Inverter | 4.61 | 208 | 96.5 | Y | N |  | 0.7 |  |  | 100 | 390 | 470 | 0.46 | 0.92 | 1.38 | 2.31 | 3.46 | 4.61 | 93 | 95.3 | 95.9 | 96.1 | 95.7 | 95 | 95.7 | 94.8 | 96.8 | 97.3 | 97.5 | 97.2 | 96.6 | 97.1 | 94.6 | 96.6 | 97.1 | 97.3 | 97.1 | 96.5 | 97 |  | 2017-10-03
Canadian Solar Inc. | CSI-5000TL-CT [240V] | Utility Interactive Inverter | 5 | 240 | 97 | Y | N |  | 1 |  |  | 100 | 390 | 470 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 93.6 | 95.7 | 96.1 | 96.5 | 96.1 | 95.4 | 96 | 95.4 | 97.1 | 97.6 | 97.8 | 97.6 | 97.1 | 97.5 | 95 | 96.9 | 97.4 | 97.6 | 97.4 | 97.1 | 97.3 |  | 2017-10-03
Canadian Solar Inc. | CSI-6000TL-CT [208V] | 5.5 kW, 208 Vac Utility Interactive Inverter | 5.5 | 208 | 96.5 | Y | N |  | 1 |  |  | 100 | 380 | 470 | 0.55 | 1.1 | 1.65 | 2.75 | 4.125 | 5.5 | 92.1 | 94.8 | 95.5 | 96.1 | 96 | 95.5 | 95.7 | 93.6 | 96.1 | 96.8 | 97.3 | 97.2 | 96.8 | 97 | 93 | 95.7 | 96.5 | 97 | 96.9 | 96.6 | 96.7 |  | 2017-10-03
Canadian Solar Inc. | CSI-6000TL-CT [240V] | 6.0 kW, 240 Vac Utility Interactive Inverter | 6 | 240 | 97 | Y | N |  | 1 |  |  | 100 | 380 | 470 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 92.6 | 95.3 | 95.9 | 96.5 | 96.4 | 95.9 | 96.1 | 94.3 | 96.6 | 97.3 | 97.7 | 97.6 | 97.3 | 97.4 | 93.7 | 96.1 | 96.9 | 97.4 | 97.4 | 97.2 | 97.1 |  | 2017-10-03
Canadian Solar Inc. | CSI-23KTL-CT [480V] | 23 kW, 480 Vac Utility Interactive Inverter | 23 | 480 | 98 | Y | N |  | 1 |  |  | 480 | 720 | 800 | 2.3 | 4.6 | 6.9 | 11.5 | 17.25 | 23 | 95.8 | 97 | 97.2 | 97.4 | 97.4 | 97.3 | 97.3 | 97 | 98.2 | 98.4 | 98.6 | 98.5 | 98.4 | 98.4 | 96.6 | 98 | 98.2 | 98.4 | 98.4 | 98.3 | 98.3 |  | 2017-10-03
Canadian Solar Inc. | CSI-28KTL-CT [480V] | 28 kW, 480 Vac Utility Interactive Inverter | 28 | 480 | 98 | Y | N |  | 0.9 |  |  | 500 | 725 | 800 | 2.8 | 5.6 | 8.4 | 14 | 21 | 28 | 96.3 | 97.2 | 97.4 | 97.5 | 97.4 | 97.2 | 97.3 | 97.5 | 98.3 | 98.5 | 98.5 | 98.4 | 98.2 | 98.4 | 97.2 | 98.1 | 98.4 | 98.4 | 98.3 | 98.1 | 98.3 |  | 2018-11-01
Canadian Solar Inc. | CSI-36KTL-CT | 36 kVA, 3-phase, transformerless Utility Interactive Inverter | 36 |  | 98 | Y | N | Multiple Listing of CHINT POWER SYSTEMS America CPS SCA36KTL-DO/US and Solectria Renewables,LLC PVI 36TL-479 | 0 |  |  | 540 | 730 | 800 | 3.6 | 7.2 | 10.8 | 18 | 27 | 36 | 95.5 | 96.8 | 97.2 | 97.5 | 97.5 | 97.3 | 97.3 | 97.4 | 98.3 | 98.5 | 98.5 | 98.5 | 98.3 | 98.4 | 97.1 | 98 | 98.3 | 98.4 | 98.3 | 98.2 | 98.3 |  | 2018-11-01
Canadian Solar Inc. | CSI-50KTL-CT [480V] | 50 kVA , 480 Vac, 3-phase Utility Interactive Inverter, non-isolated, 1000Vdc | 50 | 480 | 98.5 | N | N | Multiple Listing of CHINT POWER SYSTEMS America CPS SCA50KTL-DO/US and Solectria Renewables,LLC PVI 50TL-480 | 0.88 |  |  | 480 | 730 | 850 | 5 | 10 | 15 | 25 | 37.5 | 50 | 95.6089 | 96.843 | 97.4816 | 97.8549 | 97.8327 | 97.6904 | 97.6497 | 98.0184 | 98.6275 | 98.7749 | 98.8023 | 98.7196 | 98.6108 | 98.7055 | 97.7339 | 98.4586 | 98.6223 | 98.6594 | 98.5869 | 98.4698 | 98.56 | 2017-10-01 | 2018-11-01
Canadian Solar Inc. | CSI-60KTL-CT [480V] | 60 kVA , 480 Vac, 3-phase Utility Interactive Inverter, non-isolated, 1000Vdc | 60 | 480 | 98.5 | N | N | Multiple Listing of CHINT POWER SYSTEMS America CPS SCA60KTL-DO/US and Solectria Renewables,LLC PVI 60TL-480 | 0.88 |  |  | 540 | 730 | 850 | 6 | 12 | 18 | 30 | 45 | 60 | 96.5104 | 97.4761 | 97.8852 | 98.0525 | 97.9434 | 97.7271 | 97.8678 | 98.2227 | 98.7116 | 98.7911 | 98.779 | 98.6548 | 98.4981 | 98.6749 | 98.0008 | 98.5506 | 98.6633 | 98.6588 | 98.5228 | 98.3541 | 98.5403 | 2017-10-01 | 2018-11-01
Carlo Gavazzi | ISGA 1 22 [240V] | 2110 W, 240 Vac Utility Interactive Inverter | 2.11 | 240 | 94.5 | Y | N |  | 0.25 |  |  | 100 | 375 | 400 | 0.21 | 0.42 | 0.63 | 1.06 | 1.58 | 2.11 | 85.3 | 91.6 | 92.9 | 94.3 | 94.6 | 94.5 | 93.8 | 82.1 | 91.9 | 94.2 | 95.6 | 96.1 | 96.4 | 95 | 82.2 | 91.5 | 93.8 | 95.6 | 96.1 | 96.3 | 95
Carlo Gavazzi | ISGA 1 33 [240V] | 3180 W, 240 Vac Utility Interactive Inverter | 3.18 | 240 | 95 | Y | N |  | 0.25 |  |  | 100 | 375 | 400 | 0.32 | 0.64 | 0.95 | 1.59 | 2.39 | 3.18 | 88.8 | 92.9 | 94.1 | 94.6 | 94.3 | 94 | 94 | 88.8 | 94.4 | 95.3 | 96.2 | 96.3 | 95.9 | 95.7 | 89.5 | 93.7 | 95.3 | 96.2 | 96.3 | 96.1 | 95.7
Carlo Gavazzi | ISGA 1 42 [240V] | 4100 W, 240 Vac Utility Interactive Inverter | 4.16 | 240 | 95.5 | Y | N |  | 0.2 |  |  | 100 | 380 | 400 | 0.42 | 0.83 | 1.25 | 2.08 | 3.12 | 4.16 | 90.6 | 93.8 | 94.5 | 94.8 | 94.6 | 94.2 | 94.4 | 91.4 | 95 | 95.7 | 96.1 | 96.2 | 95.9 | 95.9 | 90.7 | 94.7 | 95.5 | 96.1 | 96.1 | 95.9 | 95.7
Carlo Gavazzi | ISGA 1 53 [240V] | 5000 W, 240 Vac Utility Interactive Inverter | 5.24 | 240 | 95.5 | Y | N |  | 0.2 |  |  | 100 | 380 | 400 | 0.52 | 1.05 | 1.57 | 2.62 | 3.93 | 5.24 | 91.8 | 94.1 | 94.6 | 94.7 | 94.3 | 93.5 | 94.3 | 92.5 | 95.1 | 96.1 | 96.2 | 95.9 | 95.6 | 95.8 | 92.3 | 95.3 | 95.8 | 96.1 | 95.9 | 95.5 | 95.8
CFM Equipment Distributors | Green Power 1100 [120V] | 1100 W, 120 Vac Utility Interactive Inverter | 1.1 | 120 | 90.5 | Y | N |  | 3.6 |  |  | 100 | 182 | 380 | 0.11 | 0.22 | 0.33 | 0.55 | 0.83 | 1.1 | 81.8 | 89 | 90.9 | 92.1 | 92.4 | 92.5 | 91.6 | 79.9 | 88 | 90.1 | 91.7 | 92.2 | 92.3 | 91.1 | 74.8 | 84.7 | 87.8 | 90 | 90.8 | 91.1 | 89.3
CFM Equipment Distributors | Green Power 2000 [240V] | 2000 W, 240 Vac Utility Interactive Inverter | 2 | 240 | 92 | Y | N |  | 3.6 |  |  | 100 | 199 | 380 | 0.2 | 0.4 | 0.6 | 1 | 1.5 | 2 | 87.3 | 91.7 | 92.6 | 93.5 | 93.2 | 93 | 92.9 | 85.7 | 90.8 | 92.1 | 92.9 | 92.9 | 92.6 | 92.4 | 82.4 | 88.8 | 90.5 | 91.6 | 91.8 | 91.6 | 91.1
CFM Equipment Distributors | Green Power 2500 [240V] | 2500 W, 240 Vac Utility Interactive Inverter | 2.5 | 240 | 94.5 | Y | N |  | 3.9 |  |  | 100 | 218 | 400 | 0.25 | 0.5 | 0.75 | 1.25 | 1.88 | 2.5 | 87.1 | 93.3 | 94.9 | 95.8 | 95.8 | 95.6 | 95.2 | 85.2 | 92.4 | 93.8 | 95.2 | 95.4 | 95.1 | 94.6 | 80.4 | 90 | 91.7 | 93.7 | 94.5 | 93.8 | 93.2
CFM Equipment Distributors | Green Power 3000 [240V] | 3000 W, 240 Vac Utility Interactive Inverter | 3 | 240 | 93.5 | Y | N |  | 3.63 |  |  | 100 | 222.5 | 380 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 88.9 | 92.9 | 93.8 | 94.3 | 94.2 | 93.9 | 93.9 | 87.9 | 92.5 | 93.5 | 94.1 | 94 | 93.8 | 93.7 | 84.9 | 90.9 | 92.4 | 93.3 | 93.2 | 93 | 92.7
CFM Equipment Distributors | Green Power 3500 [240V] | 3500 W, 240 Vac Utility Interactive Inverter | 3.5 | 240 | 95.5 | Y | N |  | 3.86 |  |  | 100 | 263 | 400 | 0.35 | 0.7 | 1.05 | 1.75 | 2.63 | 3.5 | 87.2 | 93.1 | 95.4 | 96.5 | 96.7 | 96.6 | 95.9 | 85.7 | 92.2 | 94.9 | 96.2 | 96.4 | 96.3 | 95.5 | 82.1 | 90.2 | 93.6 | 95.4 | 95.7 | 95.6 | 94.5
CFM Equipment Distributors | Green Power 4600 [208V] | 4600 W, 208 Vac Utility Interactive Inverter | 4.6 | 208 | 95.5 | Y | N |  | 4 |  |  | 100 | 254 | 400 | 0.46 | 0.92 | 1.38 | 2.3 | 3.45 | 4.6 | 90.3 | 94.8 | 95.9 | 96.5 | 96.5 | 96.2 | 96.1 | 89.2 | 94.3 | 95.6 | 96.3 | 96.4 | 96.1 | 95.9 | 86.5 | 92.9 | 94.7 | 95.6 | 95.7 | 95.4 | 95
CFM Equipment Distributors | Green Power 4800 [240V] | 4800 W, 240 Vac Utility Interactive Inverter | 4.8 | 240 | 96 | Y | N |  | 4.1 |  |  | 100 | 263 | 400 | 0.48 | 0.96 | 1.44 | 2.4 | 3.6 | 4.8 | 86.8 | 93.5 | 95.5 | 97 | 97.2 | 97.1 | 96.4 | 85.5 | 92.9 | 95 | 96.7 | 96.9 | 96.8 | 96 | 84.5 | 91.5 | 93.9 | 95.9 | 96.2 | 96.1 | 95.1
CFM Equipment Distributors | Green Power 5200 [240V] | 5200 W, 240 Vac Utility Interactive Inverter | 5.2 | 240 | 96 | Y | N |  | 4 |  |  | 100 | 280 | 400 | 0.52 | 1.04 | 1.56 | 2.6 | 3.9 | 5.2 | 89.4 | 94.8 | 96 | 96.8 | 97 | 96.8 | 96.4 | 88.6 | 94.4 | 95.7 | 96.7 | 96.8 | 96.6 | 96.2 | 87.7 | 93.1 | 94.8 | 96.1 | 96.3 | 96.1 | 95.5
Changzhou Nesl Solartech | DJ-230P-ST15 [240V] | 225 W, 240 Vac Inverter | 0.225 | 240 | 94.5 | N | Y | This component is specific to ACPV modules and is not available as an individual unit.
Changzhou Nesl Solartech | DJ-235P-ST15 [240V] | 225 W, 240 Vac Inverter | 0.225 | 240 | 94.5 | N | Y | This component is specific to ACPV modules and is not available as an individual unit.
Changzhou Nesl Solartech | DJ-240DA/C-ST15 [240V] | 225 W, 240 Vac Inverter | 0.225 | 240 | 94.5 | N | Y | This component is specific to ACPV modules and is not available as an individual unit.
Changzhou Nesl Solartech | DJ-240P-ST15 [240V] | 225 W, 240 Vac Inverter | 0.225 | 240 | 94.5 | N | Y | This component is specific to ACPV modules and is not available as an individual unit.
Changzhou Nesl Solartech | DJ-245DA/C-ST15 [240V] | 225 W, 240 Vac Inverter | 0.225 | 240 | 94.5 | N | Y | This component is specific to ACPV modules and is not available as an individual unit.
Changzhou Nesl Solartech | DJ-250DA/C-ST15 [240V] | 225 W, 240 Vac Inverter | 0.225 | 240 | 94.5 | N | Y | This component is specific to ACPV modules and is not available as an individual unit.
Changzhou Nesl Solartech | DJ-255D/C-ST15 [240V] | 225 W, 240 Vac Inverter | 0.225 | 240 | 94.5 | N |  | This component is specific to ACPV modules and is not available as an individual unit.
Chiconypower | MU300SAP2 [240V] | 300 W, 240 Vac Utility Interactive Inverter | 0.29 | 240 | 96 | N | Y |  | 0.1 |  |  | 26 | 31 | 43 | 0.03 | 0.06 | 0.09 | 0.14 | 0.22 | 0.29 | 92.1 | 94.4 | 95 | 95.7 | 96.3 | 95.9 | 95.7 | 91.6 | 95.1 | 94.8 | 96.5 | 96.5 | 96.5 | 96.1 | 89.9 | 94.3 | 95.3 | 96.3 | 96.2 | 96.2 | 95.8
Chilicon Power, LLC | CP-250-60-208/240-MC4 [208V] | 250 W, 208 Vac Utility Interactive Inverter | 0.22 | 208 | 96 | N | Y |  | 0.04 |  |  | 24 | 28 | 35 | 0.22 | 0.44 | 0.66 | 1.1 | 1.65 | 2.2 | 93 | 95.7 | 96.2 | 96.3 | 96 | 95.3 | 95.9 | 91.7 | 95.2 | 96.1 | 96.4 | 96.2 | 95.7 | 95.9 | 89 | 93.8 | 95.2 | 96.2 | 96.2 | 95.9 | 95.7 |  | 2019-02-01
Chilicon Power, LLC | CP-250-60-208/240-MC4 [240V] | 250 W, 240 Vac Utility Interactive Inverter | 0.22 | 240 | 96 | N | Y |  | 0.08 |  |  | 24 | 28 | 35 | 0.22 | 0.44 | 0.66 | 1.1 | 1.65 | 2.2 | 93.1 | 95.6 | 96.3 | 96.5 | 96.2 | 95.6 | 96.1 | 92 | 95.4 | 96.3 | 96.6 | 96.5 | 96.1 | 96.2 | 89.2 | 94 | 95.4 | 96.5 | 96.6 | 96.3 | 96 |  | 2019-02-01
Chilicon Power, LLC | CP-250E-60/72-208/240-MC4 [208V] | 277 W, 208 Vac Utility Interactive Inverter | 0.277 | 208 | 95.5 | N | Y |  | 0.02 |  |  | 28 | 30 | 32 | 0.03 | 0.06 | 0.08 | 0.14 | 0.21 | 0.28 | 92 | 95.1 | 95.9 | 96 | 95.6 | 94.9 | 95.5 | 91.2 | 94.8 | 95.7 | 96 | 95.6 | 95.1 | 95.5 | 90.6 | 94.5 | 95.6 | 96 | 95.7 | 95.2 | 95.4 | 2017-12-15 | 2019-02-01
Chilicon Power, LLC | CP-250E-60/72-208/240-MC4 [240V] | 289 W, 240 Vac Utility Interactive Inverter | 0.289 | 240 | 96 | N | Y |  | 0.06 |  |  | 28 | 30 | 32 | 0.03 | 0.06 | 0.09 | 0.14 | 0.22 | 0.29 | 92.3 | 95.4 | 96.1 | 96.2 | 95.9 | 95.2 | 95.8 | 91.6 | 95.2 | 96 | 96.3 | 96 | 95.4 | 95.8 | 91 | 95.1 | 95.9 | 96.3 | 96.1 | 95.6 | 95.8 | 2017-12-15 | 2019-02-01
Chint Power Systems America | CPS SCA3KTL-O/US [208V] | Utility Interactive Inverter | 2.86 | 208 | 96 | Y | N |  | 1 |  |  | 100 | 390 | 470 | 0.29 | 0.57 | 0.86 | 1.43 | 2.15 | 2.86 | 91.1 | 94.1 | 95.1 | 95.6 | 95.6 | 95 | 95.3 | 93.4 | 95.7 | 96.7 | 97.1 | 97 | 96.6 | 96.8 | 93 | 95.4 | 96.4 | 96.9 | 96.8 | 96.4 | 96.6
Chint Power Systems America | CPS SCA3KTL-O/US [240V] | Utility Interactive Inverter | 3 | 240 | 96.5 | Y | N |  | 1 |  |  | 100 | 390 | 470 | 0.3 | 0.6 | 0.9 | 1.5 | 2.3 | 3 | 91.5 | 94.5 | 95.5 | 96 | 96 | 95.6 | 95.7 | 94.1 | 96.2 | 97.1 | 97.5 | 97.4 | 97.1 | 97.2 | 93.8 | 95.8 | 96.8 | 97.3 | 97.3 | 97 | 97
Chint Power Systems America | CPS SCE4KTL-O US [208V] | 3.7 kW, 208 Vac Utility Interactive Inverter | 3.69 | 208 | 97 | Y | N |  | 0.21 |  |  | 100 | 360 | 470 | 0.37 | 0.74 | 1.11 | 1.85 | 2.77 | 3.69 | 94.7 | 96.6 | 97.3 | 97.7 | 97.6 | 97.4 | 97.4 | 94.1 | 96.4 | 97.2 | 97.6 | 97.5 | 97.4 | 97.3 | 92.5 | 95.5 | 96.6 | 97.2 | 97.2 | 97.2 | 96.9
Chint Power Systems America | CPS SCA4KTL-O/US [208V] | Utility Interactive Inverter | 3.81 | 208 | 96.5 | Y | N |  | 1 |  |  | 100 | 390 | 470 | 0.381 | 0.762 | 1.143 | 1.905 | 2.858 | 3.81 | 91.4 | 94.6 | 95.4 | 96 | 95.8 | 95.2 | 95.5 | 93.7 | 96.2 | 97 | 97.3 | 97.2 | 96.8 | 97 | 93.1 | 95.6 | 96.5 | 97.1 | 97 | 96.6 | 96.7
Chint Power Systems America | CPS SCE4KTL-O US [240V] | 4 kW, 240 Vac Utility Interactive Inverter | 3.98 | 240 | 97 | Y | N |  | 0.16 |  |  | 100 | 360 | 450 | 0.4 | 0.8 | 1.19 | 1.99 | 2.99 | 3.98 | 92 | 95.1 | 96.3 | 97 | 97 | 96.9 | 96.6 | 94.1 | 96.5 | 97.4 | 97.3 | 97.1 | 97.7 | 97.1 | 92.3 | 95.8 | 96.9 | 97.5 | 97.6 | 97.6 | 97.2
Chint Power Systems America | CPS SCE4KTL-O US [277V] | 4 kW, 277 Vac Utility Interactive Inverter | 3.98 | 277 | 97 | Y | N |  | 0.11 |  |  | 100 | 360 | 450 | 0.4 | 0.8 | 1.19 | 1.99 | 2.99 | 3.98 | 90.7 | 94.5 | 96 | 96.9 | 97 | 97 | 96.5 | 92.8 | 95.9 | 96.9 | 97.5 | 97.7 | 97.6 | 97.2 | 93 | 96 | 97.2 | 97.9 | 98 | 97.9 | 97.6
Chint Power Systems America | CPS SCA4KTL-O/US [240V] | Utility Interactive Inverter | 4.02 | 240 | 97 | Y | N |  | 1 |  |  | 100 | 390 | 470 | 0.402 | 0.804 | 1.206 | 2.01 | 3.015 | 4.02 | 92.1 | 94.9 | 95.8 | 96.3 | 96.2 | 95.8 | 95.9 | 94.2 | 96.6 | 97.2 | 97.7 | 97.6 | 97.4 | 97.4 | 93.4 | 95.9 | 96.8 | 97.4 | 97.5 | 97.1 | 97.1
Chint Power Systems America | CPS SCE5KTL-O US [208V] | 4.5 kW, 208 Vac Utility Interactive Inverter | 4.47 | 208 | 97 | Y | N |  | 0.07 |  |  | 100 | 360 | 470 | 0.45 | 0.89 | 1.34 | 2.24 | 3.35 | 4.47 | 94.5 | 96.9 | 97.5 | 97.7 | 97.6 | 97.4 | 97.4 | 94 | 96.6 | 97.2 | 97.5 | 97.5 | 97.3 | 97.2 | 92.6 | 95.4 | 96.3 | 97.1 | 97.2 | 97.1 | 96.8
Chint Power Systems America | CPS SCA5KTL-O US [208V] | 4.8 kW, 208 Vac Utility Interactive Inverter | 4.61 | 208 | 96.5 | Y | N |  | 0.7 |  |  | 100 | 390 | 470 | 0.46 | 0.92 | 1.38 | 2.31 | 3.46 | 4.61 | 93 | 95.3 | 95.9 | 96.1 | 95.7 | 95 | 95.7 | 94.8 | 96.8 | 97.3 | 97.5 | 97.2 | 96.6 | 97.1 | 94.6 | 96.6 | 97.1 | 97.3 | 97.1 | 96.5 | 97
Chint Power Systems America | CPS SCE5KTL-O US [240V] | 4.8 kW, 240 Vac Utility Interactive Inverter | 4.83 | 240 | 97 | Y | N |  | 0.12 |  |  | 100 | 360 | 450 | 0.48 | 0.97 | 1.45 | 2.42 | 3.62 | 4.83 | 92.8 | 95.8 | 96.6 | 96.9 | 96.9 | 96.8 | 96.6 | 94.7 | 96.8 | 97.2 | 97.7 | 97.5 | 97.6 | 97.4 | 93.2 | 96.3 | 97 | 97.5 | 97.5 | 97.5 | 97.2
Chint Power Systems America | CPS SCE5KTL-O US [277V] | 4.8 kW, 277 Vac Utility Interactive Inverter | 4.83 | 277 | 97 | Y | N |  | 0.09 |  |  | 100 | 360 | 450 | 0.48 | 0.97 | 1.45 | 2.42 | 3.62 | 4.83 | 91 | 94.4 | 95.7 | 96.6 | 96.9 | 96.9 | 96.3 | 93.3 | 96.3 | 97 | 97.5 | 97.6 | 97.6 | 97.3 | 94 | 96.7 | 97.3 | 97.8 | 97.9 | 97.9 | 97.6
Chint Power Systems America | CPS SCA5KTL-O US [240V] | Utility Interactive Inverter | 5 | 240 | 97 | Y | N |  | 1 |  |  | 100 | 390 | 470 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 93.6 | 95.7 | 96.1 | 96.5 | 96.1 | 95.4 | 96 | 95.4 | 97.1 | 97.6 | 97.8 | 97.6 | 97.1 | 97.5 | 95 | 96.9 | 97.4 | 97.6 | 97.4 | 97.1 | 97.3
Chint Power Systems America | CPS SCA6KTL-O US [208V] | 5.5 kW, 208 Vac Utility Interactive Inverter. For outdoor use. | 5.5 | 208 | 96.5 | Y | N |  | 1 |  |  | 100 | 380 | 470 | 0.55 | 1.1 | 1.65 | 2.75 | 4.125 | 5.5 | 92.1 | 94.8 | 95.5 | 96.1 | 96 | 95.5 | 95.7 | 93.6 | 96.1 | 96.8 | 97.3 | 97.2 | 96.8 | 97 | 93 | 95.7 | 96.5 | 97 | 96.9 | 96.6 | 96.7
Chint Power Systems America | CPS SCE6KTL-O US [208V] | 6 kW, 208 Vac Utility Interactive Inverter | 5.68 | 208 | 97 | Y | N |  | 0.11 |  |  | 100 | 360 | 470 | 0.6 | 1.2 | 1.79 | 2.99 | 4.49 | 5.98 | 95.9 | 97.2 | 97.5 | 97.5 | 97.3 | 97 | 97.3 | 94.9 | 96.9 | 97.4 | 97.4 | 97.3 | 97 | 97.2 | 93 | 96 | 96.6 | 97.1 | 97 | 96.8 | 96.7
Chint Power Systems America | CPS SCA6KTL-O US [240V] | 6.0 kW, 240 Vac Utility Interactive Inverter. For outdoor use. | 6 | 240 | 97 | Y | N |  | 1 |  |  | 100 | 380 | 470 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 92.6 | 95.3 | 95.9 | 96.5 | 96.4 | 95.9 | 96.1 | 94.3 | 96.6 | 97.3 | 97.7 | 97.6 | 97.3 | 97.4 | 93.7 | 96.1 | 96.9 | 97.4 | 97.4 | 97.2 | 97.1
Chint Power Systems America | CPS SCE6KTL-O US [240V] | 6 kW, 240 Vac Utility Interactive Inverter | 6 | 240 | 97 | Y | N |  | 0.07 |  |  | 100 | 360 | 450 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 91.5 | 94.7 | 95.9 | 96.6 | 96.8 | 96.8 | 96.3 | 93.3 | 96.2 | 96.9 | 97.4 | 97.4 | 97.4 | 97.1 | 94.3 | 96.7 | 97.3 | 97.9 | 97.8 | 97.7 | 97.6
Chint Power Systems America | CPS SCE6KTL-O US [277V] | 6 kW, 277 Vac Utility Interactive Inverter | 6.01 | 277 | 97 | Y | N |  | 0.08 |  |  | 100 | 360 | 450 | 0.6 | 1.2 | 1.8 | 3.01 | 4.51 | 6.01 | 93.8 | 96.1 | 96.4 | 96.8 | 96.8 | 96.6 | 96.6 | 95.5 | 97.1 | 97.7 | 97.7 | 97.7 | 97.4 | 97.5 | 93.9 | 96.2 | 97.1 | 97.4 | 97.4 | 97.2 | 97.2
Chint Power Systems America | CPS SCE7KTL-O US [240V] | 7 kW, 240 Vac Utility Interactive Inverter | 6.92 | 240 | 97 | Y | N |  | 0.17 |  |  | 100 | 360 | 450 | 0.69 | 1.38 | 2.08 | 3.46 | 5.19 | 6.92 | 94.3 | 96.2 | 96.7 | 96.8 | 96.7 | 96.4 | 96.6 | 95.5 | 97 | 97.5 | 97.6 | 97.5 | 97.3 | 97.4 | 94 | 96.2 | 96.9 | 97.3 | 97.3 | 97.2 | 97.1
Chint Power Systems America | CPS SCE7KTL-O US [208V] | 7 kW, 208 Vac Utility Interactive Inverter | 6.95 | 208 | 97 | Y | N |  | 0.09 |  |  | 100 | 360 | 470 | 0.7 | 1.39 | 2.09 | 3.48 | 5.21 | 6.95 | 96.1 | 97.3 | 97.5 | 97.3 | 97 | 96.5 | 97.1 | 95.6 | 97 | 97.4 | 97.1 | 96.9 | 96.6 | 97 | 93.8 | 96 | 96.6 | 96.9 | 96.7 | 96.4 | 96.6
Chint Power Systems America | CPS SCE7KTL-O US [277V] | 7 kW, 277 Vac Utility Interactive Inverter | 7.01 | 277 | 97 | Y | N |  | 0.02 |  |  | 100 | 360 | 450 | 0.7 | 1.4 | 2.1 | 3.51 | 5.26 | 7.01 | 93.4 | 95.9 | 96.5 | 96.8 | 96.6 | 96.4 | 96.5 | 94.8 | 96.6 | 97.2 | 97.5 | 97.1 | 97.1 | 97.1 | 94.9 | 96.9 | 97.4 | 97.7 | 97.6 | 97.4 | 97.5
Chint Power Systems America | CPS SC14KTL-DO/xx-208 [208V] | 14 kW, 208 Vac Utility Interactive Inverter with dual inputs (CA) | 14 | 208 | 96 | Y | N |  | 4 |  |  | 300 | 385 | 540 | 1.4 | 2.8 | 4.2 | 7 | 10.5 | 14 | 94.9 | 95.4 | 95.6 | 95.6 | 95.2 | 94.7 | 95.3 | 95.7 | 96.5 | 96.9 | 96.8 | 96.5 | 96.1 | 96.6 | 93.7 | 96.8 | 95.9 | 96.2 | 96 | 95.6 | 96
Chint Power Systems America | CPS SC20KTL-DO/xx-480 [480V] | 20 kW, 480 Vac Utility Interactive Inverter with dual inputs (CA) | 20 | 480 | 97 | Y | N |  | 2 |  |  | 300 | 480 | 550 | 2 | 4 | 6 | 10 | 15 | 20 | 94.9 | 96.2 | 96.4 | 96.6 | 96.2 | 95.7 | 96.2 | 95.2 | 96.7 | 97.1 | 97.2 | 97.1 | 96.9 | 97 | 95.3 | 96.8 | 97.2 | 97.4 | 97.3 | 97.2 | 97.2
Chint Power Systems America | CPS SCA23KTL-DO/US-480 [480V] | 23 kVA, 3-phase, transformerless Utility Interactive Inverter | 23 | 480 | 98 | Y | N |  | 1 |  |  | 480 | 720 | 800 | 2.3 | 4.6 | 6.9 | 11.5 | 17.25 | 23 | 95.8 | 97 | 97.2 | 97.4 | 97.4 | 97.3 | 97.3 | 97 | 98.2 | 98.4 | 98.6 | 98.5 | 98.4 | 98.4 | 96.6 | 98 | 98.2 | 98.4 | 98.4 | 98.3 | 98.3
Chint Power Systems America | CPS SCA28KTL-DO/US-480 [480V] | 28 kVA 3-phase, transformerless Utility Interactive Inverter | 28 | 480 | 98 | Y | N |  | 0.9 |  |  | 500 | 725 | 800 | 2.8 | 5.6 | 8.4 | 14 | 21 | 28 | 96.3 | 97.2 | 97.4 | 97.5 | 97.4 | 97.2 | 97.3 | 97.5 | 98.3 | 98.5 | 98.5 | 98.4 | 98.2 | 98.4 | 97.2 | 98.1 | 98.4 | 98.4 | 98.3 | 98.1 | 98.3
Chint Power Systems America | CPS SCA36KTL-DO/US [480V] | 36 kVA, 480 Vac, 1000 Vdc, 3-phase, non-isolated Utility Interactive Inverter | 36 | 480 | 98 | Y | N | Multiple Listings: Solectria Renewables, LLC PVI 36TL-480 and Canadian Solar Inc CSI-36KTL-CT | 0 |  |  | 540 | 730 | 800 | 3.6 | 7.2 | 10.8 | 18 | 27 | 36 | 95.5 | 96.8 | 97.2 | 97.5 | 97.5 | 97.3 | 97.3 | 97.4 | 98.3 | 98.5 | 98.5 | 98.5 | 98.3 | 98.4 | 97.1 | 98 | 98.3 | 98.4 | 98.3 | 98.2 | 98.3 | 2017-09-01 | 2018-10-15
Chint Power Systems America | CPS SCA50KTL-DO/US-480 [480V] | 50 kVA , 1000 Vdc, 480 Vac, 3-phase, non-isolated Utility Interactive Inverter | 50 | 480 | 98.5 | Y | N | Multiple Listings: Solectria Renewables, LLC PVI 50TL-480 and Canadian Solar Inc CSI-50KTL-CT | 0.88 |  |  | 480 | 730 | 850 | 5 | 10 | 15 | 25 | 37.5 | 50 | 95.6 | 96.8 | 97.5 | 97.9 | 97.8 | 97.7 | 97.6 | 98 | 98.6 | 98.8 | 98.8 | 98.7 | 98.6 | 98.7 | 97.7 | 98.5 | 98.6 | 98.7 | 98.6 | 98.5 | 98.6 | 2017-08-01 | 2018-10-15
Chint Power Systems America | CPS SCA60KTL-DO/US-480 [480V] | 60 kVA , 1000 Vdc, 480 Vac, 3-phase, non-isolated Utility Interactive Inverter | 60 | 480 | 98.5 | Y | N | Multiple Listings: Solectria Renewables, LLC PVI 60TL-480 and Canadian Solar Inc CSI-60KTL-CT | 0.88 |  |  | 540 | 730 | 850 | 6 | 12 | 18 | 30 | 45 | 60 | 96.5 | 97.5 | 97.9 | 98.1 | 97.9 | 97.7 | 97.9 | 98.2 | 98.7 | 98.8 | 98.8 | 98.7 | 98.5 | 98.7 | 98 | 98.6 | 98.7 | 98.7 | 98.5 | 98.4 | 98.5 | 2017-08-01 | 2018-10-15
Chint Power Systems America | CPS SC100KT-O/xx-480 [480V] | 100 kW, 480 Vac Utility Interactive Inverter with dual inputs (US) | 100 | 480 | 96 | Y | N |  | 34 |  |  | 330 | 430 | 500 | 10 | 20 | 30 | 50 | 75 | 100 | 94 | 96.2 | 96.6 | 96.8 | 96.6 | 96.2 | 96.5 | 92.7 | 95.7 | 96.1 | 96.5 | 96.3 | 95.9 | 96.1 | 92.2 | 95.2 | 95.8 | 96.3 | 96.1 | 95.7 | 95.9
Chint Power Systems America | CPS SCH100KTL-DO/US-600 [600V] | 100 kVA , 1500Vdc, 600Vac, 3 Phase, Non-isolated Utility Interactive Inverter | 100 | 600 | 98.5 | N | N |  | 4.5 |  |  | 870 | 1000 | 1300 | 10 | 20 | 30 | 50 | 75 | 100 | 98.5519 | 98.9972 | 99.062 | 99.0008 | 98.8738 | 98.7452 | 98.9099 | 97.9026 | 98.4849 | 98.5322 | 98.5674 | 98.447 | 98.2811 | 98.4543 | 97.098 | 97.901 | 98.071 | 98.1053 | 98.08 | 97.9054 | 98.0273 | 2018-08-01 | 2018-10-15
Chint Power Systems America | CPS SCH125KTL-DO/US-600 [600V] | 125 kVA , 1500Vdc, 600Vac, 3 Phase, Non-isolated Utility Interactive Inverter | 125 | 600 | 98.5 | N | N |  | 4.9 |  |  | 870 | 1000 | 1300 | 12.5 | 25 | 37.5 | 62.5 | 93.75 | 125 | 98.7077 | 99.0329 | 99.0691 | 98.9523 | 98.7899 | 98.5613 | 98.8549 | 98.1008 | 98.563 | 98.5841 | 98.5384 | 98.352 | 98.0513 | 98.4045 | 97.4171 | 98.0383 | 98.14 | 98.1411 | 97.9782 | 97.6992 | 97.9985 | 2018-08-01 | 2018-10-15
Chint Solar Zhejiang | CHPI3KTL-US [208V] | Utility Interactive Inverter | 2.86 | 208 | 96 | Y | N |  | 1 |  |  | 100 | 390 | 470 | 0.29 | 0.57 | 0.86 | 1.43 | 2.15 | 2.86 | 91.1 | 94.1 | 95.1 | 95.6 | 95.6 | 95 | 95.3 | 93.4 | 95.7 | 96.7 | 97.1 | 97 | 96.6 | 96.8 | 93 | 95.4 | 96.4 | 96.9 | 96.8 | 96.4 | 96.6
Chint Solar Zhejiang | CHPI3KTL-US [240V] | Utility Interactive Inverter | 3 | 240 | 96.5 | Y | N |  | 1 |  |  | 100 | 390 | 470 | 0.3 | 0.6 | 0.9 | 1.5 | 2.3 | 3 | 91.5 | 94.5 | 95.5 | 96 | 96 | 95.6 | 95.7 | 94.1 | 96.2 | 97.1 | 97.5 | 97.4 | 97.1 | 97.2 | 93.8 | 95.8 | 96.8 | 97.3 | 97.3 | 97 | 97
Chint Solar Zhejiang | CHPI4KTL-US [208V] | Utility Interactive Inverter | 3.81 | 208 | 96.5 | Y | N |  | 1 |  |  | 100 | 390 | 470 | 0.381 | 0.762 | 1.143 | 1.905 | 2.858 | 3.81 | 91.4 | 94.6 | 95.4 | 96 | 95.8 | 95.2 | 95.5 | 93.7 | 96.2 | 97 | 97.3 | 97.2 | 96.8 | 97 | 93.1 | 95.6 | 96.5 | 97.1 | 97 | 96.6 | 96.7
Chint Solar Zhejiang | CHPI4KTL-US [240V] | Utility Interactive Inverter | 4.02 | 240 | 97 | Y | N |  | 1 |  |  | 100 | 390 | 470 | 0.402 | 0.804 | 1.206 | 2.01 | 3.015 | 4.02 | 92.1 | 94.9 | 95.8 | 96.3 | 96.2 | 95.8 | 95.9 | 94.2 | 96.6 | 97.2 | 97.7 | 97.6 | 97.4 | 97.4 | 93.4 | 95.9 | 96.8 | 97.4 | 97.5 | 97.1 | 97.1
Chint Solar Zhejiang | CHPI5KTL-US [208V] | Utility Interactive Inverter | 4.61 | 208 | 96.5 | Y | N |  | 0.7 |  |  | 100 | 390 | 470 | 0.461 | 0.922 | 1.383 | 2.305 | 3.458 | 4.61 | 93 | 95.3 | 95.9 | 96.1 | 95.7 | 95 | 95.7 | 94.8 | 96.8 | 97.3 | 97.5 | 97.2 | 96.6 | 97.1 | 94.6 | 96.6 | 97.1 | 97.3 | 97.1 | 96.5 | 97
Chint Solar Zhejiang | CHPI5KTL-US [240V] | Utility Interactive Inverter | 5 | 240 | 97 | Y | N |  | 1 |  |  | 100 | 390 | 470 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 93.6 | 95.7 | 96.1 | 96.5 | 96.1 | 95.4 | 96 | 95.4 | 97.1 | 97.6 | 97.8 | 97.6 | 97.1 | 97.5 | 95 | 96.9 | 97.4 | 97.6 | 97.4 | 97.1 | 97.3
Chint Solar Zhejiang | CHPI 6KTL-US [208V] | 5.5 kW, 208 Vac Utility Interactive Inverter | 5.5 | 208 | 96.5 | Y | N |  | 1 |  |  | 100 | 380 | 470 | 0.55 | 1.1 | 1.65 | 2.75 | 4.125 | 5.5 | 92.1 | 94.8 | 95.5 | 96.1 | 96 | 95.5 | 95.7 | 93.6 | 96.1 | 96.8 | 97.3 | 97.2 | 96.8 | 97 | 93 | 95.7 | 96.5 | 97 | 96.9 | 96.6 | 96.7
Chint Solar Zhejiang | CHPI 6KTL-US [240V] | 6.0 kW, 240 Vac Utility Interactive Inverter | 6 | 240 | 97 | Y | N |  | 1 |  |  | 100 | 380 | 470 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 92.6 | 95.3 | 95.9 | 96.5 | 96.4 | 95.9 | 96.1 | 94.3 | 96.6 | 97.3 | 97.7 | 97.6 | 97.3 | 97.4 | 93.7 | 96.1 | 96.9 | 97.4 | 97.4 | 97.2 | 97.1
Chint Solar Zhejiang | CHPI14KTL-US | Utility Interactive Inverter | 14 |  | 96 | Y | N |  | 4 |  |  | 300 | 385 | 540 | 1.4 | 2.8 | 4.2 | 7 | 10.5 | 14 | 94.9 | 95.4 | 95.6 | 95.6 | 95.2 | 94.7 | 95.3 | 95.7 | 96.5 | 96.9 | 96.8 | 96.5 | 96.1 | 96.6 | 93.7 | 96.8 | 95.9 | 96.2 | 96 | 95.6 | 96
Chint Solar Zhejiang | CHPI20KTL-US | Utility Interactive Inverter | 20 |  | 97 | Y | N |  | 2 |  |  | 300 | 480 | 550 | 2 | 4 | 6 | 10 | 15 | 20 | 94.9 | 96.2 | 96.4 | 96.6 | 96.2 | 95.7 | 96.2 | 95.2 | 96.7 | 97.1 | 97.2 | 97.1 | 96.9 | 97 | 95.3 | 96.8 | 97.2 | 97.4 | 97.3 | 97.2 | 97.2
Chint Solar Zhejiang | CHPI 23KTL-US | 23 kVA, 3-phase, transformerless Utility Interactive Inverter | 23 |  | 98 | Y | N |  | 1 |  |  | 480 | 720 | 800 | 2.3 | 4.6 | 6.9 | 11.5 | 17.25 | 23 | 95.8 | 97 | 97.2 | 97.4 | 97.4 | 97.3 | 97.3 | 97 | 98.2 | 98.4 | 98.6 | 98.5 | 98.4 | 98.4 | 96.6 | 98 | 98.2 | 98.4 | 98.4 | 98.3 | 98.3
Chint Solar Zhejiang | CHPI 28KTL-US | 28 kVA, 3-phase, transformerless Utility Interactive Inverter | 28 |  | 98 | Y | N |  | 0.9 |  |  | 500 | 725 | 800 | 2.8 | 5.6 | 8.4 | 14 | 21 | 28 | 96.3 | 97.2 | 97.4 | 97.5 | 97.4 | 97.2 | 97.3 | 97.5 | 98.3 | 98.5 | 98.5 | 98.4 | 98.2 | 98.4 | 97.2 | 98.1 | 98.4 | 98.4 | 98.3 | 98.1 | 98.3
Concept by US | Power Station PS247-05-180 [120V] | 5 kW, 120 Vac Utility Interactive Inverter | 5.02 | 120 | 94 | Y | N |  | 0 |  |  | 210 | 310 | 420 | 0.502 | 1.004 | 1.506 | 2.51 | 3.765 | 5.02 | 96.5419 | 94.6876 | 93.4665 | 92.9563 | 93.3258 | 92.4851 | 93.4198 | 96.0637 | 96.782 | 96.7023 | 93.7118 | 94.6159 | 92.3483 | 94.7292 | 95.1281 | 93.4382 | 95.5797 | 94.4897 | 94.2959 | 92.9827 | 94.4154
Concept by US | Power Station PS247-10-180 [120V] | 10 kW, 120 Vac Utility Interactive Inverter | 10.08 | 120 | 94 | Y | N |  | 0 |  |  | 210 | 310 | 420 | 1.01 | 2.02 | 3.02 | 5.04 | 7.56 | 10.08 | 96.9 | 94.3 | 93.9 | 93.1 | 92.3 | 91.4 | 92.9 | 97.2 | 96.1 | 95.4 | 93.8 | 94.9 | 92.6 | 94.8 | 96.4 | 94 | 93.9 | 95.2 | 93.7 | 93 | 94.1
Concept by US | Power Station PS247-15-180 [120V] | 15 kW, 120 Vac Utility Interactive Inverter | 15.16 | 120 | 94 | Y | N |  | 0 |  |  | 210 | 310 | 420 | 1.52 | 3.03 | 4.55 | 7.58 | 11.37 | 15.16 | 95.4 | 94.3 | 94.4 | 93.2 | 92.4 | 92.1 | 93 | 96.9 | 96 | 95.8 | 94.2 | 94.8 | 93 | 94.8 | 96.4 | 95.4 | 94 | 94.7 | 93.9 | 93.7 | 94.2
Connect Renewable Energy | CE 4000 [240V] | 3000 W Grid Tied, 240 Vac, Low DC Voltage Inverter | 3 | 240 | 93 | Y | N |  | 7 | 3 | 7 | 54 | 62 | 77 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 85.3 | 92.8 | 93.8 | 94.4 | 94.3 | 93.4 | 93.8 | 85.6 | 91.7 | 93.1 | 94.4 | 93.6 | 92.6 | 93.3 | 82.8 | 89.3 | 91.1 | 93.8 | 93.3 | 93.2 | 92.5
Danfoss | MLX 480V [480V] | 60 kW, 480 Vac, Utility Interactive Inverter | 60 | 480 | 98.5 | N | N |  | 8.16 |  |  | 685 | 710 | 800 | 6 | 12 | 18 | 30 | 45 | 60 | 97.7 | 98.5 | 98.7 | 98.8 | 98.6 | 98.5 | 98.6 | 97.5 | 98.4 | 98.7 | 98.7 | 98.6 | 98.4 | 98.6 | 96.9 | 98.1 | 98.4 | 98.4 | 98.3 | 98.1 | 98.3
Danfoss Solar | DLX 2.0 UL [208V] | 2.0 kW, 208 Vac Utility Interactive Inverter | 2.01 | 208 | 96.5 | Y | N |  | 0.9 |  |  | 100 | 365 | 490 | 0.2 | 0.4 | 0.6 | 1 | 1.51 | 2.01 | 91.7 | 95.1 | 95.6 | 96.5 | 96.6 | 96.3 | 96.2 | 92.9 | 95.4 | 96.2 | 96.8 | 96.9 | 96.7 | 96.6 | 91 | 94 | 95.3 | 96.3 | 96.6 | 96.6 | 96
Danfoss Solar | DLX 2.0 UL [240V] | 2.0 kW, 240 Vac Utility Interactive Inverter | 2.01 | 240 | 96.5 | Y | N |  | 0.97 |  |  | 100 | 375 | 490 | 0.2 | 0.4 | 0.6 | 1.01 | 1.51 | 2.01 | 91.9 | 95.3 | 96.1 | 96.7 | 96.8 | 96.7 | 96.4 | 91.2 | 95.2 | 96.1 | 96.9 | 97.1 | 97.1 | 96.6 | 91 | 94.5 | 95.6 | 96.6 | 97 | 97.1 | 96.4
Danfoss Solar | DLX 2.9 UL [240V] | 2.9 kW, 240 Vac Utility Interactive Inverter | 2.9 | 240 | 96.5 | Y | N |  | 0.98 |  |  | 100 | 375 | 490 | 0.29 | 0.58 | 0.87 | 1.45 | 2.18 | 2.9 | 93.4 | 95.9 | 96.5 | 96.8 | 96.5 | 96.1 | 96.4 | 93.3 | 96.1 | 96.8 | 97.2 | 97.1 | 97 | 96.9 | 92.2 | 95.5 | 96.3 | 96.9 | 97 | 96.9 | 96.6
Danfoss Solar | DLX 2.9 UL [208V] | 2.9 kW, 208 Vac Utility Interactive Inverter | 2.91 | 208 | 96.5 | Y | N |  | 0.92 |  |  | 100 | 365 | 490 | 0.29 | 0.58 | 0.87 | 1.45 | 2.18 | 2.91 | 93.7 | 95.9 | 96.2 | 96.5 | 96.3 | 95.6 | 96.2 | 93.9 | 96.1 | 96.6 | 96.8 | 96.6 | 96.3 | 96.5 | 91.9 | 95.1 | 96 | 96.5 | 96.5 | 96.3 | 96.2
Danfoss Solar | DLX 3.8 UL [208V] | 3.8 kW, 208 Vac Utility Interactive Inverter | 3.81 | 208 | 96.5 | Y | N |  | 0.77 |  |  | 100 | 360 | 500 | 0.38 | 0.76 | 1.14 | 1.91 | 2.86 | 3.81 | 94.6 | 96.3 | 96.7 | 96.7 | 96.2 | 95.6 | 96.3 | 94.8 | 96.5 | 96.9 | 97 | 96.8 | 96.5 | 96.7 | 93.1 | 95.6 | 96.4 | 96.8 | 96.7 | 96.5 | 96.5
Danfoss Solar | DLX 3.8 UL [240V] | 3.8 kW, 240 Vac Utility Interactive Inverter | 3.81 | 240 | 97 | Y | N |  | 0.9 |  |  | 100 | 370 | 500 | 0.38 | 0.76 | 1.14 | 1.91 | 2.86 | 3.81 | 94.8 | 96.6 | 96.9 | 96.9 | 96.5 | 96 | 96.6 | 94.6 | 96.6 | 97.1 | 97.3 | 97.2 | 96.8 | 97 | 93.3 | 95.8 | 96.6 | 97 | 97.1 | 96.9 | 96.8
Danfoss Solar | DLX 4.4 UL [208V] | 4.4 kW, 208 Vac Utility Interactive Inverter | 4.4 | 208 | 96.5 | Y | N |  | 0.8 |  |  | 100 | 360 | 500 | 0.44 | 0.88 | 1.32 | 2.2 | 3.3 | 4.4 | 95.1 | 96.5 | 96.7 | 96.4 | 95.9 | 95.1 | 96 | 95.2 | 96.6 | 97 | 97 | 96.7 | 96.3 | 96.7 | 93.6 | 95.9 | 96.4 | 96.7 | 96.5 | 96.2 | 96.4
Danfoss Solar | DLX 4.4 UL [240V] | 4.4 kW, 240 Vac Utility Interactive Inverter | 4.4 | 240 | 97 | Y | N |  | 0.97 |  |  | 100 | 370 | 500 | 0.44 | 0.88 | 1.32 | 2.2 | 3.3 | 4.4 | 95.3 | 96.8 | 96.9 | 96.8 | 96.4 | 95.6 | 96.5 | 95.2 | 96.8 | 97.2 | 97.2 | 97.1 | 96.7 | 97 | 93.9 | 96.2 | 96.7 | 97 | 97 | 96.7 | 96.8
Danfoss Solar | MLX 400V [400V] | 60 kW, 400 Vac, Utility Interactive Inverter | 59.86 | 400 | 98 | N | N |  | 7.1 |  |  | 570 | 630 | 800 | 5.99 | 11.97 | 17.96 | 29.93 | 44.89 | 59.86 | 97.9 | 98.6 | 98.7 | 98.6 | 98.4 | 98.1 | 98.4 | 97.5 | 98.3 | 98.4 | 98.3 | 98.1 | 97.9 | 98.2 | 96.5 | 97.7 | 98 | 98 | 97.7 | 97.5 | 97.8
Darfon Electronics Corp. | MIG240UL00 [240V] | 220 W, 240V Utility Interactive Inverter | 0.23 | 240 | 95 | N | N |  | 0.047 |  |  | 27 | 35 | 40 | 0.02 | 0.05 | 0.07 | 0.11 | 0.17 | 0.23 | 88.9 | 93.3 | 94.6 | 94.9 | 95.2 | 95.1 | 94.7 | 89 | 93 | 94.6 | 95.3 | 95.5 | 95.6 | 95 | 88.2 | 92.7 | 94.3 | 95.3 | 95.5 | 95.7 | 94.9
Darfon Electronics Corp. | MIG300UL00 [240V] | Utility Interactive Inverter | 0.25 | 240 | 95 | N | N |  | 0.089 |  |  | 30 | 36 | 40 | 0.025 | 0.051 | 0.076 | 0.127 | 0.19 | 0.254 | 90.3 | 93.7 | 95 | 95.3 | 95.5 | 95.4 | 95.1 | 89.9 | 93.5 | 94.9 | 95.2 | 95.7 | 95.7 | 95.1 | 89.8 | 93.3 | 94.7 | 95.2 | 95.7 | 95.8 | 95.1
Darfon Electronics Corp. | G32xxxxxx [208V] | 300 W, 208 Vac Utility Interactive Inverter, where x = 0-9, A-Z, or (blank) | 0.303 | 208 | 95.5 | N | Y |  | 0.014 |  |  | 24 | 27.5 | 37 | 0.03 | 0.06 | 0.09 | 0.15 | 0.23 | 0.3 | 92.3 | 95.5 | 96 | 96.1 | 95.6 | 94.7 | 95.6 | 91.9 | 95.3 | 95.9 | 96 | 95.5 | 94.7 | 95.5 | 90.6 | 94.7 | 95.4 | 95.6 | 95.3 | 94.5 | 95.1 | 2017-03
Darfon Electronics Corp. | G32xxxxxx [240V] | 300 W, 240 Vac Utility Interactive Inverter, where x = 0-9, A-Z, or (blank) | 0.305 | 240 | 96.3 | N | Y |  | 0.065 |  |  | 24 | 27.5 | 37 | 0.03 | 0.06 | 0.09 | 0.15 | 0.23 | 0.31 | 91.9819 | 95.7436 | 96.4819 | 96.7075 | 96.4925 | 95.9914 | 96.2935 | 91.5101 | 95.3888 | 96.2557 | 96.5292 | 96.3443 | 95.8729 | 96.1078 | 89.9942 | 94.7422 | 95.7649 | 96.1578 | 96.0436 | 95.6311 | 95.7065
Darfon Electronics Corp. | G32xxxxxx [277V] | 300 W, 277 Vac Utility Interactive Inverter, where x = 0-9, A-Z ,or (Blank) | 0.305 | 277 | 96 | N | Y |  | 0.065 |  |  | 24 | 27.5 | 37 | 0.03 | 0.06 | 0.09 | 0.15 | 0.23 | 0.31 | 92 | 95.7 | 96.5 | 96.7 | 96.5 | 96 | 96.3 | 91.5101 | 95.3888 | 96.2557 | 96.5292 | 96.3443 | 95.8729 | 96.1078 | 89.9942 | 94.7422 | 95.7649 | 96.1578 | 96.0436 | 95.6311 | 95.7065
Darfon Electronics Corp. | G64xxxxxx [240V] | 600 W, 240 Vac Utility Interactive Microinverter, where x =0-9, A-Z or blank, for marking use only | 0.60098 | 240 | 95.5 | N | Y |  | 0.057 |  |  | 26 | 30 | 35 | 0.060098 | 0.1202 | 0.18029 | 0.30049 | 0.45074 | 0.60098 | 90.4144 | 94.8593 | 95.7396 | 96.0257 | 95.8002 | 95.1867 | 95.5471 | 89.9759 | 94.6419 | 95.597 | 95.9482 | 95.5545 | 95.2089 | 95.3562 | 89.1799 | 94.3065 | 95.3164 | 95.764 | 95.6469 | 95.127 | 95.2801 | 2019-01-02
Darfon Electronics Corp. | H5000x [240V] | 5000 W, 240 Vac Utility Interactive Inverter, where x = 0-9, A-Z or blank, (0-9 for color; A-Z for customer) | 5.074 | 240 | 95.5 | N | N |  | 0.43 |  |  | 300 | 360 | 380 | 0.508 | 1.016 | 1.524 | 2.54 | 3.81 | 5.076 | 89.2283 | 93.7363 | 94.9074 | 95.7518 | 95.8863 | 95.613 | 95.3531 | 89.4891 | 93.9486 | 95.2566 | 95.9139 | 96.0338 | 95.8858 | 95.5419 | 89.3177 | 94.0048 | 95.2025 | 95.9477 | 96.0161 | 95.9196 | 95.5308 | 2018-03-15 | 2018-10-15
DASS tech | DSP-M33250KUS | Utility Interactive Inverter | 250 |  | 95 | Y | N |  | 107.7 |  |  | 330 | 378 | 480 | 25 | 50 | 75 | 125 | 187.5 | 250 | 91.5 | 94.7 | 95.5 | 95.2 | 95.1 | 94.5 | 95 | 91.5 | 94.5 | 95.2 | 95.1 | 94.9 | 94.6 | 94.8 | 91.1 | 94.2 | 94.9 | 95 | 94.8 | 94.5 | 94.7
Delta Electronics | DDP-260AB XX | Utility Interactive, transformer isolated PV Microinverter | 0.26 |  | 95 | N | Y |  | 0.2 |  |  | 27.5 | 33.8 | 36 | 0.03 | 0.05 | 0.08 | 0.13 | 0.2 | 0.26 | 91.1 | 93.7 | 95 | 95.3 | 94.8 | 93.6 | 94.6 | 90.6 | 94.3 | 94.5 | 95.4 | 95.6 | 95 | 95.1 | 90.6 | 93.8 | 94.5 | 95.6 | 95.5 | 94.9 | 95.1
Delta Electronics | SOLIVIA 3.8 NA G4 TL [208V] | 3800W, 208Vac transformerless Utility Interactive Inverter. All the SOLIVIA models are same firmare version tested for Utility Interactive type. | 3.32 | 208 | 97.5 | Y | N |  | 1.14 |  |  | 100 | 380 | 500 | 0.33 | 0.66 | 1 | 1.66 | 2.49 | 3.32 | 94.6 | 96.1 | 97 | 97.3 | 97.1 | 96.8 | 97 | 96.3 | 96.9 | 97.8 | 97.9 | 98.1 | 97.5 | 97.8 | 95.9 | 95.8 | 96.9 | 97.4 | 97.4 | 97.1 | 97.2 | 2017-10-16 | 2018-10-15
Delta Electronics | SOLIVIA 3.8 NA G4 TL [240V] | 3800 W, 240 Vac transformerless Utility Interactive Inverter. All the SOLIVIA models are same firmare version tested for Utility Interactive type. | 3.81 | 240 | 97.5 | Y | N |  | 1.19 |  |  | 100 | 380 | 500 | 0.38 | 0.76 | 1.14 | 1.91 | 2.86 | 3.81 | 94.1 | 95.9 | 96.9 | 97.3 | 97.2 | 96.8 | 97 | 95.5 | 96.9 | 98 | 98.3 | 98.1 | 98 | 98 | 94.6 | 95.6 | 97.3 | 97.8 | 97.8 | 97.6 | 97.5 | 2017-10-16 | 2018-10-15
Delta Electronics | SOLIVIA 5.2 NA G4 TL [208V] | 5200W, 208Vac transformerless Utility Interactive Inverter. All the SOLIVIA models are same firmare version tested for Utility Interactive type. | 5.2 | 208 | 97.5 | Y | N |  | 1.31 |  |  | 100 | 380 | 500 | 0.52 | 1.04 | 1.56 | 2.6 | 3.9 | 5.2 | 93.6 | 95.6 | 96.3 | 97.2 | 97.1 | 96.8 | 96.8 | 95.2 | 96.6 | 97.5 | 98 | 98 | 97.7 | 97.7 | 93.6 | 96.3 | 97 | 97.7 | 97.7 | 97.5 | 97.4 | 2017-10-16 | 2018-10-15
Delta Electronics | SOLIVIA 5.2 NA G4 TL [240V] | 5200 W, 240Vac transformerless Utility Interactive Inverter. All the SOLIVIA models are same firmare version tested for Utility Interactive type. | 5.2 | 240 | 97.5 | Y | N |  | 1.42 |  |  | 100 | 380 | 500 | 0.52 | 1.04 | 1.56 | 2.6 | 3.9 | 5.2 | 94 | 95.8 | 96.4 | 97.3 | 97.4 | 97.1 | 97 | 95.2 | 97 | 97.5 | 98.2 | 98.3 | 98.1 | 98 | 93.8 | 96.6 | 97.2 | 97.9 | 98 | 98 | 97.7 | 2017-10-16 | 2018-10-15
Delta Electronics | RPI H7U [208V] | 6 kW, 208 Vac transformerless Utility Interactive Inverter with arc detector | 5.99 | 208 | 97 | Y | N |  | 1.087 |  |  | 280 | 370 | 400 | 0.6 | 1.2 | 1.8 | 3 | 4.49 | 5.99 | 96.1 | 96.8 | 97 | 97 | 96.7 | 96.3 | 96.8 | 95.8 | 97.4 | 97.6 | 97.5 | 97.3 | 96.9 | 97.3 | 95.7 | 97.3 | 97.5 | 97.5 | 97.3 | 96.9 | 97.3
Delta Electronics | RPI H7U [240V] [6kVa] | 6 kW, 240 Vac transformerless Utility Interactive Inverter with arc detector | 6.06 | 240 | 97.5 | Y | N |  | 1.181 |  |  | 280 | 370 | 400 | 0.61 | 1.21 | 1.82 | 3.03 | 4.55 | 6.06 | 96 | 96.1 | 96.6 | 96.7 | 96.7 | 96.4 | 96.6 | 96 | 97.7 | 97.9 | 97.9 | 97.7 | 97.5 | 97.7 | 95.8 | 97.6 | 97.8 | 97.9 | 97.7 | 97.5 | 97.6
Delta Electronics | SOLIVIA 6.6 NA G4 TL [208V] | 6600W, 208Vac transformerless Utility Interactive Inverter. All the SOLIVIA models are same firmare version tested for Utility Interactive type. | 6.6 | 208 | 97.5 | Y | N |  | 1.23 |  |  | 100 | 380 | 500 | 0.66 | 1.32 | 1.98 | 3.3 | 4.95 | 6.6 | 94.4 | 96.1 | 97 | 97.2 | 96.9 | 96.2 | 96.8 | 95.9 | 96.9 | 97.8 | 98 | 97.7 | 97.3 | 97.7 | 95 | 96.4 | 97.4 | 97.7 | 97.6 | 97.1 | 97.4 | 2017-10-16 | 2018-10-15
Delta Electronics | SOLIVIA 6.6 NA G4 TL [240V] | 6600W, 208Vac transformerless Utility Interactive Inverter. All the SOLIVIA models are same firmare version tested for Utility Interactive type. | 6.6 | 240 | 97.5 | Y | N |  | 1.45 |  |  | 100 | 380 | 500 | 0.66 | 1.32 | 1.98 | 3.3 | 4.95 | 6.6 | 94.3 | 96.2 | 96.9 | 97.4 | 97.2 | 96.8 | 97 | 96 | 97.3 | 97.9 | 98.3 | 98.2 | 97.9 | 98 | 95 | 96.8 | 97.6 | 98 | 98 | 97.7 | 97.7 | 2017-10-16 | 2018-10-15
Delta Electronics | SOLIVIA 7.6 NA G4 TL [208V] | 7600W, 208Vac transformerless Utility Interactive Inverter. All the SOLIVIA models are same firmare version tested for Utility Interactive type. | 6.6 | 208 | 97.5 | Y | N |  | 1.23 |  |  | 100 | 380 | 500 | 0.66 | 1.32 | 1.98 | 3.3 | 4.95 | 6.6 | 94.4 | 96.1 | 97 | 97.2 | 96.9 | 96.2 | 96.8 | 95.9 | 96.9 | 97.8 | 98 | 97.7 | 97.3 | 97.7 | 95 | 96.4 | 97.4 | 97.7 | 97.6 | 97.1 | 97.4 | 2017-10-16 | 2018-10-15
Delta Electronics | RPI H7U [240V] [7kVa] | 7 kW, 240 Vac transformerless Utility Interactive Inverter with arc detector | 7.014 | 240 | 97.5 | Y | N |  | 1.169 |  |  | 280 | 370 | 400 | 0.7 | 1.4 | 2.1 | 3.51 | 5.26 | 7.01 | 96.3 | 96.3 | 96.7 | 96.8 | 96.6 | 96.2 | 96.6 | 96.9 | 97.8 | 97.9 | 97.9 | 97.6 | 97.3 | 97.7 | 96.7 | 97.7 | 97.9 | 97.9 | 97.6 | 97.4 | 97.7
Delta Electronics | SOLIVIA 7.6 NA G4 TL [240V] | 7600W,240Vac transformerless Utility Interactive Inverter. All the SOLIVIA models are same firmare version tested for Utility Interactive type. | 7.6 | 240 | 97.5 | Y | N |  | 1.43 |  |  | 100 | 380 | 500 | 0.76 | 1.52 | 2.28 | 3.8 | 5.7 | 7.6 | 95 | 96.4 | 97.3 | 97.4 | 97 | 96.4 | 97 | 96.3 | 97.4 | 98.1 | 98.3 | 98 | 97.7 | 98 | 95.5 | 97.2 | 97.7 | 98 | 97.9 | 97.5 | 97.7 | 2017-10-16 | 2018-10-15
Delta Electronics | Delta 15 TL | 15 kW, 3-phase, transformerless Utility Interactive Inverter | 15.13 |  | 98 | Y | N |  | 0.82 |  |  | 420 | 700 | 800 | 1.51 | 3.03 | 4.54 | 7.56 | 11.34 | 15.13 | 94.7 | 96.5 | 97 | 97.4 | 97.5 | 97.4 | 97.2 | 95.6 | 97.2 | 97.7 | 98.1 | 98.2 | 98.1 | 97.9 | 96.2 | 97.6 | 98.1 | 98.4 | 98.4 | 98.4 | 98.3
Delta Electronics | Delta 20 TL | 20 kW, 3-phase, transformerless Utility Interactive Inverter | 20.2 |  | 98 | Y | N |  | 0.82 |  |  | 500 | 720 | 800 | 2.02 | 4.04 | 6.06 | 10.1 | 15.15 | 20.2 | 95.5 | 96.8 | 97.3 | 97.6 | 97.7 | 97.6 | 97.5 | 97.3 | 98.2 | 98.5 | 98.6 | 98.6 | 98.5 | 98.5 | 96.9 | 97.9 | 98.3 | 98.4 | 98.4 | 98.4 | 98.3
Delta Electronics | M24U_XXX [480V] | 26.4 kW, 480 Vac Utility Interactive Inverter, where xxx = 120, 121, or 122 | 26.403 | 480 | 98 | N | N |  | 2.6 |  |  | 415 | 710 | 830 | 2.64 | 5.28 | 7.92 | 13.2 | 19.8 | 26.4 | 95.28 | 96.42 | 97.03 | 97.41 | 97.46 | 97.3 | 97.25 | 97.39 | 98.27 | 98.56 | 98.65 | 98.65 | 98.57 | 98.57 | 96.51 | 97.77 | 98.06 | 98.35 | 98.36 | 98.27 | 98.21 | 2017-12-15 | 2018-10-15
Delta Electronics | M28U_XXX [480V] | 30.7 kW, 480 Vac Utility Interactive Inverter, where xxx = 120, 121, or 122 | 30.709 | 480 | 98 | N | N |  | 2.4 |  |  | 485 | 710 | 830 | 3.07 | 6.14 | 9.21 | 15.35 | 23.03 | 30.71 | 95.98 | 97.06 | 97.64 | 97.78 | 97.74 | 97.52 | 97.62 | 97.67 | 98.38 | 98.6 | 98.65 | 98.6 | 98.49 | 98.56 | 96.9 | 97.95 | 98.21 | 98.35 | 98.32 | 98.18 | 98.23 | 2017-12-15 | 2018-10-15
Delta Electronics | M36U_XXX [480V] | 39.7 kW, 480 Vac Utility Interactive Inverter, where xxx = 120, 121, or 122 | 39.737 | 480 | 98 | N | N |  | 2.9 |  |  | 520 | 710 | 830 | 3.97 | 7.95 | 11.92 | 19.87 | 29.8 | 39.74 | 96.36 | 97.47 | 97.83 | 97.97 | 97.81 | 97.59 | 97.76 | 97.75 | 98.45 | 98.6 | 98.6 | 98.43 | 98.28 | 98.45 | 96.89 | 97.92 | 98.22 | 98.3 | 98.16 | 97.95 | 98.12 | 2017-12-15 | 2018-10-15
Delta Electronics | M42U_XXX [480V] | 45.9 kW, 480 Vac Utility Interactive Inverter, where xxx = 120, 121, or 122 | 45.972 | 480 | 98 | N | N |  | 2.9 |  |  | 545 | 710 | 830 | 4.6 | 9.19 | 13.79 | 22.99 | 34.48 | 45.97 | 96.83 | 97.76 | 97.97 | 98.02 | 97.8 | 97.54 | 97.81 | 97.98 | 98.53 | 98.6 | 98.55 | 98.35 | 98.16 | 98.41 | 97.21 | 98.04 | 98.26 | 98.26 | 98.07 | 97.86 | 98.09 | 2017-12-15 | 2018-10-15
Delta Electronics | M60U_XXX [480V] | 65.47 kW, 480 Vac Utility Interactive Inverter, where xxx = 120, 121, or 122 | 65.47 | 480 | 98.5 | N | N |  | 2.863 |  |  | 540 | 710 | 800 | 6.55 | 13.09 | 19.64 | 32.74 | 49.1 | 65.47 | 96.77 | 97.69 | 97.62 | 98.1 | 98.02 | 97.46 | 97.89 | 98.52 | 98.59 | 98.63 | 98.71 | 98.46 | 98.29 | 98.54 | 97.76 | 98.59 | 98.41 | 98.51 | 98.32 | 98.14 | 98.35 | 2017-12-15 | 2018-10-15
Delta Electronics | M80U_XXX [480V] | 82.76 kW, 480 Vac Utility Interactive Inverter, where xxx = 120, 121, or 122 | 82.764 | 480 | 98.5 | N | N |  | 2.6 |  |  | 600 | 710 | 800 | 8.28 | 16.55 | 24.83 | 41.38 | 62.07 | 82.76 | 97.48 | 98.39 | 98.4 | 98.22 | 97.97 | 97.79 | 98.06 | 98.31 | 98.79 | 98.85 | 98.69 | 98.54 | 98.18 | 98.59 | 98.37 | 98.68 | 98.69 | 98.49 | 98.23 | 98.09 | 98.36 | 2017-12-15 | 2018-10-15
Delta Energy Systems | SI 1800 US [208V] | 1800 W, 208 Vac Grid-Tied Solar PV Inverter | 1.8 | 208 | 92.5 | Y | N |  | 0.26 |  |  | 100 | 290 | 320 | 0.18 | 0.36 | 0.54 | 0.9 | 1.35 | 1.8 | 83.5 | 90 | 91.6 | 92.5 | 92.8 | 92.4 | 92 | 84 | 91.4 | 91.6 | 93.1 | 93.4 | 93.5 | 92.6 | 84.8 | 90.4 | 92.1 | 93.4 | 93.6 | 93.5 | 92.8
Delta Energy Systems | SI 1800 US [240V] | 1800 W, 240 Vac Grid-Tied Solar PV Inverter | 1.8 | 240 | 92.5 | Y | N |  | 0.14 |  |  | 100 | 290 | 320 | 0.18 | 0.36 | 0.54 | 0.9 | 1.35 | 1.8 | 83.6 | 89.6 | 91.2 | 92.3 | 92.6 | 92.3 | 91.8 | 84.1 | 90.1 | 91.8 | 93.2 | 93.4 | 93.2 | 92.6 | 85 | 90.1 | 92.2 | 93.3 | 93.5 | 93.3 | 92.8
Delta Energy Systems | SI 2500 US [208V] | 2500 W, 208 Vac Grid-Tied Solar PV Inverter | 2.5 | 208 | 92 | Y | N |  | 0.32 |  |  | 100 | 290 | 320 | 0.25 | 0.5 | 0.75 | 1.25 | 1.88 | 2.5 | 85.3 | 90.2 | 91.6 | 92.1 | 91.8 | 90.8 | 91.4 | 86.7 | 90.7 | 92.3 | 92.7 | 92.6 | 92.1 | 92.2 | 86.6 | 91 | 92.4 | 93 | 92.5 | 92 | 92.3
Delta Energy Systems | SI 2500 US [240V] | 2500 W, 240 Vac Grid-Tied Solar PV Inverter | 2.5 | 240 | 93 | Y | N |  | 0.32 |  |  | 100 | 290 | 320 | 0.25 | 0.5 | 0.75 | 1.25 | 1.88 | 2.5 | 86.5 | 91.2 | 92.7 | 93.1 | 92.6 | 91.7 | 92.4 | 86.8 | 91.7 | 93.1 | 93.7 | 93.6 | 92.9 | 93.2 | 87.6 | 92.1 | 93.3 | 93.8 | 93.6 | 93 | 93.3
Delta Energy Systems | SOLIVIA 2.5 NA G4 TR [240V] | 2500 W, 240 Vac Grid-Tied Solar PV Inverter | 2.53 | 240 | 95 | Y | N |  | 0.44 |  |  | 100 | 350 | 500 | 0.2525 | 0.505 | 0.7575 | 1.263 | 1.894 | 2.525 | 87.88 | 92.81 | 94.3 | 95.16 | 95.39 | 95.43 | 94.78 | 88.06 | 92.94 | 94.4 | 95.57 | 95.81 | 96.07 | 95.15 | 87.32 | 93.18 | 94.41 | 95.57 | 96.11 | 96.19 | 95.3
Delta Energy Systems | SOLIVIA 2.5 NA G4 TR [208V] | 2500 W, 208 Vac Grid-Tied Solar PV Inverter | 2.55 | 208 | 94.5 | Y | N |  | 0.33 |  |  | 100 | 350 | 500 | 0.2554 | 0.5108 | 0.7662 | 1.277 | 1.916 | 2.554 | 87.8 | 92.51 | 93.67 | 94.83 | 95.11 | 95.18 | 94.46 | 87.84 | 92.59 | 93.98 | 95.14 | 95.44 | 95.71 | 94.77 | 87.07 | 92.88 | 94.1 | 95.22 | 95.67 | 95.82 | 94.91
Delta Energy Systems | SOLIVIA 3.3 NA G4 TR [208V] | 3300 W, 208 Vac Grid-Tied Solar PV Inverter | 3.33 | 208 | 95 | Y | N |  | 0.33 |  |  | 100 | 350 | 500 | 0.3325 | 0.665 | 0.9975 | 1.663 | 2.494 | 3.325 | 89.6 | 93.39 | 94.38 | 95.06 | 95.1 | 94.9 | 94.69 | 89.95 | 93.65 | 94.73 | 95.42 | 95.74 | 95.36 | 95.19 | 89.44 | 93.75 | 94.91 | 95.65 | 95.82 | 95.59 | 95.3
Delta Energy Systems | SOLIVIA 3.3 NA G4 TR [240V] | 3300 W, 240 Vac Grid-Tied Solar PV Inverter | 3.34 | 240 | 95.5 | Y | N |  | 0.44 |  |  | 100 | 350 | 500 | 0.3335 | 0.667 | 1.001 | 1.668 | 2.501 | 3.335 | 89.99 | 93.76 | 94.76 | 95.34 | 95.57 | 95.28 | 95.09 | 89.85 | 94.05 | 95 | 95.8 | 96.07 | 95.85 | 95.52 | 89.59 | 94.12 | 95.09 | 95.98 | 96.15 | 96 | 95.62
Delta Energy Systems | SOLIVIA 4.4 NA G4 TR [208V] | 4400 W, 208 Vac Grid-Tied Solar PV Inverter | 4.528 | 208 | 95 | Y | N |  | 0.39 |  |  | 100 | 350 | 500 | 0.45 | 0.91 | 1.36 | 2.26 | 3.4 | 4.53 | 89.29 | 93.12 | 93.99 | 94.56 | 94.41 | 94.04 | 94.1 | 89.82 | 93.26 | 94.33 | 95.08 | 94.86 | 94.47 | 94.54 | 89.76 | 94.05 | 95 | 95.49 | 95.38 | 94.87 | 95.04
Delta Energy Systems | SOLIVIA 4.4 NA G4 TR [240V] | 4400 W, 240 Vac Grid-Tied Solar PV Inverter | 4.564 | 240 | 95 | Y | N |  | 0.49 |  |  | 100 | 350 | 500 | 0.46 | 0.91 | 1.37 | 2.28 | 3.42 | 4.56 | 90 | 93.32 | 94.39 | 94.88 | 94.89 | 94.61 | 94.54 | 89.54 | 93.68 | 94.86 | 95.49 | 95.33 | 95.01 | 94.98 | 89.56 | 93.58 | 95.11 | 95.82 | 95.84 | 95.44 | 95.37
Delta Energy Systems | SOLIVIA 5.0 NA G4 TR [208V] | 5000 W, 208 Vac Grid-Tied Solar PV Inverter | 5.084 | 208 | 95 | Y | N |  | 0.39 |  |  | 100 | 350 | 500 | 0.51 | 1.02 | 1.53 | 2.54 | 3.81 | 5.08 | 90.37 | 93.22 | 94.25 | 94.49 | 94.27 | 93.72 | 94.08 | 90.53 | 93.49 | 94.69 | 94.97 | 94.66 | 93.96 | 94.47 | 90.64 | 93.95 | 94.83 | 95.49 | 95.16 | 94.56 | 94.92
Delta Energy Systems | SOLIVIA 5.0 NA G4 TR [240V] | 5000 W, 240 Vac Grid-Tied Solar PV Inverter | 5.14 | 240 | 95 | Y | N |  | 0.51 |  |  | 100 | 350 | 500 | 0.51 | 1.03 | 1.54 | 2.57 | 3.86 | 5.14 | 90.13 | 93.58 | 94.64 | 94.84 | 94.8 | 94.46 | 94.53 | 90.59 | 93.73 | 94.91 | 95.4 | 95.15 | 94.87 | 94.9 | 91.18 | 94.19 | 95.12 | 95.68 | 95.61 | 95.13 | 95.29
Destin Power Inc. | SAVEEN1000-ES02H.US [440V] | 1000 kW, 440 Vac, Utility Interactive Inverter ESS for Indoor ESS PCS | 1000 | 440 | 98 | N | N | Weighted Efficiency includes efficiency of 3000 kVA ABB Korea distribution transformer. | 149.25 |  |  | 740 | 830 | 900 | 100 | 200 | 300 | 500 | 750 | 1000 | 94.9762 | 97.2102 | 97.9516 | 98.4084 | 98.507 | 98.421 | 98.2093 | 94.252 | 96.7644 | 97.5816 | 98.1856 | 98.3254 | 98.2608 | 97.9626 | 93.5872 | 96.4774 | 97.3838 | 98.0058 | 98.2088 | 98.1694 | 97.7938 | 2018-11-01
Diehl AKO Stiftung | 4301 S-A [208V] | 3.68 kW, 208 Vac Utility Interactive Inverter | 3.19 | 208 | 94 | Y | N |  | 2.05 | 3.19 | 2.05 | 100 | 273 | 440 | 0.319 | 0.638 | 0.957 | 1.595 | 2.393 | 3.19 | 92.1 | 94.8 | 95.03 | 94.95 | 94.36 | 93.53 | 94.46 | 91.6 | 94.52 | 94.83 | 94.81 | 94.27 | 93.52 | 94.32 | 89.49 | 93.56 | 94.25 | 94.31 | 93.85 | 93.26 | 93.78
Diehl AKO Stiftung | 4301 S-A [240V] | 3.68 kW, 240 Vac Utility Interactive Inverter | 3.68 | 240 | 94.5 | Y | N |  | 2.22 | 3.68 | 2.22 | 100 | 298 | 440 | 0.368 | 0.736 | 1.104 | 1.84 | 2.76 | 3.68 | 91.69 | 94.79 | 95.17 | 95.3 | 94.92 | 94.17 | 94.86 | 91.29 | 94.51 | 94.98 | 95.1 | 94.98 | 94.13 | 94.79 | 89.47 | 93.58 | 94.4 | 94.69 | 94.42 | 93.91 | 94.21
Diehl AKO Stiftung | Platinum 100 CS-A [208V] | 100 kW, 208 Vac 3-phase Utility Interactive Inverter | 100 | 208 | 94.5 | Y | N |  | 1 |  |  | 300 | 350 | 480 | 10 | 20 | 30 | 50 | 75 | 100 | 90.82 | 94.01 | 94.82 | 95.34 | 95.08 | 93.88 | 94.82 | 90.27 | 93.75 | 94.58 | 95.15 | 95.04 | 93.75 | 94.69 | 89.04 | 92.9 | 93.9 | 94.75 | 94.31 | 93.33 | 94.02
Diehl AKO Stiftung | Platinum 100 CS-A [480V] | 100 kW, 480 Vac 3-phase Utility Interactive Inverter | 100 | 480 | 94.5 | Y | N |  | 3 |  |  | 300 | 350 | 480 | 10 | 20 | 30 | 50 | 75 | 100 | 90.85 | 94.14 | 94.86 | 95.17 | 95.09 | 93.98 | 94.81 | 90.33 | 93.83 | 94.68 | 95.05 | 94.99 | 93.86 | 94.66 | 88.99 | 92.99 | 93.99 | 94.61 | 94.41 | 93.54 | 94.07
Diehl AKO Stiftung | Platinum 100 CS-A HE [208V] | 100 kW, 208 Vac 3-phase Utility Interactive Inverter | 100 | 208 | 95 | Y | N |  | 1 | 100 | 1 | 300 | 350 | 480 | 10 | 20 | 30 | 50 | 75 | 100 | 91.53 | 94.8 | 95.45 | 95.79 | 95.69 | 94.57 | 95.41 | 91.06 | 94.55 | 95.25 | 95.65 | 95.55 | 94.67 | 95.26 | 89.83 | 93.76 | 94.6 | 95.2 | 95.16 | 94.4 | 94.78
Diehl AKO Stiftung | Platinum 100 CS-A HE [480V] | 100 kW, 480 Vac 3-phase Utility Interactive Inverter | 100 | 480 | 95.5 | Y | N |  | 2 | 100 | 2 | 300 | 350 | 480 | 10 | 20 | 30 | 50 | 75 | 100 | 91.91 | 95.03 | 95.69 | 95.95 | 95.84 | 94.83 | 95.6 | 91.44 | 94.7 | 95.5 | 95.81 | 95.71 | 94.7 | 95.43 | 90.22 | 94 | 94.91 | 95.38 | 95.33 | 94.33 | 94.97
Direct Grid Technologies | DGM-460 [208V] | 415W, 208 Vac Utility Interactive Inverter | 0.415 | 208 | 92 | N | N |  | 0.27 |  |  | 55 | 60 | 65 | 0.0415 | 0.083 | 0.1245 | 0.2075 | 0.3113 | 0.415 | 82.9 | 89.6 | 91.4 | 92.9 | 93.3 | 93.1 | 92.4 | 82.5 | 89.3 | 91 | 92.6 | 93.1 | 93.1 | 92.2 | 82.3 | 88.8 | 90.7 | 92.3 | 92.9 | 92.9 | 91.9
Direct Grid Technologies | DGM-S460 [240V] | 479W, 240 Vac Utility Interactive Inverter | 0.479 | 240 | 92.5 | N | N |  | 0.38 |  |  | 55 | 60 | 65 | 0.0479 | 0.0958 | 0.1437 | 0.2395 | 0.3593 | 0.479 | 84.3 | 91.1 | 92.4 | 93.4 | 93.7 | 93.5 | 93 | 83.9 | 90.8 | 92.1 | 93.1 | 93.5 | 93.5 | 92.7 | 83.6 | 90.7 | 91.8 | 92.9 | 93.3 | 93.3 | 92.5
Dow Chemical | 362589 (3.5 kW 2-string) [240V] | Powerhouse 240 Vac, 2-string, 3.5 kW Utility Interactive Inverter | 3.504 | 240 | 94.5 | N | N |  | 1.39 |  |  | 100 | 300 | 420 | 0.35 | 0.7 | 1.05 | 1.75 | 2.63 | 3.5 | 86.8 | 91.5 | 93.5 | 94.1 | 95 | 94.7 | 94.1 | 87.2 | 92.3 | 93.9 | 95.1 | 95.4 | 95.3 | 94.7 | 86.1 | 90.6 | 94 | 95.3 | 95.6 | 95.6 | 94.7
Dow Chemical | 362590 (3.5 kW 3-string) [240V] | Powerhouse 240 Vac, 3-string, 3.5 kW Utility Interactive Inverter | 3.53 | 240 | 94 | N | N |  | 1.42 |  |  | 100 | 300 | 420 | 0.35 | 0.71 | 1.06 | 1.77 | 2.65 | 3.53 | 85.6 | 90.8 | 92.7 | 94.1 | 94.2 | 94 | 93.5 | 86.3 | 91.6 | 93.3 | 94.7 | 95.1 | 95.1 | 94.3 | 87 | 91.9 | 93.6 | 95 | 95.6 | 95.7 | 94.7
Dow Chemical | 362591 (3.5 kW 4-string) [240V] | Powerhouse 240 Vac, 4-string, 3.5 kW Utility Interactive Inverter | 3.54 | 240 | 94 | N | N |  | 1.14 |  |  | 100 | 300 | 420 | 0.35 | 0.71 | 1.06 | 1.77 | 2.65 | 3.54 | 84.1 | 90.3 | 92.2 | 93.8 | 94.2 | 94.1 | 93.3 | 86.9 | 91.7 | 93.2 | 94.5 | 95 | 95 | 94.2 | 86.6 | 91.5 | 93.3 | 94.8 | 95.2 | 95.3 | 94.4
Dow Chemical | 362592 (5.0 kW 2-string) [240V] | Powerhouse 240 Vac, 2-string, 5.0 kW Utility Interactive Inverter | 4.95 | 240 | 95 | N | N |  | 1.26 |  |  | 100 | 360 | 475 | 0.5 | 0.99 | 1.49 | 2.48 | 3.72 | 4.95 | 89.17 | 93.99 | 94.92 | 95.31 | 94.86 | 94.24 | 94.7 | 90.43 | 94.42 | 95.25 | 95.69 | 95.46 | 94.24 | 95.2 | 89.11 | 93.51 | 94.69 | 95.31 | 95.15 | 94.67 | 94.8
Eaton | PV238 [208V] | 3.7 kW, 208 Vac Utility Interactive Inverter | 3.69 | 208 | 97 | Y | N |  | 0.21 |  |  | 100 | 360 | 470 | 0.37 | 0.74 | 1.11 | 1.85 | 2.77 | 3.69 | 94.7 | 96.6 | 97.3 | 97.7 | 97.6 | 97.4 | 97.4 | 94.1 | 96.4 | 97.2 | 97.6 | 97.5 | 97.4 | 97.3 | 92.5 | 95.5 | 96.6 | 97.2 | 97.2 | 97.2 | 96.9
Eaton | PV240 [208V] | 3.7 kW, 208 Vac Utility Interactive Inverter | 3.69 | 208 | 97 | Y | N |  | 0.21 |  |  | 100 | 360 | 470 | 0.37 | 0.74 | 1.11 | 1.85 | 2.77 | 3.69 | 94.7 | 96.6 | 97.3 | 97.7 | 97.6 | 97.4 | 97.4 | 94.1 | 96.4 | 97.2 | 97.6 | 97.5 | 97.4 | 97.3 | 92.5 | 95.5 | 96.6 | 97.2 | 97.2 | 97.2 | 96.9
Eaton | PV238 [240V] | 3.7 kW, 240 Vac Utility Interactive Inverter | 3.71 | 240 | 97 | Y | N |  | 0.06 |  |  | 100 | 360 | 450 | 0.37 | 0.74 | 1.11 | 1.86 | 2.78 | 3.71 | 92 | 95.1 | 96.3 | 97 | 97 | 96.9 | 96.6 | 94.1 | 96.5 | 97.4 | 97.3 | 97.1 | 97.7 | 97.1 | 92.3 | 95.8 | 96.9 | 97.5 | 97.6 | 97.6 | 97.2
Eaton | PV238 [277V] | 3.7 kW, 277 Vac Utility Interactive Inverter | 3.71 | 277 | 97 | Y | N |  | 0.14 |  |  | 100 | 360 | 450 | 0.37 | 0.74 | 1.11 | 1.86 | 2.78 | 3.71 | 90.8 | 94.6 | 95.9 | 96.8 | 97 | 97 | 96.5 | 92.9 | 95.9 | 96.8 | 97.6 | 97.6 | 97.6 | 97.2 | 93.4 | 96.3 | 97.2 | 97.8 | 97.9 | 97.9 | 97.5
Eaton | PV240 [240V] | 4 kW, 240 Vac Utility Interactive Inverter | 3.98 | 240 | 97 | Y | N |  | 0.16 |  |  | 100 | 360 | 450 | 0.4 | 0.8 | 1.19 | 1.99 | 2.99 | 3.98 | 92 | 95.1 | 96.3 | 97 | 97 | 96.9 | 96.6 | 94.1 | 96.5 | 97.4 | 97.3 | 97.1 | 97.7 | 97.1 | 92.3 | 95.8 | 96.9 | 97.5 | 97.6 | 97.6 | 97.2
Eaton | PV240 [277V] | 4 kW, 277 Vac Utility Interactive Inverter | 3.98 | 277 | 97 | Y | N |  | 0.11 |  |  | 100 | 360 | 450 | 0.4 | 0.8 | 1.19 | 1.99 | 2.99 | 3.98 | 90.7 | 94.5 | 96 | 96.9 | 97 | 97 | 96.5 | 92.8 | 95.9 | 96.9 | 97.5 | 97.7 | 97.6 | 97.2 | 93 | 96 | 97.2 | 97.9 | 98 | 97.9 | 97.6
Eaton | PV250 [208V] | 4.5 kW, 208 Vac Utility Interactive Inverter | 4.47 | 208 | 97 | Y | N |  | 0.07 |  |  | 100 | 360 | 470 | 0.45 | 0.89 | 1.34 | 2.24 | 3.35 | 4.47 | 94.5 | 96.9 | 97.5 | 97.7 | 97.6 | 97.4 | 97.4 | 94 | 96.6 | 97.2 | 97.5 | 97.5 | 97.3 | 97.2 | 92.6 | 95.4 | 96.3 | 97.1 | 97.2 | 97.1 | 96.8
Eaton | PV250 [240V] | 4.8 kW, 240 Vac Utility Interactive Inverter | 4.83 | 240 | 97 | Y | N |  | 0.12 |  |  | 100 | 360 | 450 | 0.48 | 0.97 | 1.45 | 2.42 | 3.62 | 4.83 | 92.8 | 95.8 | 96.6 | 96.9 | 96.9 | 96.8 | 96.6 | 94.7 | 96.8 | 97.2 | 97.7 | 97.5 | 97.6 | 97.4 | 93.2 | 96.3 | 97 | 97.5 | 97.5 | 97.5 | 97.2
Eaton | PV250 [277V] | 4.8 kW, 277 Vac Utility Interactive Inverter | 4.83 | 277 | 97 | Y | N |  | 0.09 |  |  | 100 | 360 | 450 | 0.48 | 0.97 | 1.45 | 2.42 | 3.62 | 4.83 | 91 | 94.4 | 95.7 | 96.6 | 96.9 | 96.9 | 96.3 | 93.3 | 96.3 | 97 | 97.5 | 97.6 | 97.6 | 97.3 | 94 | 96.7 | 97.3 | 97.8 | 97.9 | 97.9 | 97.6
Eaton | PV260 [208V] | 6 kW, 208 Vac Utility Interactive Inverter | 5.98 | 208 | 97 | Y | N |  | 0.11 |  |  | 100 | 360 | 470 | 0.6 | 1.2 | 1.79 | 2.99 | 4.49 | 5.98 | 95.9 | 97.2 | 97.5 | 97.5 | 97.3 | 97 | 97.3 | 94.9 | 96.9 | 97.4 | 97.4 | 97.3 | 97 | 97.2 | 93 | 96 | 96.6 | 97.1 | 97 | 96.8 | 96.7
Eaton | PV260 [277V] | 6 kW, 277 Vac Utility Interactive Inverter | 6 | 277 | 97 | Y | N |  | 0.07 |  |  | 100 | 360 | 450 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 91.5 | 94.7 | 95.9 | 96.6 | 96.8 | 96.8 | 96.3 | 93.3 | 96.2 | 96.9 | 97.4 | 97.4 | 97.4 | 97.1 | 94.3 | 96.7 | 97.3 | 97.9 | 97.8 | 97.7 | 97.6
Eaton | PV260 [240V] | 6 kW, 240 Vac Utility Interactive Inverter | 6.01 | 240 | 97 | Y | N |  | 0.08 |  |  | 100 | 360 | 450 | 0.6 | 1.2 | 1.8 | 3.01 | 4.51 | 6.01 | 93.8 | 96.1 | 96.4 | 96.8 | 96.8 | 96.6 | 96.6 | 95.5 | 97.1 | 97.7 | 97.7 | 97.7 | 97.4 | 97.5 | 93.9 | 96.2 | 97.1 | 97.4 | 97.4 | 97.2 | 97.2
Eaton | PV270 [240V] | 7 kW, 208 Vac Utility Interactive Inverter | 6.92 | 240 | 97 | Y | N |  | 0.17 |  |  | 100 | 360 | 450 | 0.69 | 1.38 | 2.08 | 3.46 | 5.19 | 6.92 | 94.3 | 96.2 | 96.7 | 96.8 | 96.7 | 96.4 | 96.6 | 95.5 | 97 | 97.5 | 97.6 | 97.5 | 97.3 | 97.4 | 94 | 96.2 | 96.9 | 97.3 | 97.3 | 97.2 | 97.1
Eaton | PV270 [208V] | 7 kW, 240 Vac Utility Interactive Inverter | 6.95 | 208 | 97 | Y | N |  | 0.09 |  |  | 100 | 360 | 470 | 0.7 | 1.39 | 2.09 | 3.48 | 5.21 | 6.95 | 96.1 | 97.3 | 97.5 | 97.3 | 97 | 96.5 | 97.1 | 95.6 | 97 | 97.4 | 97.1 | 96.9 | 96.6 | 97 | 93.8 | 96 | 96.6 | 96.9 | 96.7 | 96.4 | 96.6
Eaton | PV270 [277V] | 7 kW, 277 Vac Utility Interactive Inverter | 7.01 | 277 | 97 | Y | N |  | 0.02 |  |  | 100 | 360 | 450 | 0.7 | 1.4 | 2.1 | 3.51 | 5.26 | 7.01 | 93.4 | 95.9 | 96.5 | 96.8 | 96.6 | 96.4 | 96.5 | 94.8 | 96.6 | 97.2 | 97.5 | 97.1 | 97.1 | 97.1 | 94.9 | 96.9 | 97.4 | 97.7 | 97.6 | 97.4 | 97.5
Eaton | S-Max 250KW [480V] | S-Max™ Series 250 kW, 480 Vac ,3-phase Utility Interactive Inverter, 300-600 Vdc input | 250 | 480 | 96 | Y | N |  | 69.32 |  |  | 300 | 345 | 480 | 25 | 50 | 75 | 125 | 187.5 | 250 | 93.2 | 95.7 | 96.3 | 96.5 | 96.7 | 96.5 | 96.4 | 92.7 | 95.3 | 96 | 96.1 | 96.3 | 96.1 | 96 | 91.4 | 94.6 | 95.4 | 95.5 | 95.7 | 95.6 | 95.4
Eaton | Xpert1500 | 3-phase Utility Interactive Inverter | 1501 |  | 98 | Y | N |  | 332.5 |  |  | 500 | 575 | 800 | 150.1 | 300.2 | 450.3 | 750.5 | 1126 | 1501 | 96.7 | 98.2 | 98.5 | 98.6 | 98.5 | 98.5 | 98.4 | 96.3 | 98 | 98.3 | 98.5 | 98.3 | 98.4 | 98.3 | 95.1 | 97.4 | 97.9 | 98.2 | 98 | 98.2 | 97.9
Eaton | Xpert1670 | 3-phase Utility Interactive Inverter | 1671 |  | 98.5 | Y | N |  | 334.4 |  |  | 550 | 613 | 800 | 167.2 | 334.3 | 501.4 | 835.7 | 1254 | 1671 | 96.8 | 98.2 | 98.5 | 98.7 | 98.5 | 98.6 | 98.5 | 96.4 | 98 | 98.4 | 98.6 | 98.5 | 98.6 | 98.4 | 95.4 | 97.6 | 98.1 | 98.3 | 98.2 | 98.4 | 98.1
Elettronica Santerno | TG100NA208Y [208V] | 100 kW, 208 Vac, Utility Interactive Inverter | 100 | 208 | 96 | N | N |  | 27.4 |  |  | 300 | 345 | 480 | 10 | 20 | 30 | 50 | 75 | 100 | 90.1 | 94.5 | 95.8 | 96.5 | 96.5 | 96.5 | 96.1 | 89.5 | 94.3 | 95.7 | 96.4 | 96.5 | 96.4 | 96 | 88.6 | 93.5 | 95.2 | 96.1 | 96.2 | 96.2 | 95.6
Elettronica Santerno | TG100NA480Y [480V] | 125 kW, 480 Vac, Utility Interactive Inverter | 100 | 480 | 96 | N | N |  | 25.3 |  |  | 300 | 345 | 480 | 10 | 20 | 30 | 50 | 75 | 100 | 90.9 | 95 | 96 | 96.6 | 96.7 | 96.5 | 96.3 | 90.5 | 94.8 | 95.9 | 96.5 | 96.6 | 96.5 | 96.1 | 89.3 | 94 | 95.4 | 96.2 | 96.3 | 96.2 | 95.8
Elettronica Santerno | TG125NA208Y [208V] | 125 kW, 208 Vac, Utility Interactive Inverter | 125 | 208 | 96 | Y | N |  | 26.9 |  |  | 315 | 365 | 480 | 12.5 | 25 | 37.5 | 62.5 | 93.75 | 125 | 91.7 | 95.2 | 96.1 | 96.7 | 96.7 | 96.5 | 96.3 | 91.5 | 95 | 95.9 | 96.6 | 96.6 | 96.4 | 96.2 | 90.6 | 94.5 | 95.6 | 96.3 | 96.4 | 96.4 | 95.9
Elettronica Santerno | TG125NA480Y [480V] | 125 kW, 480 Vac, Utility Interactive Inverter | 125 | 480 | 96.5 | N | N |  | 17 |  |  | 315 | 365 | 480 | 12.5 | 25 | 37.5 | 62.5 | 93.75 | 125 | 92.1 | 95.6 | 96.4 | 96.7 | 96.9 | 96.7 | 96.5 | 91.7 | 95.3 | 96.2 | 96.8 | 96.8 | 96.6 | 96.4 | 90.5 | 94.7 | 95.8 | 96.5 | 96.6 | 96.4 | 96.1
Eltek | Theia 2.0He-t UL [208V] | 2.0 kW, 208 Vac Utility Interactive Inverter | 2.01 | 208 | 96.5 | Y | N |  | 0.9 |  |  | 100 | 365 | 490 | 0.2 | 0.4 | 0.6 | 1 | 1.51 | 2.01 | 91.7 | 95.1 | 95.6 | 96.5 | 96.6 | 96.3 | 96.2 | 92.9 | 95.4 | 96.2 | 96.8 | 96.9 | 96.7 | 96.6 | 91 | 94 | 95.3 | 96.3 | 96.6 | 96.6 | 96
Eltek | Theia 2.0He-t UL [240V] | 2.0 kW, 240 Vac Utility Interactive Inverter | 2.01 | 240 | 96.5 | Y | N |  | 0.97 |  |  | 100 | 375 | 490 | 0.2 | 0.4 | 0.6 | 1.01 | 1.51 | 2.01 | 91.9 | 95.3 | 96.1 | 96.7 | 96.8 | 96.7 | 96.4 | 91.2 | 95.2 | 96.1 | 96.9 | 97.1 | 97.1 | 96.6 | 91 | 94.5 | 95.6 | 96.6 | 97 | 97.1 | 96.4
Eltek | Theia 2.9He-t UL [240V] | 2.9 kW, 240 Vac Utility Interactive Inverter | 2.9 | 240 | 96.5 | Y | N |  | 0.98 |  |  | 100 | 375 | 490 | 0.29 | 0.58 | 0.87 | 1.45 | 2.18 | 2.9 | 93.4 | 95.9 | 96.5 | 96.8 | 96.5 | 96.1 | 96.4 | 93.3 | 96.1 | 96.8 | 97.2 | 97.1 | 97 | 96.9 | 92.2 | 95.5 | 96.3 | 96.9 | 97 | 96.9 | 96.6
Eltek | Theia 2.9He-t UL [208V] | 2.9 kW, 208 Vac Utility Interactive Inverter | 2.91 | 208 | 96.5 | Y | N |  | 0.92 |  |  | 100 | 365 | 490 | 0.29 | 0.58 | 0.87 | 1.45 | 2.18 | 2.91 | 93.7 | 95.9 | 96.2 | 96.5 | 96.3 | 95.6 | 96.2 | 93.9 | 96.1 | 96.6 | 96.8 | 96.6 | 96.3 | 96.5 | 91.9 | 95.1 | 96 | 96.5 | 96.5 | 96.3 | 96.2
Eltek | Theia 3.8He-t UL [208V] | 3.8 kW, 208 Vac Utility Interactive Inverter | 3.81 | 208 | 96.5 | Y | N |  | 0.77 |  |  | 100 | 360 | 500 | 0.381 | 0.762 | 1.143 | 1.905 | 2.858 | 3.81 | 94.62 | 96.34 | 96.7 | 96.68 | 96.21 | 95.57 | 96.28 | 94.76 | 96.49 | 96.91 | 97.03 | 96.77 | 96.53 | 96.74 | 93.09 | 95.63 | 96.36 | 96.79 | 96.73 | 96.51 | 96.49
Eltek | Theia 3.8He-t UL [240V] | 3.8 kW, 240 Vac Utility Interactive Inverter | 3.81 | 240 | 97 | Y | N |  | 0.9 |  |  | 100 | 370 | 500 | 0.381 | 0.762 | 1.143 | 1.905 | 2.858 | 3.81 | 94.77 | 96.6 | 96.9 | 96.88 | 96.53 | 95.99 | 96.55 | 94.57 | 96.59 | 97.08 | 97.27 | 97.17 | 96.84 | 97.03 | 93.25 | 95.84 | 96.59 | 97.02 | 97.06 | 96.92 | 96.78
Eltek | Theia 4.4He-t UL [208V] | 4.4 kW, 208 Vac Utility Interactive Inverter | 4.4 | 208 | 96.5 | Y | N |  | 0.8 |  |  | 100 | 360 | 500 | 0.4402 | 0.8804 | 1.321 | 2.201 | 3.302 | 4.402 | 95.08 | 96.51 | 96.69 | 96.45 | 95.87 | 95.09 | 96.05 | 95.24 | 96.64 | 96.98 | 96.99 | 96.71 | 96.25 | 96.71 | 93.55 | 95.89 | 96.43 | 96.74 | 96.52 | 96.17 | 96.38
Eltek | Theia 4.4He-t UL [240V] | 4.4 kW, 240 Vac Utility Interactive Inverter | 4.4 | 240 | 97 | Y | N |  | 0.97 |  |  | 100 | 370 | 500 | 0.44 | 0.88 | 1.32 | 2.2 | 3.3 | 4.4 | 95.3 | 96.75 | 96.95 | 96.75 | 96.4 | 95.59 | 96.47 | 95.22 | 96.8 | 97.18 | 97.24 | 97.09 | 96.74 | 97.02 | 93.92 | 96.15 | 96.69 | 97.02 | 96.98 | 96.73 | 96.78
Emerson Network Power | SPV-4.0AIUSO [240V] | 4 kW, 240 Vac, 1-phase Utility Interactive Inverter | 4 | 240 | 95 | N | N |  | 1.26 |  |  | 100 | 360 | 475 | 0.4 | 0.8 | 1.2 | 2 | 3 | 4 | 88.5 | 93.2 | 94.5 | 95.2 | 95.2 | 94.8 | 94.7 | 88.7 | 93.7 | 94.8 | 95.6 | 95.6 | 94.8 | 95.1 | 87.3 | 92.6 | 94.1 | 95.2 | 95.3 | 95.1 | 94.7
Emerson Network Power | SPV-4.5AIUSO [240V] | 4.5 kW, 240 Vac, 1-phase Utility Interactive Inverter | 4.49 | 240 | 95 | N | N |  | 1.26 |  |  | 100 | 360 | 475 | 0.45 | 0.9 | 1.35 | 2.24 | 3.36 | 4.49 | 88.88 | 93.68 | 94.71 | 95.29 | 95.06 | 94.49 | 94.7 | 89.9 | 94.07 | 95.07 | 95.66 | 95.57 | 94.49 | 95.2 | 88.73 | 93.09 | 94.42 | 95.25 | 95.27 | 94.89 | 94.8
Emerson Network Power | SPV-5.0AIUSO [240V] | 5 kW, 240 Vac, 1-phase Utility Interactive Inverter | 4.95 | 240 | 95 | N | N |  | 1.26 |  |  | 100 | 360 | 475 | 0.5 | 0.99 | 1.49 | 2.48 | 3.72 | 4.95 | 89.17 | 93.99 | 94.92 | 95.31 | 94.86 | 94.24 | 94.7 | 90.43 | 94.42 | 95.25 | 95.69 | 95.46 | 94.24 | 95.2 | 89.11 | 93.51 | 94.69 | 95.31 | 95.15 | 94.67 | 94.8
Enecsys | SMI-220 | 1-phase Microinverter with built-in monitoring system | 0.22 |  | 93 | N | Y |  | 0.06 |  |  | 30 | 34 | 42 | 0.022 | 0.044 | 0.066 | 0.11 | 0.165 | 0.22 | 84.9 | 91.38 | 93.21 | 94.16 | 94.17 | 93.59 | 93.51 | 82.55 | 90.46 | 92.55 | 93.97 | 94.18 | 93.75 | 93.27 | 78.52 | 88.13 | 90.82 | 92.99 | 93.85 | 93.93 | 92.41
Enecsys | SMI-240-60 | 1-phase Microinverter with built-in monitoring system | 0.225 |  | 93.5 | N | Y |  | 0.03 |  |  | 23 | 29 | 35 | 0.0225 | 0.045 | 0.0675 | 0.1125 | 0.1688 | 0.225 | 84.63 | 90.56 | 93.22 | 94.73 | 94.78 | 94.36 | 93.94 | 80.74 | 88.03 | 91.68 | 94.05 | 94.82 | 94.68 | 93.37 | 77.8 | 86.84 | 89.61 | 92.98 | 94.34 | 94.56 | 92.46
Enecsys | 240-60-xx | 1-phase Microinverter, where xx = MP, MM, or MM-S | 0.24 |  | 96 | N | Y |  | 0.03 |  |  | 24 | 29 | 35 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 92.6 | 95 | 95.6 | 96.4 | 96.3 | 95.9 | 96 | 90.7 | 94.3 | 95.3 | 96.1 | 96.4 | 96.2 | 95.8 | 89.6 | 93.5 | 94.7 | 95.6 | 96.2 | 96.2 | 95.5
Enecsys | 250NL | 0.25 kW, 1-phase Utility Interactive Microinverter | 0.25 |  | 95.5 | N | Y |  | 0.08 |  |  | 24 | 29 | 35 | 0.03 | 0.05 | 0.08 | 0.13 | 0.19 | 0.25 | 92.4 | 95.2 | 96 | 96 | 95.4 | 94.5 | 95.4 | 90.5 | 94.1 | 95.4 | 96 | 95.7 | 95.2 | 95.4 | 89.4 | 93.4 | 94.8 | 95.7 | 95.8 | 95.4 | 95.3
Enecsys | 260-60-xx | 1-phase Microinverter, where xx = MP, MM, or MM-S | 0.26 |  | 96 | N | Y |  | 0.03 |  |  | 24 | 29 | 35 | 0.03 | 0.05 | 0.08 | 0.13 | 0.2 | 0.26 | 93 | 95.2 | 95.6 | 96.4 | 96.2 | 95.7 | 96 | 91.2 | 94.6 | 95.3 | 96.2 | 96.3 | 96 | 95.9 | 90.2 | 93.6 | 94.8 | 95.7 | 96.2 | 96.1 | 95.5
Enecsys | SMI-280-72 | 1-phase Microinverter with built-in monitoring system | 0.265 |  | 94.5 | N | Y |  | 0.03 |  |  | 30 | 34 | 42 | 0.0265 | 0.053 | 0.0795 | 0.1325 | 0.1988 | 0.265 | 85.57 | 92.75 | 94.36 | 95.41 | 95.29 | 94.87 | 94.67 | 82.99 | 91.53 | 93.74 | 95.17 | 95.35 | 95.08 | 94.42 | 80.03 | 89.45 | 92.28 | 94.42 | 95.1 | 95.12 | 93.73
Enecsys | 280-60-xx | 1-phase Microinverter, where xx = MP, MM, or MM-S | 0.28 |  | 96 | N | Y |  | 0.03 |  |  | 24 | 29 | 35 | 0.03 | 0.06 | 0.08 | 0.14 | 0.21 | 0.28 | 93.3 | 95.3 | 95.6 | 96.4 | 96.1 | 95.5 | 95.9 | 91.4 | 94.7 | 95.4 | 96.4 | 96.3 | 95.9 | 95.9 | 90.5 | 93.9 | 94.8 | 95.8 | 96.1 | 96 | 95.6
Enecsys | 300-60-xx | 1-phase Microinverter, where xx = MP, MM, or MM-S | 0.3 |  | 96 | N | Y |  | 0.03 |  |  | 24 | 29 | 35 | 0.03 | 0.06 | 0.09 | 0.15 | 0.23 | 0.3 | 93.6 | 95.4 | 95.7 | 96.4 | 95.9 | 95.3 | 95.9 | 91.9 | 94.8 | 95.4 | 96.4 | 96.2 | 95.8 | 95.9 | 91.1 | 94.1 | 95 | 96 | 96.1 | 96 | 95.7
Enecsys | SMI-360-72 | 1-phase Microinverter with built-in monitoring system | 0.34 |  | 94.5 | N | Y |  | 0.03 |  |  | 30 | 34 | 42 | 0.034 | 0.068 | 0.102 | 0.17 | 0.255 | 0.34 | 89.15 | 93.97 | 94.95 | 95.41 | 95 | 94.49 | 94.77 | 87.1 | 93.07 | 94.48 | 95.4 | 95.14 | 94.58 | 94.66 | 83.7 | 91.1 | 93.35 | 94.94 | 95.13 | 94.95 | 94.21
Enecsys | SMI-480-60 | 1-phase Microinverter with built-in monitoring system | 0.455 |  | 94.5 | N | Y |  | 0.05 |  |  | 24 | 29 | 35 | 0.0455 | 0.091 | 0.1365 | 0.2275 | 0.3413 | 0.455 | 91.9 | 94.3 | 95.1 | 95 | 94.4 | 93.8 | 94.5 | 90.5 | 93 | 94.3 | 95.1 | 95 | 94.4 | 94.6 | 89.2 | 91.3 | 93.1 | 94 | 94.6 | 94.4 | 93.9
EnluxSolar | EL-300 | 300 W Utility Interactive Inverter | 0.3 |  | 96 | N | N |  | 0.064 |  |  | 25 | 30 | 35 | 0.0305 | 0.061 | 0.0915 | 0.1525 | 0.2288 | 0.305 | 92.8 | 95.8 | 96.5 | 96.6 | 96.1 | 95.5 | 96.1 | 92.4 | 95.6 | 96.4 | 96.6 | 96.2 | 95.5 | 96.1 | 92 | 95.5 | 96.3 | 96.5 | 96.2 | 95.6 | 96 | 2017-03
Enphase Energy Inc. | M175-24-208-Sxx [208V] | 175 W, 24 Vdc, 208 Vac, Utility Interactive modular Inverter, where xx = 01 or 02. | 0.175 | 208 | 94.5 | N | Y |  | 0.56 | 0.175 | 0.56 | 25 | 32.5 | 40 | 0.0175 | 0.035 | 0.0525 | 0.0875 | 0.1313 | 0.175 | 91.9 | 93.5 | 94.2 | 94.6 | 94.5 | 94.1 | 94.3 | 91.6 | 92.9 | 94 | 94.6 | 94.9 | 94.7 | 94.5 | 91.3 | 92.3 | 93.3 | 94.3 | 94.9 | 94.9 | 94.3
Enphase Energy Inc. | M175-24-208-Sxx-NA [208V] | 175 W, 24 Vdc, 208 Vac Inverter, xx = connector types, -NA if North American | 0.175 | 208 | 94.5 | N | Y |  | 0.56 | 0.175 | 0.56 | 25 | 32.5 | 40 | 0.0175 | 0.035 | 0.0525 | 0.0875 | 0.1313 | 0.175 | 91.9 | 93.5 | 94.2 | 94.6 | 94.5 | 94.1 | 94.3 | 91.6 | 92.9 | 94 | 94.6 | 94.9 | 94.7 | 94.5 | 91.3 | 92.3 | 93.3 | 94.3 | 94.9 | 94.9 | 94.3
Enphase Energy Inc. | M175-24-240-Sxx [240V] | 175 W, 24 Vdc, 240 Vac, Utility Interactive modular Inverter, where xx = 01 or 02. | 0.175 | 240 | 94.5 | N | Y |  | 0.58 | 0.175 | 0.58 | 25 | 32.5 | 40 | 0.0175 | 0.035 | 0.0525 | 0.0875 | 0.1313 | 0.175 | 91.2 | 93 | 94.1 | 94.6 | 94.6 | 94.3 | 94.3 | 90.7 | 92.6 | 93.8 | 94.4 | 94.9 | 94.9 | 94.4 | 90.2 | 91.9 | 93.1 | 94 | 94.7 | 94.9 | 94.1
Enphase Energy Inc. | M175-24-240-Sxx-NA [240V] | 175 W, 24 Vdc, 240 Vac Inverter, xx = connector types, -NA if North American | 0.175 | 240 | 94.5 | N | Y |  | 0.58 | 0.175 | 0.58 | 25 | 32.5 | 40 | 0.0175 | 0.035 | 0.0525 | 0.0875 | 0.1313 | 0.175 | 91.2 | 93 | 94.1 | 94.6 | 94.6 | 94.3 | 94.3 | 90.7 | 92.6 | 93.8 | 94.4 | 94.9 | 94.9 | 94.4 | 90.2 | 91.9 | 93.1 | 94 | 94.7 | 94.9 | 94.1
Enphase Energy Inc. | M190-72-208-Sxx [208V] | 190 W, 32Vdc, 208 Vac, Utility Interactive modular Inverter, where xx = 11, 12, or 13. | 0.19 | 208 | 95 | N | Y |  | 0.01 | 0.19 | 0.01 | 22 | 32 | 40 | 0.019 | 0.038 | 0.057 | 0.095 | 0.1425 | 0.19 | 93.6 | 94.6 | 94.9 | 95 | 94.6 | 93.7 | 94.6 | 93.4 | 94.6 | 94.7 | 95.2 | 95.2 | 94.8 | 95 | 93.4 | 94.4 | 94.8 | 95.1 | 95.3 | 95.1 | 95.1
Enphase Energy Inc. | M190-72-208-Sxx-NA [208V] | 190 W, 24 Vdc, 208 Vac Inverter, xx = connector types, -NA if North American | 0.19 | 208 | 95 | N | Y |  | 0.01 | 0.19 | 0.01 | 22 | 32 | 40 | 0.019 | 0.038 | 0.057 | 0.095 | 0.1425 | 0.19 | 93.6 | 94.6 | 94.9 | 95 | 94.6 | 93.7 | 94.6 | 93.4 | 94.6 | 94.7 | 95.2 | 95.2 | 94.8 | 95 | 93.4 | 94.4 | 94.8 | 95.1 | 95.3 | 95.1 | 95.1
Enphase Energy Inc. | M190-72-240-Sxx [240V] | 175 W, 24 Vdc, 240 Vac Inverter, xx = connector types, -NA if North American | 0.19 | 240 | 95 | N | Y |  | 0.03 | 0.19 | 0.03 | 22 | 32.5 | 40 | 0.019 | 0.038 | 0.057 | 0.095 | 0.1425 | 0.19 | 93.3 | 94.4 | 94.7 | 95.1 | 94.9 | 94.2 | 94.8 | 93.3 | 94.4 | 94.6 | 95.2 | 95.4 | 95.1 | 95.1 | 93.5 | 94.4 | 94.6 | 94.9 | 95.4 | 95.4 | 95.1
Enphase Energy Inc. | M190-72-240-Sxx-NA [240V] | 190 W, 24 Vdc, 240 Vac Inverter, xx = connector types, -NA if North American | 0.19 | 240 | 95 | N | Y |  | 0.03 | 0.19 | 0.03 | 22 | 32.5 | 40 | 0.019 | 0.038 | 0.057 | 0.095 | 0.1425 | 0.19 | 93.3 | 94.4 | 94.7 | 95.1 | 94.9 | 94.2 | 94.8 | 93.3 | 94.4 | 94.6 | 95.2 | 95.4 | 95.1 | 95.1 | 93.5 | 94.4 | 94.6 | 94.9 | 95.4 | 95.4 | 95.1
Enphase Energy Inc. | M200-32-208-Sxx [240V] | 175 W, 24 Vdc, 240 Vac Inverter, xx = connector types, -NA if North American | 0.2 | 240 | 95 | N | Y |  | 0.56 | 0.2 | 0.56 | 44 | 54.5 | 65 | 0.02 | 0.04 | 0.06 | 0.1 | 0.15 | 0.2 | 92.5 | 94.2 | 94.6 | 95.2 | 95.3 | 95.1 | 95 | 92.4 | 94.3 | 94.5 | 95 | 95.4 | 95.3 | 95 | 91.9 | 94.1 | 94.2 | 94.6 | 95.2 | 95.3 | 94.8
Enphase Energy Inc. | M200-32-208-Sxx-NA [208V] | 200 W, 52.5 Vdc, 208 Vac, xx = connector types, -NA if North American | 0.2 | 208 | 95 | N | Y |  | 0.56 | 0.2 | 0.56 | 44 | 54.5 | 65 | 0.02 | 0.04 | 0.06 | 0.1 | 0.15 | 0.2 | 92.5 | 94.2 | 94.6 | 95.2 | 95.3 | 95.1 | 95 | 92.4 | 94.3 | 94.5 | 95 | 95.4 | 95.3 | 95 | 91.9 | 94.1 | 94.2 | 94.6 | 95.2 | 95.3 | 94.8
Enphase Energy Inc. | M200-32-240-Sxx [240V] | 200 W, 52.5 Vdc, 240 Vac, Utility Interactive modular Inverter, where xx = 01 or 02. | 0.2 | 240 | 95 | N | Y |  | 0.48 | 0.2 | 0.48 | 44 | 54.5 | 65 | 0.02 | 0.04 | 0.06 | 0.1 | 0.15 | 0.2 | 92.5 | 94.2 | 94.6 | 95.2 | 95.3 | 95.1 | 95 | 92.4 | 94.3 | 94.5 | 95 | 95.4 | 95.3 | 95 | 91.9 | 94.1 | 94.2 | 94.6 | 95.2 | 95.3 | 94.8
Enphase Energy Inc. | M200-32-240-Sxx-NA [240V] | 200 W, 52.5 Vdc, 240 Vac, xx = connector types, -NA if North American | 0.2 | 240 | 95 | N | Y |  | 0.48 | 0.2 | 0.48 | 44 | 54.5 | 65 | 0.02 | 0.04 | 0.06 | 0.1 | 0.15 | 0.2 | 92.5 | 94.2 | 94.6 | 95.2 | 95.3 | 95.1 | 95 | 92.4 | 94.3 | 94.5 | 95 | 95.4 | 95.3 | 95 | 91.9 | 94.1 | 94.2 | 94.6 | 95.2 | 95.3 | 94.8
Enphase Energy Inc. | M210-84-208-Sxx [208V] | 210 W, 40.5 Vdc, 208 Vac, Utility Interactive modular Inverter, where xx = 11, 12, or 13. | 0.21 | 208 | 95.5 | N | Y |  | 0 | 0.21 | 0 | 31 | 40.5 | 50 | 0.021 | 0.042 | 0.063 | 0.105 | 0.1575 | 0.21 | 94 | 95.3 | 95.5 | 95.8 | 95.3 | 94.6 | 95.3 | 94.1 | 95.3 | 95.5 | 95.9 | 95.8 | 95.3 | 95.6 | 94 | 95 | 95.5 | 95.8 | 95.9 | 95.6 | 95.7
Enphase Energy Inc. | M210-84-208-Sxx-NA [208V] | 210 W, 40.5 Vdc, 208 Vac Inverter, xx = connector types, -NA if North American | 0.21 | 208 | 95.5 | N | Y |  | 0 | 0.21 | 0 | 31 | 40.5 | 50 | 0.021 | 0.042 | 0.063 | 0.105 | 0.1575 | 0.21 | 94 | 95.3 | 95.5 | 95.8 | 95.3 | 94.6 | 95.3 | 94.1 | 95.3 | 95.5 | 95.9 | 95.8 | 95.3 | 95.6 | 94 | 95 | 95.5 | 95.8 | 95.9 | 95.6 | 95.7
Enphase Energy Inc. | M210-84-240-Sxx [240V] | 210 W, 40.5 Vdc, 240 Vac, Utility Interactive modular Inverter, where xx = 11, 12, or 13. | 0.21 | 240 | 95.5 | N | Y |  | 0.01 | 0.21 | 0.01 | 31 | 40.5 | 50 | 0.021 | 0.042 | 0.063 | 0.105 | 0.1575 | 0.21 | 94 | 95.3 | 95.4 | 95.8 | 95.5 | 94.8 | 95.4 | 94.2 | 95.3 | 95.6 | 95.9 | 95.8 | 95.4 | 95.7 | 94.2 | 95.2 | 95.5 | 95.8 | 95.9 | 95.7 | 95.7
Enphase Energy Inc. | M210-84-240-Sxx-NA [240V] | 210 W, 40.5 Vdc, 240 Vac Inverter, xx = connector types, -NA if North American | 0.21 | 240 | 95.5 | N | Y |  | 0.01 | 0.21 | 0.01 | 31 | 40.5 | 50 | 0.021 | 0.042 | 0.063 | 0.105 | 0.1575 | 0.21 | 94 | 95.3 | 95.4 | 95.8 | 95.5 | 94.8 | 95.4 | 94.2 | 95.3 | 95.6 | 95.9 | 95.8 | 95.4 | 95.7 | 94.2 | 95.2 | 95.5 | 95.8 | 95.9 | 95.7 | 95.7
Enphase Energy Inc. | M215-60-2LL-S2x [208V] | 215 W, 208 Vac Inverter, S2x are connector types | 0.215 | 208 | 96 | N | Y |  | 0.04 | 0.215 | 0.04 | 22 | 29 | 36 | 0.02 | 0.04 | 0.06 | 0.11 | 0.16 | 0.22 | 94.5 | 95.5 | 95.9 | 96 | 95.5 | 94.7 | 95.6 | 94.5 | 95.5 | 95.9 | 96.1 | 96 | 95.5 | 95.9 | 94.4 | 95.4 | 95.7 | 96.1 | 96.1 | 95.8 | 95.9
Enphase Energy Inc. | M215-60-2LL-S2x [240V] | 215 W, 240 Vac Inverter, S2x are connector types | 0.215 | 240 | 96 | N | Y |  | 0.04 | 0.215 | 0.04 | 22 | 29 | 36 | 0.02 | 0.04 | 0.06 | 0.11 | 0.16 | 0.22 | 94.5 | 95.5 | 95.9 | 96 | 95.5 | 94.7 | 95.6 | 94.5 | 95.5 | 95.9 | 96.1 | 96 | 95.5 | 95.9 | 94.4 | 95.4 | 95.7 | 96.1 | 96.1 | 95.8 | 95.9
Enphase Energy Inc. | M215-60-2LL-S2x-IG [208V] | 208 Vac Microinverter for use with ungrounded arrays, where x = 1, 2, 3, 4, or 5 | 0.215 | 208 | 96 | N | Y |  | 0.05 | 0.215 | 0.05 | 22 | 29 | 36 | 0.0215 | 0.043 | 0.0645 | 0.1075 | 0.1613 | 0.215 | 94.64 | 95.53 | 95.86 | 95.92 | 95.53 | 94.79 | 95.58 | 94.64 | 95.62 | 95.92 | 96.11 | 96.01 | 95.61 | 95.93 | 94.6 | 95.53 | 95.83 | 96.1 | 96.15 | 95.94 | 96
Enphase Energy Inc. | M215-60-2LL-S2x-IG [240V] | 240 Vac Microinverter for use with ungrounded arrays, where x = 1, 2, 3, 4, or 5 | 0.215 | 240 | 96 | N | Y |  | 0.05 | 0.215 | 0.05 | 22 | 29 | 36 | 0.0215 | 0.043 | 0.0645 | 0.1075 | 0.1613 | 0.215 | 94.66 | 95.6 | 95.99 | 96.13 | 95.89 | 95.3 | 95.86 | 94.69 | 95.68 | 96.05 | 96.26 | 96.27 | 96 | 96.13 | 94.62 | 95.6 | 95.97 | 96.27 | 96.34 | 96.24 | 96.17
Enphase Energy Inc. | M215-60-2LL-S2x-IG-NA [208V] | 215 W, 208 Vac Inverter, where S2x are connector types | 0.215 | 208 | 96 | N | Y |  | 0.05 | 0.215 | 0.05 | 22 | 29 | 36 | 0.0215 | 0.043 | 0.0645 | 0.1075 | 0.1613 | 0.215 | 94.64 | 95.53 | 95.86 | 95.92 | 95.53 | 94.79 | 95.58 | 94.64 | 95.62 | 95.92 | 96.11 | 96.01 | 95.61 | 95.93 | 94.6 | 95.53 | 95.83 | 96.1 | 96.15 | 95.94 | 96
Enphase Energy Inc. | M215-60-2LL-S2x-IG-NA [240V] | 215 W, 240 Vac Inverter, where S2x are connector types | 0.215 | 240 | 96 | N | Y |  | 0.05 | 0.215 | 0.05 | 22 | 29 | 36 | 0.0215 | 0.043 | 0.0645 | 0.1075 | 0.1613 | 0.215 | 94.66 | 95.6 | 95.99 | 96.13 | 95.89 | 95.3 | 95.86 | 94.69 | 95.68 | 96.05 | 96.26 | 96.27 | 96 | 96.13 | 94.62 | 95.6 | 95.97 | 96.27 | 96.34 | 96.24 | 96.17
Enphase Energy Inc. | M215-60-2LL-S2x-IG-ZC [208V] | 215 W, 208 Vac Inverter, where S2x are connector types, and ZC is mount | 0.215 | 208 | 96 | N | Y |  | 0.05 | 0.215 | 0.05 | 22 | 29 | 36 | 0.0215 | 0.043 | 0.0645 | 0.1075 | 0.1613 | 0.215 | 94.64 | 95.53 | 95.86 | 95.92 | 95.53 | 94.79 | 95.58 | 94.64 | 95.62 | 95.92 | 96.11 | 96.01 | 95.61 | 95.93 | 94.6 | 95.53 | 95.83 | 96.1 | 96.15 | 95.94 | 96
Enphase Energy Inc. | M215-60-2LL-S2x-IG-ZC [240V] | 215 W, 240 Vac Inverter, where S2x are connector types, and ZC is mount | 0.215 | 240 | 96 | N | Y |  | 0.05 | 0.215 | 0.05 | 22 | 29 | 36 | 0.0215 | 0.043 | 0.0645 | 0.1075 | 0.1613 | 0.215 | 94.66 | 95.6 | 95.99 | 96.13 | 95.89 | 95.3 | 95.86 | 94.69 | 95.68 | 96.05 | 96.26 | 96.27 | 96 | 96.13 | 94.62 | 95.6 | 95.97 | 96.27 | 96.34 | 96.24 | 96.17
Enphase Energy Inc. | M215-60-2LL-S2x-IG-ZC-NA [208V] | 215 W, 208 Vac Inverter, where S2x are connector types, and ZC is mount | 0.215 | 208 | 96 | N | Y |  | 0.05 | 0.215 | 0.05 | 22 | 29 | 36 | 0.0215 | 0.043 | 0.0645 | 0.1075 | 0.1613 | 0.215 | 94.64 | 95.53 | 95.86 | 95.92 | 95.53 | 94.79 | 95.58 | 94.64 | 95.62 | 95.92 | 96.11 | 96.01 | 95.61 | 95.93 | 94.6 | 95.53 | 95.83 | 96.1 | 96.15 | 95.94 | 96
Enphase Energy Inc. | M215-60-2LL-S2x-IG-ZC-NA [240V] | 215 W, 240 Vac Inverter, where S2x are connector types, and ZC is mount | 0.215 | 240 | 96 | N | Y |  | 0.05 | 0.215 | 0.05 | 22 | 29 | 36 | 0.0215 | 0.043 | 0.0645 | 0.1075 | 0.1613 | 0.215 | 94.66 | 95.6 | 95.99 | 96.13 | 95.89 | 95.3 | 95.86 | 94.69 | 95.68 | 96.05 | 96.26 | 96.27 | 96 | 96.13 | 94.62 | 95.6 | 95.97 | 96.27 | 96.34 | 96.24 | 96.17
Enphase Energy Inc. | M215-60-2LL-S2x-NA [208V] | 215 W, 208 Vac Inverter, where S2x are connector types | 0.215 | 208 | 96 | N | Y |  | 0.04 | 0.215 | 0.04 | 22 | 29 | 36 | 0.02 | 0.04 | 0.06 | 0.11 | 0.16 | 0.22 | 94.5 | 95.5 | 95.9 | 96 | 95.5 | 94.7 | 95.6 | 94.5 | 95.5 | 95.9 | 96.1 | 96 | 95.5 | 95.9 | 94.4 | 95.4 | 95.7 | 96.1 | 96.1 | 95.8 | 95.9
Enphase Energy Inc. | M215-60-2LL-S2x-NA [240V] | 215 W, 240 Vac Inverter, where S2x are connector types | 0.215 | 240 | 96 | N | Y
Enphase Energy Inc. | M215-60-2LL-S2x-ZC [240V] | 215 W, 240 Vac Inverter, where S2x are connector types | 0.215 | 240 | 96 | N | Y |  | 0.04 | 0.215 | 0.04 | 22 | 29 | 36 | 0.02 | 0.04 | 0.06 | 0.11 | 0.16 | 0.22 | 94.5 | 95.5 | 95.9 | 96 | 95.5 | 94.7 | 95.6 | 94.5 | 95.5 | 95.9 | 96.1 | 96 | 95.5 | 95.9 | 94.4 | 95.4 | 95.7 | 96.1 | 96.1 | 95.8 | 95.9
Enphase Energy Inc. | M215-60-2LL-S2x-ZC-NA [208V] | 215 W, 208 Vac Inverter, where S2x are connector types, and ZC is mount | 0.215 | 208 | 96 | N | Y |  | 0.04 | 0.215 | 0.04 | 22 | 29 | 36 | 0.02 | 0.04 | 0.06 | 0.11 | 0.16 | 0.22 | 94.5 | 95.5 | 95.9 | 96 | 95.5 | 94.7 | 95.6 | 94.5 | 95.5 | 95.9 | 96.1 | 96 | 95.5 | 95.9 | 94.4 | 95.4 | 95.7 | 96.1 | 96.1 | 95.8 | 95.9
Enphase Energy Inc. | M215-60-2LL-S2x-ZC-NA [240V] | 215 W, 240 Vac Inverter, where S2x are connector types, and ZC is mount | 0.215 | 240 | 96 | N | Y |  | 0.04 | 0.215 | 0.04 | 22 | 29 | 36 | 0.02 | 0.04 | 0.06 | 0.11 | 0.16 | 0.22 | 94.5 | 95.5 | 95.9 | 96 | 95.5 | 94.7 | 95.6 | 94.5 | 95.5 | 95.9 | 96.1 | 96 | 95.5 | 95.9 | 94.4 | 95.4 | 95.7 | 96.1 | 96.1 | 95.8 | 95.9
Enphase Energy Inc. | M215-60-SIE-S2x [208V] | 215 W, 208 Vac Inverter, where S2x are connector types, and ZC is mount | 0.215 | 208 | 96 | N | Y |  | 0.04 | 0.215 | 0.04 | 22 | 29 | 36 | 0.02 | 0.04 | 0.06 | 0.11 | 0.16 | 0.22 | 94.5 | 95.5 | 95.9 | 96 | 95.5 | 94.7 | 95.6 | 94.5 | 95.5 | 95.9 | 96.1 | 96 | 95.5 | 95.9 | 94.4 | 95.4 | 95.7 | 96.1 | 96.1 | 95.8 | 95.9
Enphase Energy Inc. | M215-60-SIE-S2x [240V] | 215 W, 240 Vac Inverter, where S2x are connector types, and ZC is mount | 0.215 | 240 | 96 | N | Y |  | 0.04 | 0.215 | 0.04 | 22 | 29 | 36 | 0.02 | 0.04 | 0.06 | 0.11 | 0.16 | 0.22 | 94.5 | 95.5 | 95.9 | 96 | 95.5 | 94.7 | 95.6 | 94.5 | 95.5 | 95.9 | 96.1 | 96 | 95.5 | 95.9 | 94.4 | 95.4 | 95.7 | 96.1 | 96.1 | 95.8 | 95.9
Enphase Energy Inc. | M215-60-SIE-S2x-NA [208V] | 215 W, 208 Vac Inverter, where S2x are connector types, and ZC is mount | 0.215 | 208 | 96 | N | Y |  | 0.04 | 0.215 | 0.04 | 22 | 29 | 36 | 0.02 | 0.04 | 0.06 | 0.11 | 0.16 | 0.22 | 94.5 | 95.5 | 95.9 | 96 | 95.5 | 94.7 | 95.6 | 94.5 | 95.5 | 95.9 | 96.1 | 96 | 95.5 | 95.9 | 94.4 | 95.4 | 95.7 | 96.1 | 96.1 | 95.8 | 95.9
Enphase Energy Inc. | M215-60-SIE-S2x-NA [240V] | 215 W, 240 Vac Inverter, where S2x are connector types, and ZC is mount | 0.215 | 240 | 96 | N | Y |  | 0.04 | 0.215 | 0.04 | 22 | 29 | 36 | 0.02 | 0.04 | 0.06 | 0.11 | 0.16 | 0.22 | 94.5 | 95.5 | 95.9 | 96 | 95.5 | 94.7 | 95.6 | 94.5 | 95.5 | 95.9 | 96.1 | 96 | 95.5 | 95.9 | 94.4 | 95.4 | 95.7 | 96.1 | 96.1 | 95.8 | 95.9
Enphase Energy Inc. | M215-60-SIE-S2x-ZC [208V] | 215 W, 208 Vac Inverter, where S2x are connector types, and ZC is mount | 0.215 | 208 | 96 | N | Y |  | 0.04 | 0.215 | 0.04 | 22 | 29 | 36 | 0.02 | 0.04 | 0.06 | 0.11 | 0.16 | 0.22 | 94.5 | 95.5 | 95.9 | 96 | 95.5 | 94.7 | 95.6 | 94.5 | 95.5 | 95.9 | 96.1 | 96 | 95.5 | 95.9 | 94.4 | 95.4 | 95.7 | 96.1 | 96.1 | 95.8 | 95.9
Enphase Energy Inc. | M215-60-SIE-S2x-ZC [240V] | 215 W, 240 Vac Inverter, where S2x are connector types, and ZC is mount | 0.215 | 240 | 96 | N | Y |  | 0.04 | 0.215 | 0.04 | 22 | 29 | 36 | 0.02 | 0.04 | 0.06 | 0.11 | 0.16 | 0.22 | 94.5 | 95.5 | 95.9 | 96 | 95.5 | 94.7 | 95.6 | 94.5 | 95.5 | 95.9 | 96.1 | 96 | 95.5 | 95.9 | 94.4 | 95.4 | 95.7 | 96.1 | 96.1 | 95.8 | 95.9
Enphase Energy Inc. | M215-60-SIE-S2x-ZC-NA [208V] | 215 W, 208 Vac Inverter, where S2x are connector types, and ZC is mount | 0.215 | 208 | 96 | N | Y |  | 0.04 | 0.215 | 0.04 | 22 | 29 | 36 | 0.02 | 0.04 | 0.06 | 0.11 | 0.16 | 0.22 | 94.5 | 95.5 | 95.9 | 96 | 95.5 | 94.7 | 95.6 | 94.5 | 95.5 | 95.9 | 96.1 | 96 | 95.5 | 95.9 | 94.4 | 95.4 | 95.7 | 96.1 | 96.1 | 95.8 | 95.9
Enphase Energy Inc. | M215-60-SIE-S2x-ZC-NA [240V] | 215 W, 240 Vac Inverter, where S2x are connector types, and ZC is mount | 0.215 | 240 | 96 | N | Y |  | 0.04 | 0.215 | 0.04 | 22 | 29 | 36 | 0.02 | 0.04 | 0.06 | 0.11 | 0.16 | 0.22 | 94.5 | 95.5 | 95.9 | 96 | 95.5 | 94.7 | 95.6 | 94.5 | 95.5 | 95.9 | 96.1 | 96 | 95.5 | 95.9 | 94.4 | 95.4 | 95.7 | 96.1 | 96.1 | 95.8 | 95.9
Enphase Energy Inc. | S230-60-LL-x [208V] | 230 W, 240 Vac, Utility Interactive Microinverter, where x = 2, 3, 4, or 5 and may be followed by -US | 0.22 | 208 | 97 | N | Y |  | 0.051 |  |  | 27 | 32 | 37 | 0.02 | 0.04 | 0.07 | 0.11 | 0.17 | 0.22 | 94.9 | 96.5 | 96.4 | 97.2 | 97.2 | 96.9 | 97 | 94.9 | 96.4 | 96.1 | 97.1 | 97.1 | 96.8 | 96.8 | 94.8 | 96.3 | 95.8 | 96.9 | 97 | 96.7 | 96.7 | 2017-10-16 | 2018-10-15
Enphase Energy Inc. | S230-60-LL-x [240V] | 230 W, 240 Vac, Utility Interactive Microinverter, where x = 2, 3, 4, or 5 and may be followed by -US | 0.22 | 240 | 97 | N | Y |  | 0.051 |  |  | 27 | 32 | 37 | 0.02 | 0.04 | 0.07 | 0.11 | 0.17 | 0.22 | 95 | 96.4 | 96.2 | 97.4 | 97.5 | 97.4 | 97.2 | 95 | 96.5 | 95.8 | 97.2 | 97.3 | 97.2 | 97 | 94.9 | 96.4 | 95.4 | 96.9 | 97.2 | 97.2 | 96.8 | 2017-10-16 | 2018-10-15
Enphase Energy Inc. | IQ6-60-ACM-US [208V] | 230 W, 208 Vac Utility Interactive Microinverter for ACPV Module applications | 0.23 | 208 | 97 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.02 |  |  | 27 | 32 | 37 | 0.023 | 0.046 | 0.069 | 0.115 | 0.1725 | 0.23 | 94.1975 | 95.7125 | 96.3485 | 97.2626 | 97.2603 | 96.9175 | 96.9343 | 94.4525 | 95.865 | 96.241 | 97.1193 | 97.1982 | 96.9745 | 96.8791 | 94.1798 | 95.6904 | 96.0834 | 96.9677 | 97.0876 | 96.9175 | 96.7472 | 2017-08-01 | 2018-10-15
Enphase Energy Inc. | IQ6-60-ACM-US [240V] | 230W, 240 Vac Utility Interactive Microinverter for ACPV Module applications | 0.23 | 240 | 97 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.03 |  |  | 27 | 32 | 37 | 0.023 | 0.046 | 0.069 | 0.115 | 0.1725 | 0.23 | 94.6552 | 96.0377 | 96.6656 | 97.4237 | 97.4849 | 97.2559 | 97.1768 | 95.0606 | 96.3568 | 96.7065 | 97.3927 | 97.5863 | 97.5296 | 97.2747 | 94.745 | 96.1054 | 96.4314 | 97.1967 | 97.4693 | 97.4835 | 97.1111 | 2017-08-01 | 2018-10-15
Enphase Energy Inc. | IQ6-60-x-US [208V] | 230 W, 208 Vac Utility Interactive Microinverter where x = DC Connector type = 2 or 5 | 0.23 | 208 | 97 | N | Y |  | 0.02 |  |  | 27 | 32 | 37 | 23 | 46 | 69 | 115 | 172.5 | 230 | 94.1975 | 95.7125 | 96.3485 | 97.2626 | 97.2603 | 96.9175 | 96.9343 | 94.4525 | 95.865 | 96.241 | 97.1193 | 97.1982 | 96.9745 | 96.8791 | 94.1798 | 95.6904 | 96.0834 | 96.9677 | 97.0876 | 96.9175 | 96.7472 | 2017-08-01 | 2018-10-15
Enphase Energy Inc. | IQ6-60-x-US [240V] | 230 W, 240 Vac Utility Interactive Microinverter where x = DC Connector type = 2 or 5 | 0.23 | 240 | 97 | N | Y |  | 0.03 |  |  | 27 | 32 | 37 | 0.023 | 0.046 | 0.069 | 0.115 | 0.1725 | 0.23 | 94.6552 | 96.0377 | 96.6656 | 97.4237 | 97.4849 | 97.2559 | 97.1768 | 95.0606 | 96.3568 | 96.7065 | 97.3927 | 97.5863 | 97.5296 | 97.2748 | 94.745 | 96.1054 | 96.4314 | 97.1967 | 97.4693 | 97.4835 | 97.111 | 2017-08-01 | 2018-10-15
Enphase Energy Inc. | IQ7-60-x-ACM-US [208V] | 240 VA, 208 Vac Utility Interactive Microinverter for use in ACPV Module applications where x = DC Connector type = B or blank | 0.24 | 208 | 97 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.025 |  |  | 27 | 32 | 37 | 0.024 | 0.048 | 0.072 | 0.12 | 0.18 | 0.24 | 94.2043 | 96.2264 | 97.0215 | 97.5539 | 97.4142 | 96.9598 | 97.1859 | 93.3248 | 95.7344 | 96.7563 | 97.4639 | 97.4153 | 97.0564 | 97.0808 | 92.4192 | 95.0959 | 96.5384 | 97.3538 | 97.3374 | 97.0253 | 96.9205 | 2017-12-15 | 2018-10-15
Enphase Energy Inc. | IQ7-60-x-ACM-US [240V] | 240 VA, 240 Vac Utility Interactive Microinverter for use in ACPV Module applications where x = DC Connector type = B or blank | 0.24 | 240 | 97 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.025 |  |  | 27 | 32 | 37 | 0.024 | 0.048 | 0.072 | 0.12 | 0.18 | 0.24 | 93.9453 | 96.08 | 96.8145 | 97.4746 | 97.4192 | 97.0288 | 97.1328 | 92.9907 | 95.6588 | 96.5049 | 97.5523 | 97.615 | 97.4087 | 97.1755 | 92.0062 | 95.0264 | 96.2309 | 97.3813 | 97.5438 | 97.4107 | 96.9981 | 2017-12-15 | 2018-10-15
Enphase Energy Inc. | IQ7-60-x-US [208V] | 240 VA, 208 Vac Utility Interactive Microinverter where x = DC Connector type = 2, 5, or B | 0.24 | 208 | 97 | N | Y |  | 0.025 |  |  | 27 | 32 | 37 | 0.024 | 0.048 | 0.072 | 0.12 | 0.18 | 0.24 | 94.2043 | 96.2264 | 97.0215 | 97.5539 | 97.4142 | 96.9598 | 97.1859 | 93.3248 | 95.7344 | 96.7563 | 97.4639 | 97.4153 | 97.0564 | 97.0808 | 92.4192 | 95.0959 | 96.5384 | 97.3538 | 97.3374 | 97.0253 | 96.9205 | 2017-12-15 | 2018-10-15
Enphase Energy Inc. | IQ7-60-x-US [240V] | 240 VA, 240 Vac Utility Interactive Microinverter where x = DC Connector type = 2, 5, or B | 0.24 | 240 | 97 | N | Y |  | 0.025 |  |  | 27 | 32 | 37 | 0.024 | 0.048 | 0.072 | 0.12 | 0.18 | 0.24 | 93.9453 | 96.08 | 96.8145 | 97.4746 | 97.4192 | 97.0288 | 97.1328 | 92.9907 | 95.6588 | 96.5049 | 97.5523 | 97.615 | 97.4087 | 97.1755 | 92.0062 | 95.0264 | 96.2309 | 97.3813 | 97.5438 | 97.4107 | 96.9981 | 2017-12-15 | 2018-10-15
Enphase Energy Inc. | M250-60-2LL-S2x (-ZC) (-NA) [208V] | 240 W, 208 Vac Inverter, where S2x are connector types, ZC is mount, and NA is for North American | 0.24 | 208 | 96 | N | Y |  | 0.04 |  |  | 27 | 32 | 38 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 94.7 | 95.7 | 96.1 | 96.3 | 96 | 95.5 | 96 | 94.7 | 95.7 | 96 | 96.3 | 96.2 | 95.8 | 96.1 | 94.5 | 95.5 | 95.8 | 96.1 | 96.2 | 96 | 96
Enphase Energy Inc. | M250-60-2LL-S2x (-ZC) (-NA) [240V] | 240 W, 240 Vac Inverter, where S2x are connector types, ZC is mount, and NA is for North American | 0.24 | 240 | 96.5 | N | Y |  | 0.05 |  |  | 27 | 32 | 38 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 95.6 | 96 | 96.3 | 96.5 | 96.4 | 96.1 | 96.4 | 95 | 96 | 96.2 | 96.5 | 96.6 | 96.4 | 96.4 | 94.9 | 96 | 96 | 96.4 | 96.5 | 96.5 | 96.4
Enphase Energy Inc. | M250-72-2LL-S2x [208V] | 240 W, 208 Vac Microinverter, where x = 2, 3, 4, or 5 and may be followed by -US | 0.24 | 208 | 96.5 | N | Y |  | 0.04 |  |  | 27 | 37 | 48 | 24 | 48 | 72 | 120 | 180 | 240 | 95.6 | 96.4 | 96.6 | 96.6 | 96.3 | 95.6 | 96.3 | 95.4 | 96.2 | 96.4 | 96.6 | 96.6 | 96.2 | 96.5 | 95.1 | 95.8 | 96 | 96.4 | 96.5 | 96.3 | 96.3
Enphase Energy Inc. | M250-72-2LL-S2x [240V] | 240 W, 240 Vac Microinverter, where x = 2, 3, 4 ,or 5 and may be followed by -US | 0.24 | 240 | 96.5 | N | Y |  | 0.04 |  |  | 27 | 37 | 48 | 24 | 48 | 72 | 120 | 180 | 240 | 95.7 | 96.4 | 96.6 | 96.6 | 96.3 | 95.8 | 96.4 | 95.5 | 96.3 | 96.5 | 96.7 | 96.6 | 96.3 | 96.5 | 95.3 | 96 | 96.2 | 96.5 | 96.5 | 96.4 | 96.4
Enphase Energy Inc. | C250-72-2LN-S2 | 0.247 kW Utility Interactive Microinverter | 0.247 |  | 96.5 | N | Y |  | 0.071 |  |  | 27.5 | 39 | 47.5 | 0.02 | 0.05 | 0.07 | 0.12 | 0.19 | 0.25 | 95.6 | 96.2 | 96.4 | 96.6 | 96.4 | 95.9 | 96.4 | 95.1 | 96.1 | 96.4 | 96.6 | 96.6 | 96.5 | 96.5 | 94.9 | 96 | 96.1 | 96.5 | 96.6 | 96.6 | 96.4
Enphase Energy Inc. | IQ6PLUS-ACB-LL [240V] | 270 VA, 240 Vac Utility Interactive Microinverter | 0.27 | 240 | 95.5 | N | Y |  | 0.07 |  |  | 23 | 25 | 28 | 0.027 | 0.054 | 0.081 | 0.135 | 0.2025 | 0.27 | 85.8903 | 93.6164 | 95.4627 | 95.9769 | 95.5783 | 94.8032 | 95.1238 | 85.8003 | 93.4691 | 95.4058 | 96.1485 | 95.8765 | 95.2295 | 95.3213 | 85.5189 | 93.1183 | 95.1904 | 96.1928 | 96.0669 | 95.5951 | 95.3952 | 2018-05-15 | 2018-10-15
Enphase Energy Inc. | S280-60-LL-x [208V] | 270 W, 208 Vac, Utility Interactive Microinverter, where x = 2, 3, 4 , or 5 and may be followed by -US | 0.27 | 208 | 96.5 | N | Y |  | 0.051 |  |  | 27 | 32 | 37 | 0.03 | 0.05 | 0.08 | 0.14 | 0.2 | 0.27 | 95 | 96.1 | 96.5 | 96.9 | 96.7 | 96.2 | 96.6 | 95 | 96.1 | 96.1 | 96.7 | 96.6 | 96.2 | 96.5 | 94.9 | 95.7 | 95.8 | 96.6 | 96.5 | 96.1 | 96.3 | 2017-10-16 | 2018-10-15
Enphase Energy Inc. | S280-60-LL-x [240V] | 270 W, 240 Vac, Utility Interactive Microinverter, where x = 2, 3, 4, or 5 and may be followed by -US | 0.27 | 240 | 97 | N | Y |  | 0.062 |  |  | 27 | 32 | 37 | 0.03 | 0.05 | 0.08 | 0.14 | 0.2 | 0.27 | 95.2 | 96.5 | 96.9 | 97.3 | 97.3 | 97 | 97.1 | 95.3 | 96.5 | 96.7 | 97.1 | 97.2 | 96.9 | 97 | 95.1 | 96.1 | 96 | 96.9 | 97.1 | 96.9 | 96.8 | 2017-10-16 | 2018-10-15
Enphase Energy Inc. | IQ6PLUS-72-ACM-US [208V] | 280 W, 208 Vac Utility Interactive Microinverter for ACPV Module applications | 0.28 | 208 | 97 | N | Y | This microinverter is sold as an individual unit but is only for ACPV modules including LG Electronics Inc. LGxxxE1K-A5 and LGxxxE1C-A5, where xxx = 315, 320, 325, 330, or 335. | 0.02 |  |  | 27 | 36 | 45 | 0.028 | 0.056 | 0.084 | 0.14 | 0.21 | 0.28 | 94.6361 | 96.3401 | 96.9302 | 97.3761 | 97.1425 | 96.5786 | 96.9975 | 94.5629 | 95.6844 | 96.451 | 97.1497 | 97.092 | 96.6838 | 96.8353 | 93.9289 | 95.0271 | 95.9707 | 96.9185 | 96.9131 | 96.595 | 96.5716 | 2017-08-15 | 2018-10-15
Enphase Energy Inc. | IQ6PLUS-72-ACM-US [240V] | 280 W, 240 Vac Utility Interactive Microinverter for ACPV Module applications | 0.28 | 240 | 97 | N | Y | This microinverter is sold as an individual unit but is only for ACPV modules including LG Electronics Inc. LGxxxE1K-A5 and LGxxxE1C-A5, where xxx = 315, 320, 325, 330, or 335. | 0.02 |  |  | 27 | 36 | 45 | 0.028 | 0.056 | 0.084 | 0.14 | 0.21 | 0.28 | 94.2531 | 96.1631 | 96.8171 | 97.3026 | 97.1456 | 96.7165 | 96.9529 | 94.5548 | 95.7444 | 96.2814 | 97.2549 | 97.3334 | 97.1701 | 96.9919 | 93.9059 | 95.0901 | 95.7449 | 96.972 | 97.1487 | 97.0384 | 96.705 | 2017-08-15 | 2018-10-15
Enphase Energy Inc. | IQ6PLUS-72-x-US [208V] | 280 W, 208 Vac Utility Interactive Microinverter where x = DC Connector type = 2 or 5 | 0.28 | 208 | 97 | N | Y |  | 0.02 |  |  | 27 | 36 | 45 | 0.028 | 0.056 | 0.084 | 0.14 | 0.21 | 0.28 | 94.6361 | 96.3401 | 96.9302 | 97.3761 | 97.1425 | 96.5786 | 96.9975 | 94.5629 | 95.6844 | 96.451 | 97.1497 | 97.092 | 96.6838 | 96.8353 | 93.9289 | 95.0271 | 95.9707 | 96.9185 | 96.9131 | 96.595 | 96.5716 | 2017-08-01 | 2018-10-15
Enphase Energy Inc. | IQ6PLUS-72-x-US [240V] | 280 W, 240 Vac Utility Interactive Microinverter where x = DC Connector type = 2 or 5 | 0.28 | 240 | 97 | N | Y |  | 0.02 |  |  | 27 | 36 | 45 | 0.028 | 0.056 | 0.084 | 0.14 | 0.21 | 0.28 | 94.2531 | 96.1631 | 96.8171 | 97.3026 | 97.1456 | 96.7165 | 96.9529 | 94.5548 | 95.7444 | 96.2814 | 97.2549 | 97.3334 | 97.1701 | 96.9919 | 93.9059 | 95.0901 | 95.7449 | 96.972 | 97.1487 | 97.0384 | 96.705 | 2017-08-01 | 2018-10-15
Enphase Energy Inc. | IQ7PLUS-72-x-ACM-US [208V] | 290 VA, 208 Vac Utility Interactive Microinverter for use in ACPV Module applications where x = DC Connector type = B or blank | 0.29 | 208 | 96.5 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.025 |  |  | 27 | 36 | 45 | 0.029 | 0.058 | 0.087 | 0.145 | 0.2175 | 0.29 | 94.9112 | 96.2467 | 97.1081 | 97.2516 | 96.9257 | 96.2942 | 96.8699 | 93.9563 | 95.3145 | 96.7282 | 97.1587 | 96.9578 | 96.445 | 96.7446 | 93.1479 | 94.59 | 96.3899 | 96.9798 | 96.8592 | 96.3734 | 96.542 | 2017-12-15 | 2018-10-15
Enphase Energy Inc. | IQ7PLUS-72-x-ACM-US [240V] | 290 VA, 240 Vac Utility Interactive Microinverter for use in ACPV Module applications where x = DC Connector type = B or blank | 0.29 | 240 | 97 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.025 |  |  | 27 | 36 | 45 | 0.029 | 0.058 | 0.087 | 0.145 | 0.2175 | 0.29 | 95.0036 | 96.2457 | 97.1477 | 97.4291 | 97.1641 | 96.6039 | 97.0574 | 94.162 | 95.5752 | 96.7802 | 97.4953 | 97.4428 | 97.1569 | 97.1354 | 93.3214 | 94.8059 | 96.394 | 97.2732 | 97.3095 | 97.0757 | 96.8956 | 2017-12-15 | 2018-10-15
Enphase Energy Inc. | IQ7PLUS-72-x-US [208V] | 290 VA, 208 Vac Utility Interactive Microinverter where x = DC Connector type = 2, 5, or B | 0.29 | 208 | 96.5 | N | Y |  | 0.025 |  |  | 27 | 36 | 45 | 0.029 | 0.058 | 0.087 | 0.145 | 0.2175 | 0.29 | 94.9112 | 96.2467 | 97.1081 | 97.2516 | 96.9257 | 96.2942 | 96.8699 | 93.9563 | 95.3145 | 96.7282 | 97.1587 | 96.9578 | 96.445 | 96.7446 | 93.1479 | 94.59 | 96.3899 | 96.9798 | 96.8592 | 96.3734 | 96.542 | 2017-12-15 | 2018-10-15
Enphase Energy Inc. | IQ7PLUS-72-x-US [240V] | 290 VA, 240 Vac Utility Interactive Microinverter where x = DC Connector type = 2, 5, or B | 0.29 | 240 | 97 | N | Y |  | 0.025 |  |  | 27 | 36 | 45 | 0.029 | 0.058 | 0.087 | 0.145 | 0.2175 | 0.29 | 95.0036 | 96.2457 | 97.1477 | 97.4291 | 97.1641 | 96.6039 | 97.0574 | 94.162 | 95.5752 | 96.7802 | 97.4953 | 97.4428 | 97.1569 | 97.1354 | 93.3214 | 94.8059 | 96.394 | 97.2732 | 97.3095 | 97.0757 | 96.8956 | 2017-12-15 | 2018-10-15
Enphase Energy Inc. | IQ7AS-66-ACM-US-x [208V] | 290 W, 208 Vac Utility Interactive Microinverter, where x=blank or NM | 0.29291 | 208 | 96.5 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. |  |  |  | 38 | 40.5 | 43 | 0.029291 | 0.058582 | 0.087873 | 0.14645 | 0.21968 | 0.29291 | 94.5043 | 95.6178 | 96.3794 | 96.9986 | 96.8439 | 96.3109 | 96.6391 | 94.5123 | 95.5365 | 96.2796 | 96.9698 | 96.8365 | 96.3048 | 96.6131 | 94.5015 | 95.5124 | 96.1786 | 96.9216 | 96.8005 | 96.2939 | 96.5696 | 2019-03-15
Enphase Energy Inc. | IQ7X-96-x-ACM-US [208V] | 315 VA, 208 Vac Utility Interactive microinverter for ACPV Module applications where x = DC Connector type = B or blank | 0.315 | 208 | 97 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.021 |  |  | 53 | 60 | 64 | 0.0315 | 0.063 | 0.0945 | 0.1575 | 0.23625 | 0.315 | 90.4836 | 96.6628 | 97.0999 | 97.6357 | 97.5242 | 97.1035 | 97.151 | 95.4142 | 96.4654 | 96.9008 | 97.542 | 97.4613 | 97.05 | 97.2587 | 95.2705 | 96.3335 | 96.8135 | 97.5025 | 97.4299 | 97.0197 | 97.2095 | 2018-06-01 | 2018-10-15
Enphase Energy Inc. | IQ7X-96-x-ACM-US [240V] | 315 VA, 240 Vac Utility Interactive microinverter for ACPV Module applications where x = DC Connector type = B or blank | 0.315 | 240 | 97.5 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.021 |  |  | 53 | 60 | 64 | 0.0315 | 0.063 | 0.0945 | 0.1575 | 0.23625 | 0.315 | 95.7348 | 96.8402 | 96.9962 | 97.7627 | 97.7558 | 97.4686 | 97.5251 | 95.6103 | 96.6782 | 96.7549 | 97.6667 | 97.7392 | 97.5137 | 97.4564 | 95.4365 | 96.4979 | 96.6571 | 97.6038 | 97.7001 | 97.4825 | 97.3932 | 2018-06-01 | 2018-10-15
Enphase Energy Inc. | IQ7X-96-x-US [208V] | 315 VA, 208 Vac Utility Interactive Microinverter where x = DC Connector type = 2, 5, or B | 0.315 | 208 | 97 | N | Y |  | 0.021 |  |  | 53 | 60 | 64 | 0.0315 | 0.063 | 0.0945 | 0.1575 | 0.23625 | 0.315 | 90.4836 | 96.6628 | 97.0999 | 97.6357 | 97.5242 | 97.1035 | 97.151 | 95.4142 | 96.4654 | 96.9008 | 97.542 | 97.4613 | 97.05 | 97.2587 | 95.2705 | 96.3335 | 96.8135 | 97.5025 | 97.4299 | 97.0197 | 97.2095 | 2018-06-01 | 2018-10-15
Enphase Energy Inc. | IQ7X-96-x-US [240V] | 315 VA, 240 Vac Utility Interactive Microinverter where x = DC Connector type = 2, 5, or B | 0.315 | 240 | 97.5 | N | Y |  | 0.021 |  |  | 53 | 60 | 64 | 0.0315 | 0.063 | 0.0945 | 0.1575 | 0.23625 | 0.315 | 95.7348 | 96.8402 | 96.9962 | 97.7627 | 97.7558 | 97.4686 | 97.5251 | 95.6103 | 96.6782 | 96.7549 | 97.6667 | 97.7392 | 97.5137 | 97.4564 | 95.4365 | 96.4979 | 96.6571 | 97.6038 | 97.7001 | 97.4825 | 97.3932 | 2018-06-01 | 2018-10-15
Enphase Energy Inc. | IQ7XS-96-y-ACM-z [208V] | 315 VA, 208 Vac Utility Interactive microinverter for ACPV Module applications, where y = DC Connector type = B or blank, and z = US or blank | 0.315 | 208 | 97 | N | Y | This component is specific to SunPower ACPV modules and is not available as an individual unit. | 0.021 |  |  | 53 | 60 | 64 | 0.0315 | 0.063 | 0.0945 | 0.1575 | 0.23625 | 0.315 | 90.4836 | 96.6628 | 97.0999 | 97.6357 | 97.5242 | 97.1035 | 97.151 | 95.4142 | 96.4654 | 96.9008 | 97.542 | 97.4613 | 97.05 | 97.2587 | 95.2705 | 96.3335 | 96.8135 | 97.5025 | 97.4299 | 97.0197 | 97.2095 | 2018-10-01 | 2018-10-15
Enphase Energy Inc. | IQ7XS-96-y-ACM-z [240V] | 315 VA, 240 Vac Utility Interactive microinverter for ACPV Module applications, where y = DC Connector type = B or blank, and z = US or blank | 0.315 | 240 | 97.5 | N | Y | This component is specific to SunPower ACPV modules and is not available as an individual unit. | 0.021 |  |  | 53 | 60 | 64 | 0.0315 | 0.063 | 0.0945 | 0.1575 | 0.23625 | 0.315 | 95.7348 | 96.8402 | 96.9962 | 97.7627 | 97.7558 | 97.4686 | 97.5251 | 95.6103 | 96.6782 | 96.7549 | 97.6667 | 97.7392 | 97.5137 | 97.4564 | 95.4365 | 96.4979 | 96.6571 | 97.6038 | 97.7001 | 97.4825 | 97.3932 | 2018-10-01 | 2018-10-15
Enphase Energy Inc. | IQ7AS-66-ACM-US-x [240V] | 349 W, 240 Vac Utility Interactive Microinverter, where x=blank or NM | 0.349 | 240 | 97 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. |  |  |  | 38 | 40.5 | 43 | 0.03487 | 0.06974 | 0.10461 | 0.17435 | 0.26152 | 0.3487 | 95.1546 | 95.8056 | 96.6492 | 97.1481 | 96.9702 | 96.471 | 96.8132 | 95.0678 | 95.7094 | 96.5708 | 97.1127 | 96.977 | 96.4639 | 96.7913 | 95.0012 | 95.633 | 96.4691 | 97.072 | 96.9595 | 96.4604 | 96.7547 | 2019-03-15
Enphase Energy Inc. | D380-72-208-S1x [208V] | 380 W, 208 Vac, Utility Interactive modular Inverter, 1x = connector types | 0.38 | 208 | 95 | N | Y |  | 0.5 | 0.38 | 0.5 | 22 | 32 | 40 | 0.038 | 0.076 | 0.114 | 0.19 | 0.285 | 0.38 | 93.7 | 94.9 | 95.2 | 95.2 | 94.7 | 93.6 | 94.8 | 93.6 | 95 | 95.1 | 95.6 | 95.4 | 94.9 | 95.3 | 93.5 | 94.7 | 95.1 | 95.4 | 95.5 | 95.3 | 95.3
Enphase Energy Inc. | D380-72-240-S1x [240V] | 380 W, 240 Vac, Utility Interactive modular Inverter, 1x are connector types | 0.38 | 240 | 95 | N | Y |  | 0.5 | 0.38 | 0.5 | 22 | 32 | 40 | 0.038 | 0.076 | 0.114 | 0.19 | 0.285 | 0.38 | 93.8 | 94.9 | 95.1 | 95.3 | 94.8 | 93.8 | 94.9 | 93.7 | 94.9 | 95.2 | 95.6 | 95.5 | 95.1 | 95.3 | 93.7 | 94.9 | 95 | 95.4 | 95.6 | 95.4 | 95.4
Enphase Energy Inc. | D380-72-2LL-S1x [208V] | 380 W, 208 Vac Inverter, x = connector types, -NA if North American | 0.38 | 208 | 95 | N | Y |  | 0.05 | 0.38 | 0.05 | 22 | 32 | 40 | 0.038 | 0.076 | 0.114 | 0.19 | 0.285 | 0.38 | 93.71 | 94.91 | 95.17 | 95.18 | 94.7 | 93.58 | 94.77 | 93.65 | 95.03 | 95.13 | 95.55 | 95.37 | 94.93 | 95.27 | 93.45 | 94.74 | 95.07 | 95.39 | 95.54 | 95.29 | 95.31
Enphase Energy Inc. | D380-72-2LL-S1x [240V] | 380 W, 240 Vac Inverter, x = connector types, -NA if North American | 0.38 | 240 | 95 | N | Y |  | 0.05 | 0.38 | 0.05 | 22 | 32 | 40 | 0.038 | 0.076 | 0.114 | 0.19 | 0.285 | 0.38 | 93.71 | 94.91 | 95.17 | 95.18 | 94.7 | 93.58 | 94.77 | 93.65 | 95.03 | 95.13 | 95.55 | 95.37 | 94.93 | 95.27 | 93.45 | 94.74 | 95.07 | 95.39 | 95.54 | 95.29 | 95.31
Enphase Energy Inc. | D380-72-2LL-S1x-NA [208V] | 380 W, 208 Vac Inverter, x = connector types, -NA if North American | 0.38 | 208 | 95 | N | Y |  | 0.05 | 0.38 | 0.05 | 22 | 32 | 40 | 0.038 | 0.076 | 0.114 | 0.19 | 0.285 | 0.38 | 93.71 | 94.91 | 95.17 | 95.18 | 94.7 | 93.58 | 94.77 | 93.65 | 95.03 | 95.13 | 95.55 | 95.37 | 94.93 | 95.27 | 93.45 | 94.74 | 95.07 | 95.39 | 95.54 | 95.29 | 95.31
Enphase Energy Inc. | D380-72-2LL-S1x-NA [240V] | 380 W, 208 Vac Inverter, x = connector types, -NA if North American | 0.38 | 240 | 95 | N | Y
Eoplly New Energy Technology | EP156M/60-230S AC [208V] | 215 W, 208 Vac Inverter | 0.215 | 208 | 96 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.04 |  |  | 22 | 29 | 36 | 0.02 | 0.04 | 0.06 | 0.11 | 0.16 | 0.22 | 94.5 | 95.5 | 95.9 | 96 | 95.5 | 94.7 | 95.6 | 94.5 | 95.5 | 95.9 | 96.1 | 96 | 95.5 | 95.9 | 94.4 | 95.4 | 95.7 | 96.1 | 96.1 | 95.8 | 95.9
Eoplly New Energy Technology | EP156M/60-230S AC [240V] | 215 W, 240 Vac Inverter | 0.215 | 240 | 96 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.04 |  |  | 22 | 29 | 36 | 0.02 | 0.04 | 0.06 | 0.11 | 0.16 | 0.22 | 94.5 | 95.5 | 95.9 | 96 | 95.5 | 94.7 | 95.6 | 94.5 | 95.5 | 95.9 | 96.1 | 96 | 95.5 | 95.9 | 94.4 | 95.4 | 95.7 | 96.1 | 96.1 | 95.8 | 95.9
Eoplly New Energy Technology | EP156M/60-235S AC [208V] | 215 W, 208 Vac Inverter | 0.215 | 208 | 96 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.04 |  |  | 22 | 29 | 36 | 0.02 | 0.04 | 0.06 | 0.11 | 0.16 | 0.22 | 94.5 | 95.5 | 95.9 | 96 | 95.5 | 94.7 | 95.6 | 94.5 | 95.5 | 95.9 | 96.1 | 96 | 95.5 | 95.9 | 94.4 | 95.4 | 95.7 | 96.1 | 96.1 | 95.8 | 95.9
Eoplly New Energy Technology | EP156M/60-235S AC [240V] | 215 W, 240 Vac Inverter | 0.215 | 240 | 96 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.04 |  |  | 22 | 29 | 36 | 0.02 | 0.04 | 0.06 | 0.11 | 0.16 | 0.22 | 94.5 | 95.5 | 95.9 | 96 | 95.5 | 94.7 | 95.6 | 94.5 | 95.5 | 95.9 | 96.1 | 96 | 95.5 | 95.9 | 94.4 | 95.4 | 95.7 | 96.1 | 96.1 | 95.8 | 95.9
Eoplly New Energy Technology | EP156M/60-240S AC [208V] | 215 W, 208 Vac Inverter | 0.215 | 208 | 96 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.04 |  |  | 22 | 29 | 36 | 0.02 | 0.04 | 0.06 | 0.11 | 0.16 | 0.22 | 94.5 | 95.5 | 95.9 | 96 | 95.5 | 94.7 | 95.6 | 94.5 | 95.5 | 95.9 | 96.1 | 96 | 95.5 | 95.9 | 94.4 | 95.4 | 95.7 | 96.1 | 96.1 | 95.8 | 95.9
Eoplly New Energy Technology | EP156M/60-240S AC [240V] | 215 W, 240 Vac Inverter | 0.215 | 240 | 96 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.04 |  |  | 22 | 29 | 36 | 0.02 | 0.04 | 0.06 | 0.11 | 0.16 | 0.22 | 94.5 | 95.5 | 95.9 | 96 | 95.5 | 94.7 | 95.6 | 94.5 | 95.5 | 95.9 | 96.1 | 96 | 95.5 | 95.9 | 94.4 | 95.4 | 95.7 | 96.1 | 96.1 | 95.8 | 95.9
Eoplly New Energy Technology | EP156M/60-245S AC [208V] | 215 W, 208 Vac Inverter | 0.215 | 208 | 96 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.04 |  |  | 22 | 29 | 36 | 0.02 | 0.04 | 0.06 | 0.11 | 0.16 | 0.22 | 94.5 | 95.5 | 95.9 | 96 | 95.5 | 94.7 | 95.6 | 94.5 | 95.5 | 95.9 | 96.1 | 96 | 95.5 | 95.9 | 94.4 | 95.4 | 95.7 | 96.1 | 96.1 | 95.8 | 95.9
Eoplly New Energy Technology | EP156M/60-245S AC [240V] | 215 W, 240 Vac Inverter | 0.215 | 240 | 96 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.04 |  |  | 22 | 29 | 36 | 0.02 | 0.04 | 0.06 | 0.11 | 0.16 | 0.22 | 94.5 | 95.5 | 95.9 | 96 | 95.5 | 94.7 | 95.6 | 94.5 | 95.5 | 95.9 | 96.1 | 96 | 95.5 | 95.9 | 94.4 | 95.4 | 95.7 | 96.1 | 96.1 | 95.8 | 95.9
Eoplly New Energy Technology | EP156M/60-250S AC [208V] | 215 W, 208 Vac Inverter | 0.215 | 208 | 96 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.04 |  |  | 22 | 29 | 36 | 0.02 | 0.04 | 0.06 | 0.11 | 0.16 | 0.22 | 94.5 | 95.5 | 95.9 | 96 | 95.5 | 94.7 | 95.6 | 94.5 | 95.5 | 95.9 | 96.1 | 96 | 95.5 | 95.9 | 94.4 | 95.4 | 95.7 | 96.1 | 96.1 | 95.8 | 95.9
Eoplly New Energy Technology | EP156M/60-250S AC [240V] | 215 W, 240 Vac Inverter | 0.215 | 240 | 96 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.04 |  |  | 22 | 29 | 36 | 0.02 | 0.04 | 0.06 | 0.11 | 0.16 | 0.22 | 94.5 | 95.5 | 95.9 | 96 | 95.5 | 94.7 | 95.6 | 94.5 | 95.5 | 95.9 | 96.1 | 96 | 95.5 | 95.9 | 94.4 | 95.4 | 95.7 | 96.1 | 96.1 | 95.8 | 95.9
Eoplly New Energy Technology | EP156M/60-255S AC [208V] | 215 W, 208 Vac Inverter | 0.215 | 208 | 96 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.04 |  |  | 22 | 29 | 36 | 0.02 | 0.04 | 0.06 | 0.11 | 0.16 | 0.22 | 94.5 | 95.5 | 95.9 | 96 | 95.5 | 94.7 | 95.6 | 94.5 | 95.5 | 95.9 | 96.1 | 96 | 95.5 | 95.9 | 94.4 | 95.4 | 95.7 | 96.1 | 96.1 | 95.8 | 95.9
Eoplly New Energy Technology | EP156M/60-255S AC [240V] | 215 W, 240 Vac Inverter | 0.215 | 240 | 96 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.04 |  |  | 22 | 29 | 36 | 0.02 | 0.04 | 0.06 | 0.11 | 0.16 | 0.22 | 94.5 | 95.5 | 95.9 | 96 | 95.5 | 94.7 | 95.6 | 94.5 | 95.5 | 95.9 | 96.1 | 96 | 95.5 | 95.9 | 94.4 | 95.4 | 95.7 | 96.1 | 96.1 | 95.8 | 95.9
Eoplly New Energy Technology | EP156M/60-260S AC [208V] | 215 W, 208 Vac Inverter | 0.215 | 208 | 96 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.04 |  |  | 22 | 29 | 36 | 0.02 | 0.04 | 0.06 | 0.11 | 0.16 | 0.22 | 94.5 | 95.5 | 95.9 | 96 | 95.5 | 94.7 | 95.6 | 94.5 | 95.5 | 95.9 | 96.1 | 96 | 95.5 | 95.9 | 94.4 | 95.4 | 95.7 | 96.1 | 96.1 | 95.8 | 95.9
Eoplly New Energy Technology | EP156M/60-260S AC [240V] | 215 W, 240 Vac Inverter | 0.215 | 240 | 96 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.04 |  |  | 22 | 29 | 36 | 0.02 | 0.04 | 0.06 | 0.11 | 0.16 | 0.22 | 94.5 | 95.5 | 95.9 | 96 | 95.5 | 94.7 | 95.6 | 94.5 | 95.5 | 95.9 | 96.1 | 96 | 95.5 | 95.9 | 94.4 | 95.4 | 95.7 | 96.1 | 96.1 | 95.8 | 95.9
Eoplly New Energy Technology | EP156MB/60-230S AC [208V] | 215 W, 208 Vac Inverter | 0.215 | 208 | 96 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.04 |  |  | 22 | 29 | 36 | 0.02 | 0.04 | 0.06 | 0.11 | 0.16 | 0.22 | 94.5 | 95.5 | 95.9 | 96 | 95.5 | 94.7 | 95.6 | 94.5 | 95.5 | 95.9 | 96.1 | 96 | 95.5 | 95.9 | 94.4 | 95.4 | 95.7 | 96.1 | 96.1 | 95.8 | 95.9
Eoplly New Energy Technology | EP156MB/60-230S AC [240V] | 215 W, 240 Vac Inverter | 0.215 | 240 | 96 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.04 |  |  | 22 | 29 | 36 | 0.02 | 0.04 | 0.06 | 0.11 | 0.16 | 0.22 | 94.5 | 95.5 | 95.9 | 96 | 95.5 | 94.7 | 95.6 | 94.5 | 95.5 | 95.9 | 96.1 | 96 | 95.5 | 95.9 | 94.4 | 95.4 | 95.7 | 96.1 | 96.1 | 95.8 | 95.9
Eoplly New Energy Technology | EP156MB/60-235S AC [208V] | 215 W, 208 Vac Inverter | 0.215 | 208 | 96 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.04 |  |  | 22 | 29 | 36 | 0.02 | 0.04 | 0.06 | 0.11 | 0.16 | 0.22 | 94.5 | 95.5 | 95.9 | 96 | 95.5 | 94.7 | 95.6 | 94.5 | 95.5 | 95.9 | 96.1 | 96 | 95.5 | 95.9 | 94.4 | 95.4 | 95.7 | 96.1 | 96.1 | 95.8 | 95.9
Eoplly New Energy Technology | EP156MB/60-235S AC [240V] | 215 W, 240 Vac Inverter | 0.215 | 240 | 96 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.04 |  |  | 22 | 29 | 36 | 0.02 | 0.04 | 0.06 | 0.11 | 0.16 | 0.22 | 94.5 | 95.5 | 95.9 | 96 | 95.5 | 94.7 | 95.6 | 94.5 | 95.5 | 95.9 | 96.1 | 96 | 95.5 | 95.9 | 94.4 | 95.4 | 95.7 | 96.1 | 96.1 | 95.8 | 95.9
Eoplly New Energy Technology | EP156MB/60-240S AC [208V] | 215 W, 208 Vac Inverter | 0.215 | 208 | 96 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.04 |  |  | 22 | 29 | 36 | 0.02 | 0.04 | 0.06 | 0.11 | 0.16 | 0.22 | 94.5 | 95.5 | 95.9 | 96 | 95.5 | 94.7 | 95.6 | 94.5 | 95.5 | 95.9 | 96.1 | 96 | 95.5 | 95.9 | 94.4 | 95.4 | 95.7 | 96.1 | 96.1 | 95.8 | 95.9
Eoplly New Energy Technology | EP156MB/60-240S AC [240V] | 215 W, 240 Vac Inverter | 0.215 | 240 | 96 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.04 |  |  | 22 | 29 | 36 | 0.02 | 0.04 | 0.06 | 0.11 | 0.16 | 0.22 | 94.5 | 95.5 | 95.9 | 96 | 95.5 | 94.7 | 95.6 | 94.5 | 95.5 | 95.9 | 96.1 | 96 | 95.5 | 95.9 | 94.4 | 95.4 | 95.7 | 96.1 | 96.1 | 95.8 | 95.9
Eoplly New Energy Technology | EP156MB/60-245S AC [208V] | 215 W, 208 Vac Inverter | 0.215 | 208 | 96 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.04 |  |  | 22 | 29 | 36 | 0.02 | 0.04 | 0.06 | 0.11 | 0.16 | 0.22 | 94.5 | 95.5 | 95.9 | 96 | 95.5 | 94.7 | 95.6 | 94.5 | 95.5 | 95.9 | 96.1 | 96 | 95.5 | 95.9 | 94.4 | 95.4 | 95.7 | 96.1 | 96.1 | 95.8 | 95.9
Eoplly New Energy Technology | EP156MB/60-245S AC [240V] | 215 W, 240 Vac Inverter | 0.215 | 240 | 96 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.04 |  |  | 22 | 29 | 36 | 0.02 | 0.04 | 0.06 | 0.11 | 0.16 | 0.22 | 94.5 | 95.5 | 95.9 | 96 | 95.5 | 94.7 | 95.6 | 94.5 | 95.5 | 95.9 | 96.1 | 96 | 95.5 | 95.9 | 94.4 | 95.4 | 95.7 | 96.1 | 96.1 | 95.8 | 95.9
Eoplly New Energy Technology | EP156MB/60-250S AC [208V] | 215 W, 208 Vac Inverter | 0.215 | 208 | 96 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.04 |  |  | 22 | 29 | 36 | 0.02 | 0.04 | 0.06 | 0.11 | 0.16 | 0.22 | 94.5 | 95.5 | 95.9 | 96 | 95.5 | 94.7 | 95.6 | 94.5 | 95.5 | 95.9 | 96.1 | 96 | 95.5 | 95.9 | 94.4 | 95.4 | 95.7 | 96.1 | 96.1 | 95.8 | 95.9
Eoplly New Energy Technology | EP156MB/60-250S AC [240V] | 215 W, 240 Vac Inverter | 0.215 | 240 | 96 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.04 |  |  | 22 | 29 | 36 | 0.02 | 0.04 | 0.06 | 0.11 | 0.16 | 0.22 | 94.5 | 95.5 | 95.9 | 96 | 95.5 | 94.7 | 95.6 | 94.5 | 95.5 | 95.9 | 96.1 | 96 | 95.5 | 95.9 | 94.4 | 95.4 | 95.7 | 96.1 | 96.1 | 95.8 | 95.9
Eoplly New Energy Technology | EP156P/60-225S AC [208V] | 215 W, 208 Vac Inverter | 0.215 | 208 | 96 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.04 |  |  | 22 | 29 | 36 | 0.02 | 0.04 | 0.06 | 0.11 | 0.16 | 0.22 | 94.5 | 95.5 | 95.9 | 96 | 95.5 | 94.7 | 95.6 | 94.5 | 95.5 | 95.9 | 96.1 | 96 | 95.5 | 95.9 | 94.4 | 95.4 | 95.7 | 96.1 | 96.1 | 95.8 | 95.9
Eoplly New Energy Technology | EP156P/60-225S AC [240V] | 215 W, 240 Vac Inverter | 0.215 | 240 | 96 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.04 |  |  | 22 | 29 | 36 | 0.02 | 0.04 | 0.06 | 0.11 | 0.16 | 0.22 | 94.5 | 95.5 | 95.9 | 96 | 95.5 | 94.7 | 95.6 | 94.5 | 95.5 | 95.9 | 96.1 | 96 | 95.5 | 95.9 | 94.4 | 95.4 | 95.7 | 96.1 | 96.1 | 95.8 | 95.9
Eoplly New Energy Technology | EP156P/60-230S AC [208V] | 215 W, 208 Vac Inverter | 0.215 | 208 | 96 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.04 |  |  | 22 | 29 | 36 | 0.02 | 0.04 | 0.06 | 0.11 | 0.16 | 0.22 | 94.5 | 95.5 | 95.9 | 96 | 95.5 | 94.7 | 95.6 | 94.5 | 95.5 | 95.9 | 96.1 | 96 | 95.5 | 95.9 | 94.4 | 95.4 | 95.7 | 96.1 | 96.1 | 95.8 | 95.9
Eoplly New Energy Technology | EP156P/60-230S AC [240V] | 215 W, 240 Vac Inverter | 0.215 | 240 | 96 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.04 |  |  | 22 | 29 | 36 | 0.02 | 0.04 | 0.06 | 0.11 | 0.16 | 0.22 | 94.5 | 95.5 | 95.9 | 96 | 95.5 | 94.7 | 95.6 | 94.5 | 95.5 | 95.9 | 96.1 | 96 | 95.5 | 95.9 | 94.4 | 95.4 | 95.7 | 96.1 | 96.1 | 95.8 | 95.9
Eoplly New Energy Technology | EP156P/60-235S AC [208V] | 215 W, 208 Vac Inverter | 0.215 | 208 | 96 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.04 |  |  | 22 | 29 | 36 | 0.02 | 0.04 | 0.06 | 0.11 | 0.16 | 0.22 | 94.5 | 95.5 | 95.9 | 96 | 95.5 | 94.7 | 95.6 | 94.5 | 95.5 | 95.9 | 96.1 | 96 | 95.5 | 95.9 | 94.4 | 95.4 | 95.7 | 96.1 | 96.1 | 95.8 | 95.9
Eoplly New Energy Technology | EP156P/60-235S AC [240V] | 215 W, 240 Vac Inverter | 0.215 | 240 | 96 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.04 |  |  | 22 | 29 | 36 | 0.02 | 0.04 | 0.06 | 0.11 | 0.16 | 0.22 | 94.5 | 95.5 | 95.9 | 96 | 95.5 | 94.7 | 95.6 | 94.5 | 95.5 | 95.9 | 96.1 | 96 | 95.5 | 95.9 | 94.4 | 95.4 | 95.7 | 96.1 | 96.1 | 95.8 | 95.9
Eoplly New Energy Technology | EP156P/60-240S AC [208V] | 215 W, 208 Vac Inverter | 0.215 | 208 | 96 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.04 |  |  | 22 | 29 | 36 | 0.02 | 0.04 | 0.06 | 0.11 | 0.16 | 0.22 | 94.5 | 95.5 | 95.9 | 96 | 95.5 | 94.7 | 95.6 | 94.5 | 95.5 | 95.9 | 96.1 | 96 | 95.5 | 95.9 | 94.4 | 95.4 | 95.7 | 96.1 | 96.1 | 95.8 | 95.9
Eoplly New Energy Technology | EP156P/60-240S AC [240V] | 215 W, 240 Vac Inverter | 0.215 | 240 | 96 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.04 |  |  | 22 | 29 | 36 | 0.02 | 0.04 | 0.06 | 0.11 | 0.16 | 0.22 | 94.5 | 95.5 | 95.9 | 96 | 95.5 | 94.7 | 95.6 | 94.5 | 95.5 | 95.9 | 96.1 | 96 | 95.5 | 95.9 | 94.4 | 95.4 | 95.7 | 96.1 | 96.1 | 95.8 | 95.9
Eoplly New Energy Technology | EP156P/60-245S AC [208V] | 215 W, 208 Vac Inverter | 0.215 | 208 | 96 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.04 |  |  | 22 | 29 | 36 | 0.02 | 0.04 | 0.06 | 0.11 | 0.16 | 0.22 | 94.5 | 95.5 | 95.9 | 96 | 95.5 | 94.7 | 95.6 | 94.5 | 95.5 | 95.9 | 96.1 | 96 | 95.5 | 95.9 | 94.4 | 95.4 | 95.7 | 96.1 | 96.1 | 95.8 | 95.9
Eoplly New Energy Technology | EP156P/60-245S AC [240V] | 215 W, 240 Vac Inverter | 0.215 | 240 | 96 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.04 |  |  | 22 | 29 | 36 | 0.02 | 0.04 | 0.06 | 0.11 | 0.16 | 0.22 | 94.5 | 95.5 | 95.9 | 96 | 95.5 | 94.7 | 95.6 | 94.5 | 95.5 | 95.9 | 96.1 | 96 | 95.5 | 95.9 | 94.4 | 95.4 | 95.7 | 96.1 | 96.1 | 95.8 | 95.9
Eoplly New Energy Technology | EP156P/60-250S AC [208V] | 215 W, 208 Vac Inverter | 0.215 | 208 | 96 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.04 |  |  | 22 | 29 | 36 | 0.02 | 0.04 | 0.06 | 0.11 | 0.16 | 0.22 | 94.5 | 95.5 | 95.9 | 96 | 95.5 | 94.7 | 95.6 | 94.5 | 95.5 | 95.9 | 96.1 | 96 | 95.5 | 95.9 | 94.4 | 95.4 | 95.7 | 96.1 | 96.1 | 95.8 | 95.9
Eoplly New Energy Technology | EP156P/60-250S AC [240V] | 215 W, 240 Vac Inverter | 0.215 | 240 | 96 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.04 |  |  | 22 | 29 | 36 | 0.02 | 0.04 | 0.06 | 0.11 | 0.16 | 0.22 | 94.5 | 95.5 | 95.9 | 96 | 95.5 | 94.7 | 95.6 | 94.5 | 95.5 | 95.9 | 96.1 | 96 | 95.5 | 95.9 | 94.4 | 95.4 | 95.7 | 96.1 | 96.1 | 95.8 | 95.9
Eoplly New Energy Technology | EP156P/60-255S AC [208V] | 215 W, 208 Vac Inverter | 0.215 | 208 | 96 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.04 |  |  | 22 | 29 | 36 | 0.02 | 0.04 | 0.06 | 0.11 | 0.16 | 0.22 | 94.5 | 95.5 | 95.9 | 96 | 95.5 | 94.7 | 95.6 | 94.5 | 95.5 | 95.9 | 96.1 | 96 | 95.5 | 95.9 | 94.4 | 95.4 | 95.7 | 96.1 | 96.1 | 95.8 | 95.9
Eoplly New Energy Technology | EP156P/60-255S AC [240V] | 215 W, 240 Vac Inverter | 0.215 | 240 | 96 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.04 |  |  | 22 | 29 | 36 | 0.02 | 0.04 | 0.06 | 0.11 | 0.16 | 0.22 | 94.5 | 95.5 | 95.9 | 96 | 95.5 | 94.7 | 95.6 | 94.5 | 95.5 | 95.9 | 96.1 | 96 | 95.5 | 95.9 | 94.4 | 95.4 | 95.7 | 96.1 | 96.1 | 95.8 | 95.9
Eoplly New Energy Technology | EP156P/60-260S AC [208V] | 215 W, 208 Vac Inverter | 0.215 | 208 | 96 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.04 |  |  | 22 | 29 | 36 | 0.02 | 0.04 | 0.06 | 0.11 | 0.16 | 0.22 | 94.5 | 95.5 | 95.9 | 96 | 95.5 | 94.7 | 95.6 | 94.5 | 95.5 | 95.9 | 96.1 | 96 | 95.5 | 95.9 | 94.4 | 95.4 | 95.7 | 96.1 | 96.1 | 95.8 | 95.9
Eoplly New Energy Technology | EP156P/60-260S AC [240V] | 215 W, 240 Vac Inverter | 0.215 | 240 | 96 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.04 |  |  | 22 | 29 | 36 | 0.02 | 0.04 | 0.06 | 0.11 | 0.16 | 0.22 | 94.5 | 95.5 | 95.9 | 96 | 95.5 | 94.7 | 95.6 | 94.5 | 95.5 | 95.9 | 96.1 | 96 | 95.5 | 95.9 | 94.4 | 95.4 | 95.7 | 96.1 | 96.1 | 95.8 | 95.9
Eoplly New Energy Technology | EP156M/60-250 AC [208V] | 240 W, 208 Vac Inverter | 0.24 | 208 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 88.7 | 93.7 | 94 | 94.9 | 95 | 94.7 | 94.5 | 87.7 | 93.5 | 94.8 | 95.1 | 95.5 | 95.5 | 94.9 | 86.9 | 93.2 | 94.6 | 95.1 | 95.7 | 95.7 | 94.9
Eoplly New Energy Technology | EP156M/60-250 AC [240V] | 240 W, 240 Vac Inverter | 0.24 | 240 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 88.7 | 93.7 | 94 | 94.9 | 95 | 94.7 | 94.5 | 87.7 | 93.5 | 94.8 | 95.1 | 95.5 | 95.5 | 94.9 | 86.9 | 93.2 | 94.6 | 95.1 | 95.7 | 95.7 | 94.9
Eoplly New Energy Technology | EP156M/60-255 AC [208V] | 240 W, 208 Vac Inverter | 0.24 | 208 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 88.7 | 93.7 | 94 | 94.9 | 95 | 94.7 | 94.5 | 87.7 | 93.5 | 94.8 | 95.1 | 95.5 | 95.5 | 94.9 | 86.9 | 93.2 | 94.6 | 95.1 | 95.7 | 95.7 | 94.9
Eoplly New Energy Technology | EP156M/60-255 AC [240V] | 240 W, 240 Vac Inverter | 0.24 | 240 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 88.7 | 93.7 | 94 | 94.9 | 95 | 94.7 | 94.5 | 87.7 | 93.5 | 94.8 | 95.1 | 95.5 | 95.5 | 94.9 | 86.9 | 93.2 | 94.6 | 95.1 | 95.7 | 95.7 | 94.9
Eoplly New Energy Technology | EP156M/60-260 AC [208V] | 240 W, 208 Vac Inverter | 0.24 | 208 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 88.7 | 93.7 | 94 | 94.9 | 95 | 94.7 | 94.5 | 87.7 | 93.5 | 94.8 | 95.1 | 95.5 | 95.5 | 94.9 | 86.9 | 93.2 | 94.6 | 95.1 | 95.7 | 95.7 | 94.9
Eoplly New Energy Technology | EP156M/60-260 AC [240V] | 240 W, 240 Vac Inverter | 0.24 | 240 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 88.7 | 93.7 | 94 | 94.9 | 95 | 94.7 | 94.5 | 87.7 | 93.5 | 94.8 | 95.1 | 95.5 | 95.5 | 94.9 | 86.9 | 93.2 | 94.6 | 95.1 | 95.7 | 95.7 | 94.9
Eoplly New Energy Technology | EP156MB/60-240 AC [208V] | 240 W, 208 Vac Inverter | 0.24 | 208 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 88.7 | 93.7 | 94 | 94.9 | 95 | 94.7 | 94.5 | 87.7 | 93.5 | 94.8 | 95.1 | 95.5 | 95.5 | 94.9 | 86.9 | 93.2 | 94.6 | 95.1 | 95.7 | 95.7 | 94.9
Eoplly New Energy Technology | EP156MB/60-240 AC [240V] | 240 W, 240 Vac Inverter | 0.24 | 240 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 88.7 | 93.7 | 94 | 94.9 | 95 | 94.7 | 94.5 | 87.7 | 93.5 | 94.8 | 95.1 | 95.5 | 95.5 | 94.9 | 86.9 | 93.2 | 94.6 | 95.1 | 95.7 | 95.7 | 94.9
Eoplly New Energy Technology | EP156MB/60-245 AC [208V] | 240 W, 208 Vac Inverter | 0.24 | 208 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 88.7 | 93.7 | 94 | 94.9 | 95 | 94.7 | 94.5 | 87.7 | 93.5 | 94.8 | 95.1 | 95.5 | 95.5 | 94.9 | 86.9 | 93.2 | 94.6 | 95.1 | 95.7 | 95.7 | 94.9
Eoplly New Energy Technology | EP156MB/60-245 AC [240V] | 240 W, 240 Vac Inverter | 0.24 | 240 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 88.7 | 93.7 | 94 | 94.9 | 95 | 94.7 | 94.5 | 87.7 | 93.5 | 94.8 | 95.1 | 95.5 | 95.5 | 94.9 | 86.9 | 93.2 | 94.6 | 95.1 | 95.7 | 95.7 | 94.9
Eoplly New Energy Technology | EP156P/60-240 AC [208V] | 240 W, 208 Vac Inverter | 0.24 | 208 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 88.7 | 93.7 | 94 | 94.9 | 95 | 94.7 | 94.5 | 87.7 | 93.5 | 94.8 | 95.1 | 95.5 | 95.5 | 94.9 | 86.9 | 93.2 | 94.6 | 95.1 | 95.7 | 95.7 | 94.9
Eoplly New Energy Technology | EP156P/60-240 AC [240V] | 240 W, 240 Vac Inverter | 0.24 | 240 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 88.7 | 93.7 | 94 | 94.9 | 95 | 94.7 | 94.5 | 87.7 | 93.5 | 94.8 | 95.1 | 95.5 | 95.5 | 94.9 | 86.9 | 93.2 | 94.6 | 95.1 | 95.7 | 95.7 | 94.9
Eoplly New Energy Technology | EP156P/60-245 AC [208V] | 240 W, 208 Vac Inverter | 0.24 | 208 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 88.7 | 93.7 | 94 | 94.9 | 95 | 94.7 | 94.5 | 87.7 | 93.5 | 94.8 | 95.1 | 95.5 | 95.5 | 94.9 | 86.9 | 93.2 | 94.6 | 95.1 | 95.7 | 95.7 | 94.9
Eoplly New Energy Technology | EP156P/60-245 AC [240V] | 240 W, 240 Vac Inverter | 0.24 | 240 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 88.7 | 93.7 | 94 | 94.9 | 95 | 94.7 | 94.5 | 87.7 | 93.5 | 94.8 | 95.1 | 95.5 | 95.5 | 94.9 | 86.9 | 93.2 | 94.6 | 95.1 | 95.7 | 95.7 | 94.9
ET Solar Industry | ET-P660245BAC [240V] | 240 W, 240 Vac Inverter | 0.24 | 240 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.0238 | 0.0476 | 0.0714 | 0.119 | 0.1785 | 0.238 | 88.74 | 93.68 | 94.03 | 94.87 | 94.98 | 94.74 | 94.52 | 87.73 | 93.5 | 94.82 | 95.13 | 95.52 | 95.46 | 94.94 | 86.91 | 93.18 | 94.64 | 95.08 | 95.65 | 95.69 | 94.94
ET Solar Industry | ET-P660245BBAC [240V] | 240 W, 240 Vac Inverter | 0.24 | 240 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.0238 | 0.0476 | 0.0714 | 0.119 | 0.1785 | 0.238 | 88.74 | 93.68 | 94.03 | 94.87 | 94.98 | 94.74 | 94.52 | 87.73 | 93.5 | 94.82 | 95.13 | 95.52 | 95.46 | 94.94 | 86.91 | 93.18 | 94.64 | 95.08 | 95.65 | 95.69 | 94.94
ET Solar Industry | ET-P660245BBZAC [240V] | 240 W, 240 Vac Inverter | 0.24 | 240 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.0238 | 0.0476 | 0.0714 | 0.119 | 0.1785 | 0.238 | 88.74 | 93.68 | 94.03 | 94.87 | 94.98 | 94.74 | 94.52 | 87.73 | 93.5 | 94.82 | 95.13 | 95.52 | 95.46 | 94.94 | 86.91 | 93.18 | 94.64 | 95.08 | 95.65 | 95.69 | 94.94
ET Solar Industry | ET-P660245WBZAC [240V] | 240 W, 240 Vac Inverter | 0.24 | 240 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.0238 | 0.0476 | 0.0714 | 0.119 | 0.1785 | 0.238 | 88.74 | 93.68 | 94.03 | 94.87 | 94.98 | 94.74 | 94.52 | 87.73 | 93.5 | 94.82 | 95.13 | 95.52 | 95.46 | 94.94 | 86.91 | 93.18 | 94.64 | 95.08 | 95.65 | 95.69 | 94.94
ET Solar Industry | ET-P660250 WBAC [240V] | 240 W, 240 Vac Inverter | 0.24 | 240 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.22 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 88.7 | 93.7 | 94 | 94.9 | 95 | 94.7 | 94.5 | 87.7 | 93.5 | 94.8 | 95.1 | 95.5 | 95.5 | 94.9 | 86.9 | 93.2 | 94.6 | 95.1 | 95.7 | 95.7 | 94.9
ET Solar Industry | ET-P660250 WBZAC [240V] | 240 W, 240 Vac Inverter | 0.24 | 240 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.0238 | 0.0476 | 0.0714 | 0.119 | 0.1785 | 0.238 | 88.74 | 93.68 | 94.03 | 94.87 | 94.98 | 94.74 | 94.52 | 87.73 | 93.5 | 94.82 | 95.13 | 95.52 | 95.46 | 94.94 | 86.91 | 93.18 | 94.64 | 95.08 | 95.65 | 95.69 | 94.94
ET Solar Industry | ET-P660250BAC [240V] | 240 W, 240 Vac Inverter | 0.24 | 240 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.0238 | 0.0476 | 0.0714 | 0.119 | 0.1785 | 0.238 | 88.74 | 93.68 | 94.03 | 94.87 | 94.98 | 94.74 | 94.52 | 87.73 | 93.5 | 94.82 | 95.13 | 95.52 | 95.46 | 94.94 | 86.91 | 93.18 | 94.64 | 95.08 | 95.65 | 95.69 | 94.94
ET Solar Industry | ET-P660250BBAC [240V] | 240 W, 240 Vac Inverter | 0.24 | 240 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.0238 | 0.0476 | 0.0714 | 0.119 | 0.1785 | 0.238 | 88.74 | 93.68 | 94.03 | 94.87 | 94.98 | 94.74 | 94.52 | 87.73 | 93.5 | 94.82 | 95.13 | 95.52 | 95.46 | 94.94 | 86.91 | 93.18 | 94.64 | 95.08 | 95.65 | 95.69 | 94.94
ET Solar Industry | ET-P660250BBZAC [240V] | 240 W, 240 Vac Inverter | 0.24 | 240 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.0238 | 0.0476 | 0.0714 | 0.119 | 0.1785 | 0.238 | 88.74 | 93.68 | 94.03 | 94.87 | 94.98 | 94.74 | 94.52 | 87.73 | 93.5 | 94.82 | 95.13 | 95.52 | 95.46 | 94.94 | 86.91 | 93.18 | 94.64 | 95.08 | 95.65 | 95.69 | 94.94
ET Solar Industry | ET-P660255BBAC | 240 W, 1-phase Microinverter | 0.24 |  | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 33.5 | 42.5 | 46 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.7 | 94.6 | 95.7 | 95 | 95 | 94.7 | 94.9 | 90 | 94.5 | 95.4 | 95.2 | 95.3 | 95.1 | 95 | 89.3 | 93.7 | 95.1 | 95 | 95.3 | 95.2 | 94.9
ET Solar Industry | ET-P660255BBZAC | 240 W, 1-phase Microinverter | 0.24 |  | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 33.5 | 42.5 | 46 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.7 | 94.6 | 95.7 | 95 | 95 | 94.7 | 94.9 | 90 | 94.5 | 95.4 | 95.2 | 95.3 | 95.1 | 95 | 89.3 | 93.7 | 95.1 | 95 | 95.3 | 95.2 | 94.9
ET Solar Industry | ET-P660255WBAC | 240 W, 1-phase Microinverter | 0.24 |  | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 33.5 | 42.5 | 46 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.7 | 94.6 | 95.7 | 95 | 95 | 94.7 | 94.9 | 90 | 94.5 | 95.4 | 95.2 | 95.3 | 95.1 | 95 | 89.3 | 93.7 | 95.1 | 95 | 95.3 | 95.2 | 94.9
ET Solar Industry | ET-P660255WBZAC | 240 W, 1-phase Microinverter | 0.24 |  | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 33.5 | 42.5 | 46 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.7 | 94.6 | 95.7 | 95 | 95 | 94.7 | 94.9 | 90 | 94.5 | 95.4 | 95.2 | 95.3 | 95.1 | 95 | 89.3 | 93.7 | 95.1 | 95 | 95.3 | 95.2 | 94.9
ET Solar Industry | ET-P660255WWAC | 240 W, 1-phase Microinverter | 0.24 |  | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 33.5 | 42.5 | 46 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.7 | 94.6 | 95.7 | 95 | 95 | 94.7 | 94.9 | 90 | 94.5 | 95.4 | 95.2 | 95.3 | 95.1 | 95 | 89.3 | 93.7 | 95.1 | 95 | 95.3 | 95.2 | 94.9
ET Solar Industry | ET-P660255WWZAC | 240 W, 1-phase Microinverter | 0.24 |  | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 33.5 | 42.5 | 46 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.7 | 94.6 | 95.7 | 95 | 95 | 94.7 | 94.9 | 90 | 94.5 | 95.4 | 95.2 | 95.3 | 95.1 | 95 | 89.3 | 93.7 | 95.1 | 95 | 95.3 | 95.2 | 94.9
ET Solar Industry | ET-P660260WBAC | 240 W, 1-phase Microinverter | 0.24 |  | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 33.5 | 42.5 | 46 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.7 | 94.6 | 95.7 | 95 | 95 | 94.7 | 94.9 | 90 | 94.5 | 95.4 | 95.2 | 95.3 | 95.1 | 95 | 89.3 | 93.7 | 95.1 | 95 | 95.3 | 95.2 | 94.9
ET Solar Industry | ET-P660260WBZAC | 240 W, 1-phase Microinverter | 0.24 |  | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 33.5 | 42.5 | 46 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.7 | 94.6 | 95.7 | 95 | 95 | 94.7 | 94.9 | 90 | 94.5 | 95.4 | 95.2 | 95.3 | 95.1 | 95 | 89.3 | 93.7 | 95.1 | 95 | 95.3 | 95.2 | 94.9
ET Solar Industry | ET-P660260WWAC | 240 W, 1-phase Microinverter | 0.24 |  | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 33.5 | 42.5 | 46 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.7 | 94.6 | 95.7 | 95 | 95 | 94.7 | 94.9 | 90 | 94.5 | 95.4 | 95.2 | 95.3 | 95.1 | 95 | 89.3 | 93.7 | 95.1 | 95 | 95.3 | 95.2 | 94.9
ET Solar Industry | ET-P660260WWZAC | 240 W, 1-phase Microinverter | 0.24 |  | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 33.5 | 42.5 | 46 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.7 | 94.6 | 95.7 | 95 | 95 | 94.7 | 94.9 | 90 | 94.5 | 95.4 | 95.2 | 95.3 | 95.1 | 95 | 89.3 | 93.7 | 95.1 | 95 | 95.3 | 95.2 | 94.9
ETM Electromatic | 290-480-60 | Utility Interactive Bi-Directional Inverter | 279.3 |  | 96.5 | Y | N |  | 900 |  |  | 372 | 451 | 546 | 27.93 | 55.86 | 83.79 | 139.6 | 209.5 | 279.3 | 98.1 | 98.1 | 97.8 | 97.1 | 96.2 | 95.7 | 96.7 | 98.6 | 98.3 | 97.9 | 97.1 | 96.2 | 95.4 | 96.7 | 98.9 | 98.4 | 98 | 97.1 | 96.2 | 95.3 | 96.8
E-Village Solar | EVS1100EVR [120V] | 1100W, 120 Vac Utility Interactive Inverter | 1.1 | 120 | 90.5 | Y | N |  | 3.6 |  |  | 100 | 182 | 380 | 0.11 | 0.22 | 0.33 | 0.55 | 0.83 | 1.1 | 81.8 | 89 | 90.9 | 92.1 | 92.4 | 92.5 | 91.6 | 79.9 | 88 | 90.1 | 91.7 | 92.2 | 92.3 | 91.1 | 74.8 | 84.7 | 87.8 | 90 | 90.8 | 91.1 | 89.3
E-Village Solar | EVS2000EVR [240V] | 2000 W, 240 Vac Utility Interactive Inverter | 2 | 240 | 92 | Y | N |  | 3.6 |  |  | 100 | 199 | 380 | 0.2 | 0.4 | 0.6 | 1 | 1.5 | 2 | 87.3 | 91.7 | 92.6 | 93.5 | 93.2 | 93 | 92.9 | 85.7 | 90.8 | 92.1 | 92.9 | 92.9 | 92.6 | 92.4 | 82.4 | 88.8 | 90.5 | 91.6 | 91.8 | 91.6 | 91.1
E-Village Solar | EVS2500 [240V] | 2500 W, 240 Vac Utility Interactive Inverter | 2.5 | 240 | 94.5 | Y | N |  | 3.9 |  |  | 100 | 218 | 400 | 0.25 | 0.5 | 0.75 | 1.25 | 1.88 | 2.5 | 87.1 | 93.3 | 94.9 | 95.8 | 95.8 | 95.6 | 95.2 | 85.2 | 92.4 | 93.8 | 95.2 | 95.4 | 95.1 | 94.6 | 80.4 | 90 | 91.7 | 93.7 | 94.5 | 93.8 | 93.2
E-Village Solar | EVS3000 [240V] | 3000 W, 240 Vac Utility Interactive Inverter | 3 | 240 | 93.5 | Y | N |  | 3.63 |  |  | 100 | 222.5 | 380 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 88.9 | 92.9 | 93.8 | 94.3 | 94.2 | 93.9 | 93.9 | 87.9 | 92.5 | 93.5 | 94.1 | 94 | 93.8 | 93.7 | 84.9 | 90.9 | 92.4 | 93.3 | 93.2 | 93 | 92.7
E-Village Solar | EVS3500 [240V] | 3500 W, 240 Vac Utility Interactive Inverter | 3.5 | 240 | 95.5 | Y | N |  | 3.86 |  |  | 100 | 263 | 400 | 0.35 | 0.7 | 1.05 | 1.75 | 2.63 | 3.5 | 87.2 | 93.1 | 95.4 | 96.5 | 96.7 | 96.6 | 95.9 | 85.7 | 92.2 | 94.9 | 96.2 | 96.4 | 96.3 | 95.5 | 82.1 | 90.2 | 93.6 | 95.4 | 95.7 | 95.6 | 94.5
E-Village Solar | EVS4600 [208V] | 4600 W, 208 Vac Utility Interactive Inverter | 4.6 | 208 | 95.5 | Y | N |  | 4 |  |  | 100 | 254 | 400 | 0.46 | 0.92 | 1.38 | 2.3 | 3.45 | 4.6 | 90.3 | 94.8 | 95.9 | 96.5 | 96.5 | 96.2 | 96.1 | 89.2 | 94.3 | 95.6 | 96.3 | 96.4 | 96.1 | 95.9 | 86.5 | 92.9 | 94.7 | 95.6 | 95.7 | 95.4 | 95
E-Village Solar | EVS4800 [240V] | 4800 W, 240 Vac Utility Interactive Inverter | 4.8 | 240 | 96 | Y | N |  | 4.1 |  |  | 100 | 263 | 400 | 0.48 | 0.96 | 1.44 | 2.4 | 3.6 | 4.8 | 86.8 | 93.5 | 95.5 | 97 | 97.2 | 97.1 | 96.4 | 85.5 | 92.9 | 95 | 96.7 | 96.9 | 96.8 | 96 | 84.5 | 91.5 | 93.9 | 95.9 | 96.2 | 96.1 | 95.1
E-Village Solar | EVS5200 [208V] | 5200 W, 240 Vac Utility Interactive Inverter | 5.2 | 208 | 96 | Y | N |  | 4 |  |  | 100 | 280 | 400 | 0.52 | 1.04 | 1.56 | 2.6 | 3.9 | 5.2 | 89.4 | 94.8 | 96 | 96.8 | 97 | 96.8 | 96.4 | 88.6 | 94.4 | 95.7 | 96.7 | 96.8 | 96.6 | 96.2 | 87.7 | 93.1 | 94.8 | 96.1 | 96.3 | 96.1 | 95.5
Exeltech | AC2-1-2-6-5-XX [120V] | 212 W, 120 Vac Inverter, where xx is connection option | 0.212 | 120 | 94.5 | N | Y |  | 0 |  |  | 36 | 50 | 55 | 0.0212 | 0.0424 | 0.0636 | 0.106 | 0.159 | 0.212 | 87.88 | 94.35 | 95.79 | 95.73 | 94.8 | 93.45 | 94.75 | 85.23 | 92.51 | 94.56 | 95.3 | 95.12 | 94.17 | 94.52 | 83.57 | 92.02 | 94.33 | 94.87 | 94.87 | 93.91 | 94.16
Exeltech | AC2-1-B-6-5-XX [120V] | 212 W, 120 Vac Inverter, where xx is connection option | 0.212 | 120 | 94.5 | N | Y |  | 0 |  |  | 36 | 50 | 55 | 0.0212 | 0.0424 | 0.0636 | 0.106 | 0.159 | 0.212 | 87.88 | 94.35 | 95.79 | 95.73 | 94.8 | 93.45 | 94.75 | 85.23 | 92.51 | 94.56 | 95.3 | 95.12 | 94.17 | 94.52 | 83.57 | 92.02 | 94.33 | 94.87 | 94.87 | 93.91 | 94.16
Exeltech | AC2-1-C-6-5-XX [120V] | 212 W, 120 Vac Inverter, where xx is connection option | 0.212 | 120 | 94.5 | N | Y |  | 0 |  |  | 36 | 50 | 55 | 0.0212 | 0.0424 | 0.0636 | 0.106 | 0.159 | 0.212 | 87.88 | 94.35 | 95.79 | 95.73 | 94.8 | 93.45 | 94.75 | 85.23 | 92.51 | 94.56 | 95.3 | 95.12 | 94.17 | 94.52 | 83.57 | 92.02 | 94.33 | 94.87 | 94.87 | 93.91 | 94.16
Exeltech | AC2-1-L-6-5-XX [120V] | 212 W, 120 Vac Inverter, where xx is connection option | 0.212 | 120 | 94.5 | N | Y |  | 0 |  |  | 36 | 50 | 55 | 0.0212 | 0.0424 | 0.0636 | 0.106 | 0.159 | 0.212 | 87.88 | 94.35 | 95.79 | 95.73 | 94.8 | 93.45 | 94.75 | 85.23 | 92.51 | 94.56 | 95.3 | 95.12 | 94.17 | 94.52 | 83.57 | 92.02 | 94.33 | 94.87 | 94.87 | 93.91 | 94.16
Exeltech | AM24-1-B-6-0-00 [120V] | 212W, 120 Vac Inverter | 0.212 | 120 | 94.5 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0 |  |  | 36 | 50 | 55 | 0.0212 | 0.0424 | 0.0636 | 0.106 | 0.159 | 0.212 | 87.88 | 94.35 | 95.79 | 95.73 | 94.8 | 93.45 | 94.75 | 85.23 | 92.51 | 94.56 | 95.3 | 95.12 | 94.17 | 94.52 | 83.57 | 92.02 | 94.33 | 94.87 | 94.87 | 93.91 | 94.16
Exeltech | XLGT18A60 [120V] | 1.8 kW, 120 Vac Utility Interactive Inverter | 1.8 | 120 | 96.5 | Y | N |  | 0.16 |  |  | 100 | 290 | 450 | 0.18 | 0.36 | 0.54 | 0.9 | 1.35 | 1.8 | 96.55 | 97.49 | 97.81 | 97.53 | 96.98 | 96.13 | 97.16 | 96.09 | 97.25 | 97.43 | 97.29 | 96.75 | 95.98 | 96.9 | 93.81 | 96.04 | 96.48 | 94.73 | 94.95 | 95.09 | 95.11
Exeltech | XLGT18A60-01 [120V] | 1.8 kW, 120 Vac Utility Interactive Inverter (-01 for disconnect) | 1.8 | 120 | 96.5 | Y | N |  | 0.16 |  |  | 100 | 290 | 450 | 0.18 | 0.36 | 0.54 | 0.9 | 1.35 | 1.8 | 96.55 | 97.49 | 97.81 | 97.53 | 96.98 | 96.13 | 97.16 | 96.09 | 97.25 | 97.43 | 97.29 | 96.75 | 95.98 | 96.9 | 93.81 | 96.04 | 96.48 | 94.73 | 94.95 | 95.09 | 95.11
Flextronics Industrial | FLV-IA-6.0S1UA | 6.0 kW, transformerless Utility Interactive Inverter | 6 |  | 97.5 | Y | N |  | 6 |  |  | 200 | 380 | 500 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 94.9 | 96.1 | 96.8 | 97.3 | 97.3 | 96.5 | 97.1 | 95.5 | 97 | 97.4 | 97.4 | 97.4 | 98 | 97.3 | 95.3 | 96.9 | 97.5 | 97.6 | 97.6 | 97.6 | 97.4 | 2017-05
Flextronics Industrial | FLV-IA-7.0S1UA | 7.0 kW, transformerless Utility Interactive Inverter | 7 |  | 97.5 | Y | N |  | 7 |  |  | 250 | 380 | 500 | 0.7 | 1.4 | 2.1 | 3.5 | 5.25 | 7 | 95 | 96.2 | 96.8 | 97.4 | 97.4 | 96.5 | 97.1 | 95.6 | 97 | 97.4 | 97.5 | 97.5 | 97 | 97.4 | 95.3 | 97 | 97.5 | 97.7 | 97.6 | 97.6 | 97.5 | 2017-05
Flextronics Industrial | FLV-IA-7.6S1UA | 7.6 kW, transformerless Utility Interactive Inverter | 7.6 |  | 97.5 | Y | N |  | 7 |  |  | 200 | 380 | 500 | 0.76 | 1.52 | 2.28 | 3.8 | 5.7 | 7.6 | 95.1 | 96.2 | 96.9 | 97.3 | 97.1 | 96.6 | 97 | 95.6 | 97.2 | 97.5 | 97.8 | 97.3 | 97.9 | 97.4 | 95.4 | 96.8 | 97.6 | 97.8 | 97.9 | 97.7 | 97.7 | 2017-05
Flextronics Industrial | FLV-IA-8.0S1UA | 8.0 kW, transformerless Utility Interactive Inverter | 8 |  | 97.5 | Y | N |  | 6 |  |  | 250 | 380 | 500 | 0.8 | 1.6 | 2.4 | 4 | 6 | 8 | 95.1 | 96.2 | 96.9 | 97.4 | 97.2 | 96.6 | 97 | 95.7 | 97.2 | 97.4 | 97.5 | 97.7 | 97 | 97.5 | 95.4 | 96.7 | 97.6 | 97.8 | 97.9 | 97.7 | 97.7 | 2017-05
Flextronics Industrial | FLV-IA-9.0S1UA | 9.0 kW, transformerless Utility Interactive Inverter | 9 |  | 97.5 | Y | N |  | 7 |  |  | 250 | 380 | 500 | 0.9 | 1.8 | 2.7 | 4.5 | 6.75 | 9 | 95.1 | 96.8 | 97 | 97.5 | 97.4 | 97 | 97.2 | 95.7 | 97.3 | 97.4 | 97.6 | 97.8 | 97.1 | 97.5 | 95.6 | 96.7 | 97.7 | 97.8 | 97.8 | 97.7 | 97.7 | 2017-05
Flextronics Industrial | FLV-IA-10.0S1UA | 10.0 kW, transformerless Utility Interactive Inverter | 10 |  | 97.5 | Y | N |  | 7 |  |  | 250 | 380 | 500 | 1 | 2 | 3 | 5 | 7.5 | 10 | 95.2 | 96.8 | 97.1 | 97.5 | 97.6 | 97.1 | 97.4 | 95.3 | 96.3 | 97.6 | 97.7 | 97.7 | 97.2 | 97.5 | 95.6 | 96.8 | 97.7 | 97.8 | 97.8 | 97.7 | 97.6 | 2017-05
Friem | RECon 30L-100-US | 100 kW 3-phase Utility Interactive Inverter | 100 |  | 98 | Y | N |  | 59.63 |  |  | 325 | 487 | 650 | 10 | 20 | 30 | 50 | 75 | 100 | 96.5 | 98.1 | 98.4 | 98 | 97.3 | 96.9 | 97.5 | 95.3 | 97.8 | 98.3 | 98.2 | 98.1 | 97.9 | 98 | 96 | 98.2 | 98.8 | 98.7 | 98.3 | 97.7 | 98.3
Friem | RECon 30H-150-US [300V] | 150 kW 3-phase output 300Vac/LV/MV Utility Interactive Inverter | 150 | 300 | 98 | Y | N |  | 62.53 |  |  | 480 | 615 | 750 | 15 | 30 | 45 | 75 | 112.5 | 150 | 93.6 | 96.3 | 97 | 97.5 | 97.4 | 97.7 | 97.2 | 95.6 | 97.6 | 98.4 | 98.3 | 98 | 98 | 98 | 94.1 | 96.7 | 97.7 | 97.9 | 97.8 | 97.6 | 97.6
Fronius USA | Galvo 1.5-1 208-240 [208V] | 1500 W, 208 Vac Utility Interactive Inverter with arc detector | 1.5 | 208 | 94 | Y | N |  | 0.67 |  |  | 100 | 260 | 335 | 0.15 | 0.3 | 0.45 | 0.75 | 1.125 | 1.5 | 85.7 | 91 | 92.6 | 93.8 | 93.9 | 93.8 | 93.3 | 87.4 | 92.2 | 94 | 95 | 95.5 | 95.5 | 94.7 | 87.2 | 92 | 93.5 | 94.6 | 95 | 95.2 | 94.3
Fronius USA | Galvo 1.5-1 208-240 [240V] | 1500 W, 240 Vac Utility Interactive Inverter with arc detector | 1.5 | 240 | 94.5 | Y | N |  | 0.89 |  |  | 100 | 260 | 335 | 0.15 | 0.3 | 0.45 | 0.75 | 1.125 | 1.5 | 87.1 | 91.2 | 93 | 94 | 94.2 | 94.1 | 93.6 | 88 | 92.3 | 94.1 | 95.2 | 95.7 | 95.8 | 94.9 | 87.8 | 92 | 93.6 | 94.9 | 95.3 | 95.5 | 94.5
Fronius USA | Galvo 2.0-1 208-240 [208V] | 1900 W, 208 Vac Utility Interactive Inverter with arc detector | 1.9 | 208 | 94.5 | Y | N |  | 0.67 |  |  | 100 | 260 | 335 | 0.19 | 0.38 | 0.57 | 0.95 | 1.425 | 1.9 | 87.5 | 92.1 | 93.2 | 94 | 93.9 | 93.5 | 93.4 | 89.1 | 93.4 | 94.4 | 95.3 | 95.5 | 95.4 | 94.9 | 88.7 | 93 | 94.2 | 94.5 | 95.1 | 95.2 | 94.5
Fronius USA | Galvo 2.0-1 208-240 [240V] | 2000 W 240 Vac Utility Interactive Inverter with arc detector | 2 | 240 | 94.5 | Y | N |  | 0.9 |  |  | 100 | 260 | 335 | 0.2 | 0.4 | 0.6 | 1 | 1.5 | 2 | 88.5 | 92.6 | 93.5 | 94.2 | 94.1 | 93.7 | 93.8 | 89.6 | 93.9 | 94.8 | 95.6 | 95.8 | 95.7 | 95.3 | 89.7 | 93.4 | 94.6 | 94.9 | 95.4 | 95.5 | 94.9
Fronius USA | IG 2000 NEG | 2000 W Grid-tied unit with Integrated Disconnects and Performance Meter | 2 |  | 93.5 | Y | N |  | 0.91 |  |  | 100 | 280 | 400 | 0.2 | 0.4 | 0.6 | 1 | 1.5 | 2 | 86.8 | 90.8 | 92.4 | 93.7 | 93.6 | 94.3 | 93.1 | 87.4 | 91 | 93 | 94.8 | 95.1 | 95.4 | 94.3 | 84.6 | 89.9 | 90.6 | 92.7 | 93.7 | 93.9 | 92.6
Fronius USA | IG 2000 POS | 2000 W Grid-tied unit with Integrated Disconnects and Performance Meter | 2 |  | 93.5 | Y | N |  | 0.91 |  |  | 100 | 280 | 400 | 0.2 | 0.4 | 0.6 | 1 | 1.5 | 2 | 86.8 | 90.8 | 92.4 | 93.7 | 93.6 | 94.3 | 93.1 | 87.4 | 91 | 93 | 94.8 | 95.1 | 95.4 | 94.3 | 84.6 | 89.9 | 90.6 | 92.7 | 93.7 | 93.9 | 92.6
Fronius USA | IG 2500-LV NEG | 2350W Grid-tied unit with Integrated Disconnects and Performance Meter | 2.35 |  | 93 | Y | N |  | 0.73 |  |  | 100 | 280 | 400 | 0.24 | 0.47 | 0.71 | 1.18 | 1.76 | 2.35 | 87.8 | 91.4 | 92.6 | 93.3 | 93.1 | 92.2 | 92.7 | 88.4 | 91.5 | 92.8 | 94.2 | 94.3 | 93.6 | 93.7 | 84.8 | 88.4 | 90.5 | 92.6 | 93.3 | 93.1 | 92.2
Fronius USA | IG 2500-LV POS | 2350W Grid-tied unit with Integrated Disconnects and Performance Meter | 2.35 |  | 93 | Y | N |  | 0.73 |  |  | 100 | 280 | 400 | 0.24 | 0.47 | 0.71 | 1.18 | 1.76 | 2.35 | 87.8 | 91.4 | 92.6 | 93.3 | 93.1 | 92.2 | 92.7 | 88.4 | 91.5 | 92.8 | 94.2 | 94.3 | 93.6 | 93.7 | 84.8 | 88.4 | 90.5 | 92.6 | 93.3 | 93.1 | 92.2
Fronius USA | Galvo 2.5-1 208-240 [208V] | 2500 W, 208 Vac Utility Interactive Inverter with arc detector | 2.5 | 208 | 95 | Y | N |  | 0.67 |  |  | 100 | 330 | 440 | 0.25 | 0.5 | 0.75 | 1.25 | 1.88 | 2.5 | 90.2 | 93.6 | 94.3 | 94.7 | 94.6 | 94.1 | 94.3 | 91.1 | 94.6 | 95.3 | 95.6 | 95.6 | 95.4 | 95.3 | 91.1 | 94.1 | 94.9 | 95.1 | 95.2 | 95.1 | 94.9
Fronius USA | Galvo 2.5-1 208-240 [240V] | 2500 W, 240 Vac Utility Interactive Inverter with arc detector | 2.5 | 240 | 95 | Y | N |  | 0.67 |  |  | 100 | 330 | 440 | 0.25 | 0.5 | 0.75 | 1.25 | 1.88 | 2.5 | 90.6 | 93.9 | 94.6 | 95 | 94.9 | 94.5 | 94.7 | 91.5 | 94.8 | 95.4 | 96 | 96 | 95.8 | 95.7 | 91.5 | 94.3 | 95.3 | 95.5 | 95.7 | 95.6 | 95.3
Fronius USA | IG 3000 NEG | 2700 W Grid-tied unit with Integrated Disconnects and Performance Meter | 2.7 |  | 94 | Y | N |  | 0.91 |  |  | 100 | 280 | 400 | 0.27 | 0.54 | 0.81 | 1.35 | 2.03 | 2.7 | 88.2 | 92 | 94 | 94.3 | 94.1 | 93.6 | 93.7 | 89.2 | 92.6 | 94.4 | 94.9 | 95.1 | 94.5 | 94.6 | 88.3 | 90 | 92.3 | 93.4 | 93.8 | 93.6 | 93.1
Fronius USA | IG 3000 POS | 2700 W Grid-tied unit with Integrated Disconnects and Performance Meter | 2.7 |  | 94 | Y | N |  | 0.91 |  |  | 100 | 280 | 400 | 0.27 | 0.54 | 0.81 | 1.35 | 2.03 | 2.7 | 88.2 | 92 | 94 | 94.3 | 94.1 | 93.6 | 93.7 | 89.2 | 92.6 | 94.4 | 94.9 | 95.1 | 94.5 | 94.6 | 88.3 | 90 | 92.3 | 93.4 | 93.8 | 93.6 | 93.1
Fronius USA | Galvo 3.1-1 208-240 [208V] | 2930 W, 208 Vac Utility Interactive Inverter with arc detector | 2.93 | 208 | 95 | Y | N |  | 0.7 |  |  | 100 | 330 | 440 | 0.29 | 0.59 | 0.88 | 1.47 | 2.2 | 2.93 | 90.9 | 94.1 | 94.4 | 94.7 | 94.3 | 93.6 | 94.2 | 92.2 | 95 | 95.4 | 95.6 | 95.5 | 95.1 | 95.3 | 91.9 | 94.4 | 95.1 | 95.1 | 95.2 | 94.9 | 95 |  | 2018-03-15
Fronius USA | IG Plus 3.0-1 UNI [208V] | 3000 W, 208 Vac Utility Interactive Inverter | 3 | 208 | 95 | Y | N |  | 0.62 |  |  | 100 | 366 | 480 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 92.2 | 94.4 | 95.1 | 95.3 | 94.9 | 94.1 | 94.8 | 92.5 | 95.2 | 95.3 | 95.9 | 95.8 | 95.5 | 95.6 | 92.2 | 94.5 | 94.5 | 95.2 | 95.3 | 95.1 | 95
Fronius USA | IG Plus 3.0-1 UNI [240V] | 3000 W, 240 Vac Utility Interactive Inverter | 3 | 240 | 95.5 | Y | N |  | 0.83 |  |  | 100 | 390 | 480 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 91.4 | 94.3 | 95.3 | 95.7 | 95.6 | 95.1 | 95.3 | 91.3 | 95.1 | 95.4 | 96.1 | 96.2 | 96 | 95.8 | 91.3 | 94.7 | 95 | 95.5 | 95.7 | 95.7 | 95.3
Fronius USA | IG Plus 3.0-1 UNI [277V] | 3000 W, 277 Vac Utility Interactive Inverter | 3 | 277 | 95.5 | Y | N |  | 1.1 |  |  | 100 | 330 | 480 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 90.2 | 94.4 | 95.2 | 95.9 | 96 | 95.7 | 95.5 | 91.1 | 94.9 | 95.5 | 96.1 | 96.3 | 96.2 | 95.9 | 91.5 | 94.5 | 95.4 | 95.7 | 96 | 96.1 | 95.6
Fronius USA | IG Plus A 3.0 [208V] | 3000 W, 208 Vac Utility Interactive Inverter, Same as Series V with arc detector | 3 | 208 | 95 | Y | N |  | 0.53 | 3 | 0.53 | 100 | 366 | 480 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 92.2 | 94.5 | 95.1 | 95.4 | 95.2 | 94.6 | 95 | 92.4 | 95 | 95.2 | 95.9 | 95.9 | 95.6 | 95.6 | 91.6 | 94 | 94.2 | 95.3 | 95.5 | 95.3 | 95.1
Fronius USA | IG Plus A 3.0 [240V] | 3000 W, 240 Vac Utility Interactive Inverter, Same as Series V with arc detector | 3 | 240 | 95.5 | Y | N |  | 0.7 | 3 | 0.7 | 100 | 390 | 480 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 91.9 | 94.5 | 95.3 | 95.9 | 95.8 | 95.5 | 95.5 | 92.2 | 95.1 | 95.4 | 96.1 | 96.3 | 96.2 | 95.9 | 91.9 | 94.6 | 94.6 | 95.6 | 95.9 | 95.9 | 95.5
Fronius USA | IG Plus A 3.0 [277V] | 3000 W, 277 Vac Utility Interactive Inverter, Same as Series V with arc detector | 3 | 277 | 96 | Y | N |  | 0.94 | 3 | 0.94 | 100 | 330 | 480 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 90.8 | 94.5 | 95.4 | 96.2 | 96.3 | 96 | 95.8 | 91.5 | 95 | 95.4 | 96.3 | 96.5 | 96.4 | 96 | 91.9 | 94.7 | 95.2 | 95.8 | 96.2 | 96.4 | 95.8
Fronius USA | IG Plus V 3.0 [208V] | 3000 W, 208 Vac Utility Interactive Inverter | 3 | 208 | 95 | Y | N |  | 0.53 | 3 | 0.53 | 100 | 366 | 480 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 92.22 | 94.53 | 95.11 | 95.38 | 95.19 | 94.61 | 95.04 | 92.39 | 94.99 | 95.23 | 95.89 | 95.9 | 95.55 | 95.62 | 91.58 | 94 | 94.23 | 95.3 | 95.49 | 95.34 | 95.06
Fronius USA | IG Plus V 3.0 [240V] | 3000 W, 240 Vac Utility Interactive Inverter | 3 | 240 | 95.5 | Y | N |  | 0.7 | 3 | 0.7 | 100 | 390 | 480 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 91.88 | 94.47 | 95.31 | 95.9 | 95.84 | 95.48 | 95.54 | 92.22 | 95.09 | 95.37 | 96.11 | 96.29 | 96.16 | 95.91 | 91.85 | 94.57 | 94.59 | 95.58 | 95.92 | 95.94 | 95.46
Fronius USA | IG Plus V 3.0 [277V] | 3000 W, 277 Vac Utility Interactive Inverter | 3 | 277 | 96 | Y | N |  | 0.94 | 3 | 0.94 | 100 | 330 | 480 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 90.8 | 94.51 | 95.44 | 96.17 | 96.26 | 96.04 | 95.82 | 91.52 | 95.02 | 95.35 | 96.31 | 96.49 | 96.42 | 96.04 | 91.92 | 94.72 | 95.21 | 95.82 | 96.23 | 96.39 | 95.78
Fronius USA | Galvo 3.1-1 208-240 [240V] | 3100 W, 240 Vac Utility Interactive Inverter with arc detector | 3.1 | 240 | 95.5 | Y | N |  | 0.9 |  |  | 100 | 330 | 440 | 0.31 | 0.62 | 0.93 | 1.55 | 2.33 | 3.1 | 91.6 | 94.4 | 94.8 | 95 | 94.7 | 94 | 94.6 | 92.8 | 95.4 | 95.8 | 96 | 95.9 | 95.5 | 95.7 | 92.4 | 94.9 | 95.5 | 95.6 | 95.6 | 95.4 | 95.4
Fronius USA | Fronius Primo 3.8-1 208-240 [208V] | 3800 W, 208 Vac Utility Interactive Inverter with arc detector and meter | 3.8 | 208 | 96 | Y | N |  | 0.41 |  |  | 100 | 650 | 800 | 0.38 | 0.76 | 1.14 | 1.9 | 2.85 | 3.8 | 87.3 | 92.4 | 93.9 | 95.2 | 95.6 | 95.7 | 94.8 | 90.7 | 95.2 | 96.4 | 97.2 | 97.5 | 97.6 | 96.9 | 85.7 | 93.4 | 95.2 | 96.6 | 97.1 | 97.3 | 96.1
Fronius USA | Fronius Primo 3.8-1 208-240 [240V] | 3800 W, 240 Vac Utility Interactive Inverter with arc detector and meter | 3.8 | 240 | 95.5 | Y | N |  | 0.55 |  |  | 100 | 650 | 800 | 0.38 | 0.76 | 1.14 | 1.9 | 2.85 | 3.8 | 85.5 | 91.5 | 93.3 | 94.8 | 95.4 | 95.6 | 94.4 | 87.2 | 93.4 | 95 | 96.4 | 96.9 | 97.2 | 96 | 87 | 93.7 | 95.5 | 96.9 | 97.4 | 97.6 | 96.5
Fronius USA | IG Plus 3.8-1 UNI [208V] | 3800 W, 208 Vac Utility Interactive Inverter with arc detector and meter | 3.8 | 208 | 95 | Y | N |  | 0.62 |  |  | 100 | 366 | 480 | 0.38 | 0.76 | 1.14 | 1.9 | 2.85 | 3.8 | 93 | 94.9 | 95.3 | 95.1 | 94.4 | 93 | 94.6 | 93.6 | 95.1 | 95.7 | 95.9 | 95.6 | 94.9 | 95.6 | 92.7 | 94.4 | 95 | 95.4 | 95.2 | 94.7 | 95
Fronius USA | IG Plus 3.8-1 UNI [240V] | 3800 W, 240 Vac Utility Interactive Inverter with arc detector and meter | 3.8 | 240 | 95.5 | Y | N |  | 0.83 |  |  | 100 | 390 | 480 | 0.38 | 0.76 | 1.14 | 1.9 | 2.85 | 3.8 | 91.7 | 94.7 | 95.4 | 95.5 | 95.2 | 94.2 | 95.1 | 92.3 | 95 | 95.5 | 96.1 | 96 | 95.7 | 95.8 | 92 | 94.8 | 95 | 95.6 | 95.6 | 95.5 | 95.4
Fronius USA | IG Plus 3.8-1 UNI [277V] | 3800 W, 277 Vac Utility Interactive Inverter with arc detector and meter | 3.8 | 277 | 95.5 | Y | N |  | 1.1 |  |  | 100 | 330 | 480 | 0.38 | 0.76 | 1.14 | 1.9 | 2.85 | 3.8 | 91.7 | 94.8 | 95.5 | 95.9 | 95.8 | 95.1 | 95.5 | 91.8 | 95.2 | 95.6 | 96.2 | 96.2 | 95.8 | 95.9 | 91.8 | 95.1 | 95.3 | 95.9 | 96.1 | 96 | 95.7
Fronius USA | IG Plus A 3.8 [208V] | 3800 W, 208 Vac Utility Interactive Inverter, Same as Series V with arc detector | 3.8 | 208 | 95 | Y | N |  | 0.53 | 3.8 | 0.53 | 100 | 366 | 480 | 0.38 | 0.76 | 1.14 | 1.9 | 2.85 | 3.8 | 93 | 94.9 | 95.4 | 95.3 | 94.8 | 93.8 | 94.9 | 93.5 | 95 | 95.6 | 96 | 95.7 | 95 | 95.6 | 93 | 93.9 | 94.8 | 95.5 | 95.4 | 94.9 | 95.2
Fronius USA | IG Plus A 3.8 [240V] | 3800 W, 240 Vac Utility Interactive Inverter, Same as Series V with arc detector | 3.8 | 240 | 95.5 | Y | N |  | 0.7 | 3.8 | 0.7 | 100 | 390 | 480 | 0.38 | 0.76 | 1.14 | 1.9 | 2.85 | 3.8 | 92.7 | 95 | 95.7 | 95.9 | 95.6 | 94.9 | 95.5 | 93.3 | 95.3 | 95.7 | 96.3 | 96.2 | 95.8 | 96 | 93.1 | 94.6 | 95.1 | 95.9 | 95.9 | 95.7 | 95.6
Fronius USA | IG Plus A 3.8 [277V] | 3800 W, 277 Vac Utility Interactive Inverter, Same as Series V with arc detector | 3.8 | 277 | 96 | Y | N |  | 0.94 | 3.8 | 0.94 | 100 | 330 | 480 | 0.38 | 0.76 | 1.14 | 1.9 | 2.85 | 3.8 | 92.1 | 95 | 95.8 | 96.2 | 96.1 | 95.7 | 95.9 | 92.6 | 95.4 | 95.8 | 96.5 | 96.4 | 96.1 | 96.1 | 93 | 95.2 | 95.3 | 96.1 | 96.4 | 96.3 | 96
Fronius USA | IG Plus V 3.8 [208V] | 3800 W, 208 Vac Utility Interactive Inverter with arc detector and meter | 3.8 | 208 | 95 | Y | N |  | 0.53 | 3.8 | 0.53 | 100 | 366 | 480 | 0.38 | 0.76 | 1.14 | 1.9 | 2.85 | 3.8 | 92.98 | 94.93 | 95.38 | 95.33 | 94.78 | 93.76 | 94.85 | 93.52 | 95.04 | 95.62 | 95.96 | 95.65 | 95.02 | 95.56 | 92.96 | 93.88 | 94.78 | 95.48 | 95.41 | 94.93 | 95.15
Fronius USA | IG Plus V 3.8 [240V] | 3800 W, 240 Vac Utility Interactive Inverter with arc detector and meter | 3.8 | 240 | 95.5 | Y | N |  | 0.7 | 3.8 | 0.7 | 100 | 390 | 480 | 0.38 | 0.76 | 1.14 | 1.9 | 2.85 | 3.8 | 92.7 | 95.04 | 95.67 | 95.88 | 95.57 | 94.87 | 95.47 | 93.31 | 95.3 | 95.74 | 96.28 | 96.2 | 95.81 | 95.98 | 93.05 | 94.61 | 95.08 | 95.85 | 95.93 | 95.71 | 95.62
Fronius USA | IG Plus V 3.8 [277V] | 3800 W, 277 Vac Utility Interactive Inverter with arc detector and meter | 3.8 | 277 | 96 | Y | N |  | 0.94 | 3.8 | 0.94 | 100 | 330 | 480 | 0.38 | 0.76 | 1.14 | 1.9 | 2.85 | 3.8 | 92.08 | 95.02 | 95.77 | 96.22 | 96.12 | 95.68 | 95.86 | 92.56 | 95.38 | 95.82 | 96.46 | 96.42 | 96.14 | 96.14 | 92.98 | 95.16 | 95.31 | 96.1 | 96.35 | 96.27 | 95.97
Fronius USA | IG 4000 NEG | 4000 W, Grid-tied unit with Integrated Disconnects and Performance Meter | 4 |  | 94 | Y | N |  | 0.9 |  |  | 100 | 280 | 400 | 0.4 | 0.8 | 1.2 | 2 | 3 | 4 | 90 | 92.9 | 93.4 | 93.8 | 93.8 | 93.3 | 93.5 | 90.6 | 93.8 | 94.9 | 95.1 | 95.1 | 94.9 | 94.8 | 87.1 | 91.1 | 92.6 | 93.4 | 93.6 | 93.6 | 93.1
Fronius USA | IG 4000 POS | 4000 W, Grid-tied unit with Integrated Disconnects and Performance Meter | 4 |  | 94 | Y | N |  | 0.9 |  |  | 100 | 280 | 400 | 0.4 | 0.8 | 1.2 | 2 | 3 | 4 | 90 | 92.9 | 93.4 | 93.8 | 93.8 | 93.3 | 93.5 | 90.6 | 93.8 | 94.9 | 95.1 | 95.1 | 94.9 | 94.8 | 87.1 | 91.1 | 92.6 | 93.4 | 93.6 | 93.6 | 93.1
Fronius USA | IG 4500-LV NEG | 4500 W, Grid-tied unit with Integrated Disconnects and Performance Meter | 4.5 |  | 93.5 | Y | N |  | 0.91 |  |  | 100 | 280 | 400 | 0.45 | 0.9 | 1.35 | 2.25 | 3.38 | 4.5 | 90.2 | 92.9 | 93.1 | 93.5 | 93.4 | 92.3 | 93.1 | 90.7 | 93.7 | 94.1 | 94.2 | 94.2 | 93.9 | 94 | 87.6 | 91.5 | 92.9 | 93.4 | 93.3 | 92.9 | 92.9
Fronius USA | IG 4500-LV POS | 4500 W, Grid-tied unit with Integrated Disconnects and Performance Meter | 4.5 |  | 93.5 | Y | N |  | 0.91 |  |  | 100 | 280 | 400 | 0.45 | 0.9 | 1.35 | 2.25 | 3.38 | 4.5 | 90.2 | 92.9 | 93.1 | 93.5 | 93.4 | 92.3 | 93.1 | 90.7 | 93.7 | 94.1 | 94.2 | 94.2 | 93.9 | 94 | 87.6 | 91.5 | 92.9 | 93.4 | 93.3 | 92.9 | 92.9
Fronius USA | Fronius Primo 5.0-1 208-240 [208V] | 5000 W, 208 Vac Utility Interactive Inverter with arc detector and meter | 5 | 208 | 96.5 | Y | N |  | 0.41 |  |  | 100 | 650 | 800 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 89.4 | 93.8 | 94.8 | 95.8 | 96 | 96 | 95.4 | 92.5 | 96 | 96.8 | 97.5 | 97.6 | 97.6 | 97.2 | 89.3 | 94.6 | 96 | 97 | 97.3 | 97.4 | 96.6
Fronius USA | Fronius Primo 5.0-1 208-240 [240V] | 5000 W, 240 Vac Utility Interactive Inverter with arc detector and meter | 5 | 240 | 96.5 | Y | N |  | 0.55 |  |  | 100 | 660 | 800 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 89 | 93.2 | 94.6 | 95.6 | 95.9 | 96 | 95.3 | 91.6 | 95.4 | 96.4 | 97.1 | 97.4 | 97.4 | 96.9 | 92.3 | 96 | 97 | 97.7 | 97.9 | 97.9 | 97.4
Fronius USA | IG Plus 5.0-1 UNI [208V] | 5000 W, 208 Vac Utility Interactive Inverter with arc detector and meter | 5 | 208 | 95.5 | Y | N |  | 0.71 |  |  | 100 | 366 | 480 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 93.1 | 95 | 95.1 | 95.5 | 95.1 | 94.7 | 95.1 | 93.8 | 95.1 | 95.6 | 95.9 | 95.9 | 95.8 | 95.7 | 93.1 | 94.2 | 95 | 95.1 | 95.3 | 95.3 | 95.1
Fronius USA | IG Plus 5.0-1 UNI [240V] | 5000 W, 240 Vac Utility Interactive Inverter with arc detector and meter | 5 | 240 | 95.5 | Y | N |  | 0.76 |  |  | 100 | 390 | 480 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 93.2 | 95.1 | 95.6 | 95.8 | 95.7 | 95.5 | 95.6 | 94.1 | 95.2 | 96 | 96.1 | 96.3 | 96.2 | 96 | 93.4 | 94.8 | 95.3 | 95.5 | 95.8 | 95.8 | 95.5
Fronius USA | IG Plus 5.0-1 UNI [277V] | 5000 W, 277 Vac Utility Interactive Inverter with arc detector and meter | 5 | 277 | 96 | Y | N |  | 1.02 |  |  | 100 | 330 | 480 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 93.2 | 95.3 | 95.8 | 96 | 96.1 | 96 | 95.9 | 93.6 | 95.3 | 96 | 96.1 | 96.4 | 96.4 | 96.1 | 93.5 | 95.2 | 95.6 | 95.7 | 96 | 96.1 | 95.8
Fronius USA | IG Plus A 5.0 [208V] | 5000 W, 208 Vac Utility Interactive Inverter, Same as Series V with arc detector | 5 | 208 | 95.5 | Y | N |  | 0.6 | 5 | 0.6 | 100 | 366 | 480 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 93.3 | 95 | 95.2 | 95.4 | 95.3 | 94.9 | 95.2 | 94 | 95.3 | 95.7 | 95.8 | 95.9 | 95.8 | 95.7 | 93.2 | 94.2 | 95 | 95.3 | 95.5 | 95.5 | 95.2
Fronius USA | IG Plus A 5.0 [240V] | 5000 W, 240 Vac Utility Interactive Inverter, Same as Series V with arc detector | 5 | 240 | 95.5 | Y | N |  | 0.8 | 5 | 0.8 | 100 | 390 | 480 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 93.2 | 95.3 | 95.7 | 95.8 | 95.8 | 95.7 | 95.7 | 93.8 | 95.2 | 95.8 | 96.1 | 96.3 | 96.2 | 96 | 93.4 | 94.5 | 95.4 | 95.4 | 95.9 | 95.9 | 95.5
Fronius USA | IG Plus A 5.0 [277V] | 5000 W, 277 Vac Utility Interactive Inverter, Same as Series V with arc detector | 5 | 277 | 96 | Y | N |  | 1.1 | 5 | 1.1 | 100 | 330 | 480 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 93.2 | 95.3 | 95.9 | 95.9 | 96.2 | 96.1 | 95.9 | 93.4 | 95.2 | 96 | 96.3 | 96.5 | 96.5 | 96.2 | 93.3 | 95.1 | 95.6 | 95.6 | 96 | 96.3 | 95.7
Fronius USA | IG Plus V 5.0 [208V] | 5000 W, 208 Vac Utility Interactive Inverter | 5 | 208 | 95.5 | Y | N |  | 0.6 | 5 | 0.6 | 100 | 366 | 480 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 93.34 | 95.03 | 95.2 | 95.44 | 95.25 | 94.92 | 95.18 | 93.97 | 95.26 | 95.65 | 95.77 | 95.93 | 95.78 | 95.74 | 93.18 | 94.2 | 94.99 | 95.26 | 95.45 | 95.45 | 95.2
Fronius USA | IG Plus V 5.0 [240V] | 5000 W, 240 Vac Utility Interactive Inverter | 5 | 240 | 95.5 | Y | N |  | 0.8 | 5 | 0.8 | 100 | 390 | 480 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 93.16 | 95.32 | 95.66 | 95.84 | 95.81 | 95.66 | 95.66 | 93.84 | 95.24 | 95.83 | 96.07 | 96.25 | 96.24 | 96.02 | 93.42 | 94.51 | 95.36 | 95.35 | 95.85 | 95.91 | 95.52
Fronius USA | IG Plus V 5.0 [277V] | 5000 W, 277 Vac Utility Interactive Inverter | 5 | 277 | 96 | Y | N |  | 1.1 | 5 | 1.1 | 100 | 330 | 480 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 93.16 | 95.3 | 95.92 | 95.92 | 96.2 | 96.13 | 95.94 | 93.36 | 95.17 | 95.97 | 96.32 | 96.45 | 96.45 | 96.18 | 93.31 | 95.08 | 95.59 | 95.57 | 96.02 | 96.25 | 95.73
Fronius USA | IG 5100 NEG | 5100 W Grid-tied unit with Integrated Disconnects and Performance Meter | 5.1 |  | 94.5 | Y | N |  | 0.91 |  |  | 100 | 280 | 400 | 0.51 | 1.02 | 1.53 | 2.55 | 3.83 | 5.1 | 91.8 | 93.8 | 94.2 | 94.5 | 94.4 | 93.5 | 94.2 | 92.3 | 94.6 | 95 | 95.2 | 95 | 94.2 | 94.9 | 89.2 | 92.6 | 93.6 | 94.2 | 94.1 | 93.6 | 93.7
Fronius USA | IG 5100 POS | 5100 W Grid-tied unit with Integrated Disconnects and Performance Meter | 5.1 |  | 94.5 | Y | N |  | 0.91 |  |  | 100 | 280 | 400 | 0.51 | 1.02 | 1.53 | 2.55 | 3.83 | 5.1 | 91.8 | 93.8 | 94.2 | 94.5 | 94.4 | 93.5 | 94.2 | 92.3 | 94.6 | 95 | 95.2 | 95 | 94.2 | 94.9 | 89.2 | 92.6 | 93.6 | 94.2 | 94.1 | 93.6 | 93.7
Fronius USA | Fronius Primo 6.0-1 208-240 [208V] | 6000 W, 208 Vac Utility Interactive Inverter with arc detector and meter | 6 | 208 | 96.5 | Y | N |  | 0.41 |  |  | 100 | 660 | 800 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 90.7 | 94.4 | 95.2 | 95.9 | 96 | 95.9 | 95.6 | 93.5 | 96.5 | 97.1 | 97.6 | 97.6 | 97.6 | 97.3 | 91 | 95.4 | 96.4 | 97.2 | 97.3 | 97.4 | 96.8
Fronius USA | Fronius Primo 6.0-1 208-240 [240V] | 6000 W, 240 Vac Utility Interactive Inverter with arc detector and meter | 6 | 240 | 96.5 | Y | N |  | 0.55 |  |  | 100 | 660 | 800 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 89.8 | 93.6 | 94.9 | 95.8 | 96 | 96 | 95.4 | 91.4 | 95.3 | 96.3 | 97 | 97.3 | 97.3 | 96.8 | 91.7 | 95.7 | 96.7 | 97.5 | 97.7 | 97.7 | 97.2
Fronius USA | IG Plus 6.0-1 UNI [208V] | 6000 W, 208 Vac Utility Interactive Inverter | 6 | 208 | 95.5 | Y | N |  | 0.71 |  |  | 100 | 366 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 94.1 | 95.3 | 95.1 | 95.4 | 95 | 94.2 | 95 | 95.1 | 95.8 | 95.9 | 96.1 | 96 | 95.6 | 95.9 | 94.5 | 95.1 | 95.4 | 95.5 | 95.4 | 95.2 | 95.3
Fronius USA | IG Plus 6.0-1 UNI [240V] | 6000 W, 240 Vac Utility Interactive Inverter | 6 | 240 | 96 | Y | N |  | 0.76 |  |  | 100 | 390 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 93.8 | 95.5 | 95.6 | 95.9 | 95.7 | 95.1 | 95.6 | 94.8 | 95.7 | 96.1 | 96.3 | 96.3 | 96.1 | 96.2 | 94.4 | 95.2 | 95.6 | 95.8 | 95.9 | 95.8 | 95.7
Fronius USA | IG Plus 6.0-1 UNI [277V] | 6000 W, 277 Vac Utility Interactive Inverter | 6 | 277 | 96 | Y | N |  | 1.02 |  |  | 100 | 330 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 93.8 | 95.5 | 95.9 | 96.1 | 96.1 | 95.7 | 95.9 | 94.3 | 95.7 | 96.1 | 96.3 | 96.4 | 96.3 | 96.2 | 94.4 | 95.3 | 95.9 | 96 | 96.2 | 96.2 | 96
Fronius USA | IG Plus A 6.0 [208V] | 6000 W, 208 Vac Utility Interactive Inverter, Same as Series V with arc detector | 6 | 208 | 95.5 | Y | N |  | 0.6 | 6 | 0.6 | 100 | 366 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 93.7 | 95.1 | 95.1 | 95.4 | 95.1 | 94.5 | 95.1 | 94.1 | 95.3 | 95.7 | 95.9 | 95.9 | 95.5 | 95.7 | 93.4 | 94.7 | 95.2 | 95.3 | 95.4 | 95.3 | 95.2
Fronius USA | IG Plus A 6.0 [240V] | 6000 W, 240 Vac Utility Interactive Inverter, Same as Series V with arc detector | 6 | 240 | 96 | Y | N |  | 0.8 | 6 | 0.8 | 100 | 390 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 93.9 | 95.5 | 95.7 | 95.9 | 95.8 | 95.3 | 95.7 | 94.6 | 95.5 | 96.1 | 96.1 | 96.3 | 96.1 | 96.1 | 93.9 | 95 | 95.7 | 95.6 | 95.9 | 95.9 | 95.7
Fronius USA | IG Plus A 6.0 [277V] | 6000 W, 277 Vac Utility Interactive Inverter, Same as Series V with arc detector | 6 | 277 | 96 | Y | N |  | 1.1 | 6 | 1.1 | 100 | 330 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 93.8 | 95.6 | 96.1 | 96.2 | 96.2 | 96 | 96 | 94.2 | 95.7 | 96.3 | 96.3 | 96.5 | 96.3 | 96.3 | 94.2 | 95.2 | 95.9 | 95.9 | 96.2 | 96.3 | 96
Fronius USA | IG Plus V 6.0 [208V] | 6000 W, 208 Vac Utility Interactive Inverter | 6 | 208 | 95.5 | Y | N |  | 0.6 | 6 | 0.6 | 100 | 366 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 93.72 | 95.06 | 95.09 | 95.38 | 95.12 | 94.52 | 95.08 | 94.07 | 95.31 | 95.73 | 95.86 | 95.85 | 95.45 | 95.72 | 93.4 | 94.66 | 95.15 | 95.3 | 95.4 | 95.26 | 95.23
Fronius USA | IG Plus V 6.0 [240V] | 6000 W, 240 Vac Utility Interactive Inverter | 6 | 240 | 96 | Y | N |  | 0.8 | 6 | 0.8 | 100 | 390 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 93.91 | 95.48 | 95.68 | 95.9 | 95.76 | 95.32 | 95.67 | 94.6 | 95.53 | 96.05 | 96.11 | 96.25 | 96.1 | 96.09 | 93.9 | 95.03 | 95.72 | 95.58 | 95.86 | 95.89 | 95.66
Fronius USA | IG Plus V 6.0 [277V] | 6000 W, 277 Vac Utility Interactive Inverter | 6 | 277 | 96 | Y | N |  | 1.1 | 6 | 1.1 | 100 | 330 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 93.77 | 95.63 | 96.05 | 96.16 | 96.18 | 95.95 | 96.03 | 94.23 | 95.73 | 96.25 | 96.32 | 96.46 | 96.33 | 96.27 | 94.15 | 95.17 | 95.87 | 95.85 | 96.18 | 96.33 | 95.95
Fronius USA | IG Plus 7.5-1 UNI [208V] | 7500 W, 208 Vac Utility Interactive Inverter | 7.5 | 208 | 95 | Y | N |  | 0.71 |  |  | 100 | 366 | 480 | 0.75 | 1.5 | 2.25 | 3.75 | 5.63 | 7.5 | 94.4 | 95.2 | 94.7 | 95.1 | 94.4 | 93 | 94.6 | 95 | 95.8 | 95.7 | 96 | 95.7 | 94.8 | 95.7 | 94.2 | 95.2 | 95.3 | 95.4 | 95.2 | 94.6 | 95.2
Fronius USA | IG Plus 7.5-1 UNI [240V] | 7500 W, 240 Vac Utility Interactive Inverter | 7.5 | 240 | 95.5 | Y | N |  | 0.76 |  |  | 100 | 390 | 480 | 0.75 | 1.5 | 2.25 | 3.75 | 5.63 | 7.5 | 94.4 | 95.5 | 95.3 | 95.7 | 95.3 | 94.3 | 95.3 | 94.8 | 95.8 | 96.1 | 96.2 | 96.1 | 95.7 | 96 | 94.4 | 95.4 | 95.6 | 95.7 | 95.8 | 95.5 | 95.6
Fronius USA | IG Plus 7.5-1 UNI [277V] | 7500 W, 277 Vac Utility Interactive Inverter | 7.5 | 277 | 96 | Y | N |  | 1.02 |  |  | 100 | 330 | 480 | 0.75 | 1.5 | 2.25 | 3.75 | 5.63 | 7.5 | 94 | 95.7 | 95.8 | 96.1 | 95.9 | 95.2 | 95.8 | 94.5 | 95.9 | 96.2 | 96.4 | 96.3 | 95.9 | 96.2 | 94.4 | 95.5 | 96 | 96.1 | 96.2 | 96.1 | 96
Fronius USA | IG Plus A 7.5 [208V] | 7500 W, 208 Vac Utility Interactive Inverter, Same as Series V with arc detector | 7.5 | 208 | 95 | Y | N |  | 0.6 | 7.5 | 0.6 | 100 | 366 | 480 | 0.75 | 1.5 | 2.25 | 3.75 | 5.63 | 7.5 | 94.2 | 95.2 | 95 | 95.2 | 94.7 | 93.6 | 94.8 | 94.5 | 95.7 | 95.7 | 95.9 | 95.6 | 94.9 | 95.6 | 93 | 95.1 | 95.4 | 95.4 | 95.3 | 94.9 | 95.2
Fronius USA | IG Plus A 7.5 [240V] | 7500 W, 240 Vac Utility Interactive Inverter, Same as Series V with arc detector | 7.5 | 240 | 95.5 | Y | N |  | 0.8 | 7.5 | 0.8 | 100 | 390 | 480 | 0.75 | 1.5 | 2.25 | 3.75 | 5.63 | 7.5 | 94.4 | 95.6 | 95.6 | 95.8 | 95.5 | 94.7 | 95.5 | 94.5 | 95.9 | 96.1 | 96.2 | 96.2 | 95.7 | 96.1 | 94 | 95.3 | 95.7 | 95.8 | 95.9 | 95.6 | 95.7
Fronius USA | IG Plus A 7.5 [277V] | 7500 W, 277 Vac Utility Interactive Inverter, Same as Series V with arc detector | 7.5 | 277 | 96 | Y | N |  | 1.1 | 7.5 | 1.1 | 100 | 330 | 480 | 0.75 | 1.5 | 2.25 | 3.75 | 5.63 | 7.5 | 94.1 | 95.7 | 95.9 | 96.2 | 96 | 95.5 | 95.9 | 94.3 | 95.8 | 96.1 | 96.4 | 96.3 | 96 | 96.1 | 93.9 | 95.3 | 95.8 | 96 | 96.2 | 96.1 | 95.9
Fronius USA | IG Plus V 7.5 [208V] | 7500 W, 208 Vac Utility Interactive Inverter | 7.5 | 208 | 95 | Y | N |  | 0.6 | 7.5 | 0.6 | 100 | 366 | 480 | 0.75 | 1.5 | 2.25 | 3.75 | 5.625 | 7.5 | 94.23 | 95.18 | 95 | 95.19 | 94.68 | 93.6 | 94.78 | 94.47 | 95.69 | 95.69 | 95.89 | 95.6 | 94.94 | 95.6 | 93.01 | 95.11 | 95.35 | 95.4 | 95.31 | 94.87 | 95.21
Fronius USA | IG Plus V 7.5 [240V] | 7500 W, 240 Vac Utility Interactive Inverter | 7.5 | 240 | 95.5 | Y | N |  | 0.8 | 7.5 | 0.8 | 100 | 390 | 480 | 0.75 | 1.5 | 2.25 | 3.75 | 5.625 | 7.5 | 94.37 | 95.6 | 95.61 | 95.78 | 95.46 | 94.73 | 95.47 | 94.49 | 95.9 | 96.06 | 96.22 | 96.16 | 95.73 | 96.06 | 93.98 | 95.29 | 95.68 | 95.83 | 95.86 | 95.61 | 95.71
Fronius USA | IG Plus V 7.5 [277V] | 7500 W, 277 Vac Utility Interactive Inverter | 7.5 | 277 | 96 | Y | N |  | 1.1 | 7.5 | 1.1 | 100 | 330 | 480 | 0.75 | 1.5 | 2.25 | 3.75 | 5.625 | 7.5 | 94.05 | 95.73 | 95.93 | 96.15 | 95.95 | 95.45 | 95.88 | 94.27 | 95.84 | 96.09 | 96.36 | 96.26 | 95.96 | 96.14 | 93.86 | 95.28 | 95.81 | 95.97 | 96.16 | 96.11 | 95.94
Fronius USA | Fronius Primo 7.6-1 208-240 [208V] | 7600 W, 208 Vac Utility Interactive Inverter with arc detector and meter | 7.6 | 208 | 97 | Y | N |  | 0.41 |  |  | 100 | 660 | 800 | 0.76 | 1.52 | 2.28 | 3.8 | 5.7 | 7.6 | 92.7 | 95.1 | 95.8 | 96.1 | 96.1 | 95.8 | 95.8 | 96 | 97.4 | 97.7 | 97.8 | 97.7 | 97.6 | 97.7 | 94.1 | 96.7 | 97.3 | 97.6 | 97.5 | 97.4 | 97.3
Fronius USA | Fronius Primo 7.6-1 208-240 [240V] | 7600 W, 240 Vac Utility Interactive Inverter with arc detector and meter | 7.6 | 240 | 97 | Y | N |  | 0.55 |  |  | 100 | 660 | 800 | 0.76 | 1.52 | 2.28 | 3.8 | 5.7 | 7.6 | 91.6 | 94.8 | 95.5 | 96 | 96.1 | 95.9 | 95.7 | 94 | 96.4 | 97 | 97.4 | 97.5 | 97.4 | 97.2 | 94.6 | 97 | 97.6 | 97.9 | 97.9 | 97.8 | 97.7
Fronius USA | Fronius Primo 8.2-1 208-240 [208V] | 7900 W, 208 Vac Utility Interactive Inverter with arc detector and meter | 7.9 | 208 | 97 | Y | N |  | 0.41 |  |  | 100 | 660 | 800 | 0.79 | 1.58 | 2.37 | 3.95 | 5.93 | 7.9 | 93 | 95.3 | 95.9 | 96.2 | 96.2 | 95.9 | 96 | 95.8 | 97.3 | 97.7 | 97.8 | 97.8 | 97.5 | 97.7 | 94 | 96.7 | 97.3 | 97.6 | 97.6 | 97.4 | 97.3
Fronius USA | Fronius Primo 8.2-1 208-240 [240V] | 8200 W, 240 Vac Utility Interactive Inverter with arc detector and meter | 8.2 | 240 | 97 | Y | N |  | 0.55 |  |  | 100 | 660 | 800 | 0.82 | 1.64 | 2.46 | 4.1 | 6.15 | 8.2 | 92.1 | 94.9 | 95.7 | 96.2 | 96.2 | 96.1 | 95.9 | 94.2 | 96.6 | 97.1 | 97.4 | 97.4 | 97.4 | 97.2 | 94.7 | 97.1 | 97.6 | 97.9 | 97.9 | 97.8 | 97.7
Fronius USA | Fronius Primo 10.0-1 [208V] | 9995 W, 208 Vac Utility Interactive Inverter with arc detector | 9.995 | 208 | 96.5 | Y | N |  | 0.24 |  |  | 100 | 660 | 800 | 1 | 2 | 3 | 5 | 7.5 | 10 | 92 | 94.7 | 95.1 | 95.6 | 95.6 | 95.5 | 95.3 | 94.5 | 97.4 | 96.8 | 97.3 | 97.3 | 97.4 | 97.1 | 93.3 | 97.1 | 96.5 | 97 | 97.3 | 97.3 | 97
Fronius USA | Fronius Primo 10.0-1 [240V] | 9995 W, 240 Vac Utility Interactive Inverter with arc detector | 9.995 | 240 | 96.5 | Y | N |  | 0.32 |  |  | 100 | 655 | 800 | 1 | 2 | 3 | 5 | 7.5 | 10 | 91.4 | 94.3 | 94.8 | 95.4 | 95.6 | 95.6 | 95.2 | 93.5 | 95.8 | 96.3 | 96.9 | 97.1 | 97 | 96.7 | 95.6 | 97 | 97.2 | 97.6 | 97.7 | 97.5 | 97.5
Fronius USA | Fronius Symo 10.0-3 208-240 [208V] | 9.995 kW, 208 Vac Utility Interactive Inverter | 9.995 | 208 | 96.5 | Y | N |  | 0.81 |  |  | 100 | 370 | 480 | 1 | 2 | 3 | 5 | 7.5 | 10 | 94 | 95.6 | 96.1 | 96.2 | 96.2 | 96 | 96.1 | 95.4 | 96.8 | 97 | 97.1 | 97.1 | 96.9 | 97 | 94.8 | 96.4 | 96.7 | 96.9 | 96.9 | 96.7 | 96.7
Fronius USA | Fronius Symo 10.0-3 208-240 [240V] | 9.995 kW, 240 Vac Utility Interactive Inverter | 9.995 | 240 | 96.5 | Y | N |  | 0.8 |  |  | 100 | 370 | 480 | 1 | 2 | 3 | 5 | 7.5 | 10 | 94 | 95.6 | 96.1 | 96.2 | 96.2 | 96 | 96.1 | 95.4 | 96.8 | 97 | 97.1 | 97.1 | 96.9 | 97 | 94.8 | 96.4 | 96.7 | 96.9 | 96.9 | 96.7 | 96.7
Fronius USA | Fronius Symo 10.0-3 480 [480V] | 9.995 kW, 480 Vac Utility Interactive Inverter | 9.995 | 480 | 96.5 | Y | N |  | 0.86 |  |  | 100 | 670 | 800 | 1 | 2 | 3 | 5 | 7.5 | 10 | 89.6 | 93.7 | 94.8 | 95.3 | 96 | 96.2 | 95.3 | 91.8 | 95.2 | 96.1 | 96.7 | 97.2 | 97.3 | 96.6 | 92.9 | 96.1 | 96.9 | 97.3 | 97.7 | 97.8 | 97.2
Fronius USA | IG Plus 10.0-1 UNI [208V] | 9995W, 208 Vac Utility Interactive Inverter | 9.995 | 208 | 95 | Y | N |  | 0.64 |  |  | 100 | 366 | 480 | 0.9995 | 1.999 | 2.999 | 4.998 | 7.496 | 9.995 | 93.8 | 94.5 | 95.2 | 95.3 | 94.9 | 93.8 | 94.9 | 93.5 | 95.2 | 95.6 | 95.9 | 95.8 | 95.3 | 95.6 | 92.5 | 94.4 | 94.8 | 95.2 | 95.2 | 95 | 95
Fronius USA | IG Plus 10.0-1 UNI [240V] | 9995W, 240 Vac Utility Interactive Inverter | 9.995 | 240 | 95.5 | Y | N |  | 0.85 |  |  | 100 | 390 | 480 | 0.9995 | 1.999 | 2.999 | 4.998 | 7.496 | 9.995 | 94.1 | 95.1 | 95.7 | 95.8 | 95.5 | 94.9 | 95.5 | 93.7 | 95.5 | 95.9 | 96.2 | 96.2 | 96 | 96 | 93.2 | 95 | 95.3 | 95.6 | 95.7 | 95.6 | 95.5
Fronius USA | IG Plus 10.0-1 UNI [277V] | 9995W, 277 Vac Utility Interactive Inverter | 9.995 | 277 | 96 | Y | N |  | 1.13 |  |  | 100 | 330 | 480 | 0.9995 | 1.999 | 2.999 | 4.998 | 7.496 | 9.995 | 94.2 | 95.7 | 95.9 | 96.1 | 96 | 95.6 | 95.9 | 94.5 | 96 | 96.1 | 96.3 | 96.4 | 96.3 | 96.3 | 94.5 | 95.6 | 95.7 | 96 | 96.1 | 96.2 | 96
Fronius USA | IG Plus V 10.0-3 Delta [208V] | 10000 W, 208 Vac 3-Phase Utility Interactive Inverter | 9.995 | 208 | 95.5 | Y | N |  | 0.9 | 9.995 | 0.9 | 100 | 366 | 480 | 1 | 2 | 3 | 5 | 7.5 | 10 | 94.1 | 94.7 | 95.3 | 95.3 | 95 | 94.1 | 95 | 94.3 | 95.4 | 95.7 | 96 | 95.8 | 95.2 | 95.7 | 93.3 | 95 | 95.1 | 95.4 | 95.4 | 95.1 | 95.3
Fronius USA | IG Plus V 10.0-3 Delta [240V] | 10000 W, 240 Vac 3-Phase Utility Interactive Inverter | 9.995 | 240 | 95.5 | Y | N |  | 1.2 | 9.995 | 1.2 | 100 | 366 | 480 | 1 | 2 | 3 | 5 | 7.5 | 10 | 94.5 | 95.5 | 95.7 | 95.9 | 95.7 | 95.1 | 95.6 | 94.1 | 95.5 | 95.7 | 95.9 | 95.9 | 95.6 | 95.8 | 93.5 | 95.4 | 95.4 | 95.7 | 95.9 | 95.8 | 95.7
Fronius USA | IG Plus A 10.0 [208V] | 10000 W, 208 Vac Utility Interactive Inverter, Same as Series V with arc detector | 10 | 208 | 95 | Y | N |  | 0.77 | 10 | 0.77 | 100 | 366 | 480 | 1 | 2 | 3 | 5 | 7.5 | 10 | 94 | 94.6 | 95.1 | 95.2 | 94.8 | 94 | 94.8 | 93.9 | 95.3 | 95.6 | 95.8 | 95.6 | 95.1 | 95.6 | 92.8 | 94.8 | 94.9 | 95.3 | 95.3 | 95 | 95.1
Fronius USA | IG Plus A 10.0 [240V] | 10000 W, 240 Vac Utility Interactive Inverter, Same as Series V with arc detector | 10 | 240 | 95.5 | Y | N |  | 1 | 10 | 1 | 100 | 390 | 480 | 1 | 2 | 3 | 5 | 7.5 | 10 | 94.2 | 95.2 | 95.6 | 95.7 | 95.5 | 94.9 | 95.5 | 93.8 | 95.6 | 95.8 | 96 | 96.1 | 95.9 | 95.9 | 93.2 | 95.1 | 95.2 | 95.6 | 95.8 | 95.7 | 95.5
Fronius USA | IG Plus A 10.0 [277V] | 10000 W, 277 Vac Utility Interactive Inverter, Same as Series V with arc detector | 10 | 277 | 96 | Y | N |  | 1.36 | 10 | 1.36 | 100 | 330 | 480 | 1 | 2 | 3 | 5 | 7.5 | 10 | 94.3 | 95.7 | 95.9 | 96.1 | 96 | 95.6 | 95.9 | 94.1 | 95.9 | 96 | 96.2 | 96.3 | 96.1 | 96.1 | 93.7 | 95.5 | 95.4 | 95.8 | 96.1 | 96.2 | 95.8
Fronius USA | IG Plus A 10.0-3 Delta [208V] | 10000 W, 208 Vac Utility Interactive Inverter, Same as Series V with arc detector | 10 | 208 | 95.5 | Y | N |  | 0.9 | 10 | 0.9 | 100 | 366 | 480 | 1 | 2 | 3 | 5 | 7.5 | 10 | 94.1 | 94.7 | 95.3 | 95.3 | 95 | 94.1 | 95 | 94.3 | 95.4 | 95.7 | 96 | 95.8 | 95.2 | 95.7 | 93.3 | 95 | 95.1 | 95.4 | 95.4 | 95.1 | 95.3
Fronius USA | IG Plus A 10.0-3 Delta [240V] | 10000 W, 240 Vac Utility Interactive Inverter, Same as Series V with arc detector | 10 | 240 | 95.5 | Y | N |  | 1.2 | 10 | 1.2 | 100 | 366 | 480 | 1 | 2 | 3 | 5 | 7.5 | 10 | 94.5 | 95.5 | 95.7 | 95.9 | 95.7 | 95.1 | 95.6 | 94.1 | 95.5 | 95.7 | 95.9 | 95.9 | 95.6 | 95.8 | 93.5 | 95.4 | 95.4 | 95.7 | 95.9 | 95.8 | 95.7
Fronius USA | IG Plus V 10.0 [208V] | 10000 W, 208 Vac Utility Interactive Inverter | 10 | 208 | 95 | Y | N |  | 0.77 | 10 | 0.77 | 100 | 366 | 480 | 1 | 2 | 3 | 5 | 7.5 | 10 | 93.96 | 94.59 | 95.13 | 95.15 | 94.79 | 93.95 | 94.82 | 93.94 | 95.27 | 95.61 | 95.79 | 95.64 | 95.11 | 95.55 | 92.8 | 94.78 | 94.89 | 95.27 | 95.3 | 95 | 95.1
Fronius USA | IG Plus V 10.0 [240V] | 10000 W, 240 Vac Utility Interactive Inverter | 10 | 240 | 95.5 | Y | N |  | 1 | 10 | 1 | 100 | 390 | 480 | 1 | 2 | 3 | 5 | 7.5 | 10 | 94.18 | 95.24 | 95.61 | 95.7 | 95.51 | 94.94 | 95.47 | 93.77 | 95.61 | 95.8 | 96.04 | 96.12 | 95.86 | 95.93 | 93.16 | 95.13 | 95.2 | 95.55 | 95.79 | 95.7 | 95.52
Fronius USA | IG Plus V 10.0 [277V] | 10000 W, 277 Vac Utility Interactive Inverter | 10 | 277 | 96 | Y | N |  | 1.36 | 10 | 1.36 | 100 | 330 | 480 | 1 | 2 | 3 | 5 | 7.5 | 10 | 94.28 | 95.67 | 95.87 | 96.05 | 95.98 | 95.59 | 95.88 | 94.07 | 95.87 | 96.02 | 96.23 | 96.3 | 96.08 | 96.13 | 93.68 | 95.46 | 95.44 | 95.8 | 96.12 | 96.16 | 95.84
Fronius USA | Fronius Primo 11.4-1 [208V] | 11,400W, 208 Vac Utility Interactive Inverter with arc detector | 11.4 | 208 | 96.5 | Y | N |  | 0.24 |  |  | 240 | 660 | 800 | 1.14 | 2.28 | 3.42 | 5.7 | 8.55 | 11.4 | 93 | 94.9 | 95.4 | 95.8 | 95.8 | 95.7 | 95.6 | 95.4 | 97 | 97.3 | 97.4 | 97.4 | 97.4 | 97.3 | 94.5 | 96.4 | 96.9 | 97.2 | 97.2 | 97.3 | 97.1
Fronius USA | Fronius Primo 11.4-1 [240V] | 11,400W, 240 Vac Utility Interactive Inverter with arc detector | 11.4 | 240 | 96.5 | Y | N |  | 0.32 |  |  | 240 | 660 | 800 | 1.14 | 2.28 | 3.42 | 5.7 | 8.55 | 11.4 | 92.1 | 94.8 | 95.3 | 95.8 | 95.9 | 95.8 | 95.6 | 93.7 | 96.1 | 96.6 | 97 | 97.1 | 97.1 | 96.9 | 94.8 | 96.9 | 97.4 | 97.6 | 97.6 | 97.6 | 97.4
Fronius USA | IG Plus 11.4-1 UNI [208V] | 11400 W, 208 Vac Utility Interactive Inverter | 11.4 | 208 | 95.5 | Y | N |  | 0.64 |  |  | 230 | 366 | 480 | 1.14 | 2.28 | 3.42 | 5.7 | 8.55 | 11.4 | 94.7 | 94.6 | 95.3 | 95.3 | 94.6 | 93.2 | 94.7 | 95.1 | 95.7 | 96 | 96 | 95.7 | 95 | 95.8 | 94.1 | 95.1 | 95.3 | 95.5 | 95.3 | 94.8 | 95.3
Fronius USA | IG Plus 11.4-1 UNI [240V] | 11400 W, 240 Vac Utility Interactive Inverter | 11.4 | 240 | 96 | Y | N |  | 0.85 |  |  | 230 | 390 | 480 | 1.14 | 2.28 | 3.42 | 5.7 | 8.55 | 11.4 | 94.7 | 95.2 | 95.7 | 95.8 | 95.4 | 94.5 | 95.4 | 94.6 | 95.9 | 96.2 | 96.2 | 96.2 | 95.9 | 96.1 | 94.2 | 95.4 | 95.6 | 95.8 | 95.8 | 95.7 | 95.7
Fronius USA | IG Plus 11.4-1 UNI [277V] | 11400 W, 277 Vac Utility Interactive Inverter | 11.4 | 277 | 96 | Y | N |  | 1.13 |  |  | 240 | 330 | 480 | 1.14 | 2.28 | 3.42 | 5.7 | 8.55 | 11.4 | 94.7 | 95.6 | 96 | 96.1 | 95.9 | 95.3 | 95.9 | 94.8 | 96 | 96.2 | 96.4 | 96.4 | 96 | 96.2 | 94.4 | 95.8 | 95.8 | 96.1 | 96.2 | 96 | 96
Fronius USA | IG Plus 11.4-3 Delta [208V] | 11400 W, 208 Vac 3-Phase Utility Interactive Inverter | 11.4 | 208 | 95 | Y | N |  | 0.9 |  |  | 230 | 365 | 480 | 1.14 | 2.28 | 3.42 | 5.7 | 8.55 | 11.4 | 94.2 | 94.3 | 95.1 | 95.1 | 94.4 | 93 | 94.55 | 94.4 | 95.3 | 95.8 | 95.9 | 95.6 | 94.9 | 95.59 | 93.4 | 94.6 | 95 | 95.3 | 95.2 | 94.7 | 95.05
Fronius USA | IG Plus 11.4-3 Delta [240V] | 11400 W, 240 Vac 3-Phase Utility Interactive Inverter | 11.4 | 240 | 95.5 | Y | N |  | 1 |  |  | 230 | 390 | 480 | 1.14 | 2.28 | 3.42 | 5.7 | 8.55 | 11.4 | 94.3 | 95 | 95.6 | 95.7 | 95.2 | 94.2 | 95.25 | 94.1 | 95.7 | 96 | 96.2 | 96.1 | 95.7 | 95.99 | 93.4 | 95.1 | 95.4 | 95.7 | 95.7 | 95.6 | 95.54
Fronius USA | IG Plus A 11.4 [208V] | 11400 W, 208 Vac Utility Interactive Inverter, Same as Series V with arc detector | 11.4 | 208 | 95 | Y | N |  | 0.77 | 11.4 | 0.77 | 230 | 366 | 480 | 1.14 | 2.28 | 3.42 | 5.7 | 8.55 | 11.4 | 94.4 | 94.6 | 95.1 | 95.1 | 94.5 | 93.3 | 94.6 | 94.6 | 95.3 | 95.7 | 95.8 | 95.4 | 94.8 | 95.5 | 93.3 | 95 | 95.2 | 95.3 | 95.2 | 94.7 | 95.1
Fronius USA | IG Plus A 11.4 [240V] | 11400 W, 240 Vac Utility Interactive Inverter, Same as Series V with arc detector | 11.4 | 240 | 95.5 | Y | N |  | 1 | 11.4 | 1 | 230 | 390 | 480 | 1.14 | 2.28 | 3.42 | 5.7 | 8.55 | 11.4 | 94.6 | 95.2 | 95.6 | 95.7 | 95.3 | 94.5 | 95.3 | 94.3 | 95.7 | 95.9 | 96.1 | 96 | 95.6 | 95.9 | 93.6 | 95.4 | 95.5 | 95.7 | 95.8 | 95.5 | 95.6
Fronius USA | IG Plus A 11.4 [277V] | 11400 W, 277 Vac Utility Interactive Inverter, Same as Series V with arc detector | 11.4 | 277 | 96 | Y | N |  | 1.36 | 11.4 | 1.36 | 230 | 330 | 480 | 1.14 | 2.28 | 3.42 | 5.7 | 8.55 | 11.4 | 94.7 | 95.7 | 95.9 | 96 | 95.8 | 95.3 | 95.8 | 94.5 | 95.9 | 96.1 | 96.3 | 96.2 | 95.9 | 96.1 | 93.9 | 95.7 | 95.7 | 96 | 96.1 | 96.1 | 95.9
Fronius USA | IG Plus A 11.4-3 Delta [208V] | 11400 W, 208 Vac 3-Phase Utility Interactive Inverter, Same as Series V with arc detector | 11.4 | 208 | 95 | Y | N |  | 0.77 | 11.4 | 0.77 | 230 | 366 | 480 | 1.14 | 2.28 | 3.42 | 5.7 | 8.55 | 11.4 | 94.4 | 94.6 | 95.1 | 95.1 | 94.5 | 93.3 | 94.6 | 94.6 | 95.3 | 95.7 | 95.8 | 95.4 | 94.8 | 95.5 | 93.3 | 95 | 95.2 | 95.3 | 95.2 | 94.7 | 95.1
Fronius USA | IG Plus A 11.4-3 Delta [240V] | 11400 W, 240 Vac 3-Phase Utility Interactive Inverter, Same as Series V with arc detector | 11.4 | 240 | 96 | Y | N |  | 1.2 | 11.4 | 1.2 | 230 | 390 | 480 | 1.14 | 2.28 | 3.42 | 5.7 | 8.55 | 11.4 | 94.7 | 95.4 | 95.8 | 95.8 | 95.5 | 94.7 | 95.5 | 94.5 | 95.8 | 96 | 96.3 | 96.2 | 95.8 | 96.1 | 94 | 95.4 | 95.5 | 95.8 | 95.9 | 95.7 | 95.7
Fronius USA | IG Plus V 11.4 [208V] | 11400 W, 208 Vac Utility Interactive Inverter | 11.4 | 208 | 95 | Y | N |  | 0.77 | 11.4 | 0.77 | 230 | 366 | 480 | 1.14 | 2.28 | 3.42 | 5.7 | 8.55 | 11.4 | 94.38 | 94.56 | 95.11 | 95.08 | 94.48 | 93.34 | 94.63 | 94.57 | 95.31 | 95.74 | 95.78 | 95.43 | 94.8 | 95.47 | 93.33 | 94.99 | 95.17 | 95.33 | 95.22 | 94.66 | 95.12
Fronius USA | IG Plus V 11.4 [240V] | 11400 W, 240 Vac Utility Interactive Inverter | 11.4 | 240 | 95.5 | Y | N |  | 1 | 11.4 | 1 | 230 | 390 | 480 | 1.14 | 2.28 | 3.42 | 5.7 | 8.55 | 11.4 | 94.59 | 95.19 | 95.62 | 95.67 | 95.28 | 94.5 | 95.33 | 94.33 | 95.72 | 95.9 | 96.12 | 96.01 | 95.61 | 95.92 | 93.56 | 95.36 | 95.49 | 95.7 | 95.77 | 95.51 | 95.6
Fronius USA | IG Plus V 11.4 [277V] | 11400 W, 277 Vac Utility Interactive Inverter | 11.4 | 277 | 96 | Y | N |  | 1.36 | 11.4 | 1.36 | 230 | 330 | 480 | 1.14 | 2.28 | 3.42 | 5.7 | 8.55 | 11.4 | 94.66 | 95.65 | 95.94 | 96.03 | 95.84 | 95.31 | 95.81 | 94.49 | 95.89 | 96.13 | 96.27 | 96.21 | 95.88 | 96.11 | 93.86 | 95.69 | 95.65 | 95.97 | 96.14 | 96.05 | 95.93
Fronius USA | IG Plus V 11.4-3 Delta [208V] | 11400 W, 208 Vac 3-Phase Utility Interactive Inverter | 11.4 | 208 | 95 | Y | N |  | 0.77 | 11.4 | 0.77 | 230 | 366 | 480 | 1.14 | 2.28 | 3.42 | 5.7 | 8.55 | 11.4 | 94.4 | 94.6 | 95.1 | 95.1 | 94.5 | 93.3 | 94.63 | 94.6 | 95.3 | 95.7 | 95.8 | 95.4 | 94.8 | 95.47 | 93.3 | 95 | 95.2 | 95.3 | 95.2 | 94.7 | 95.12
Fronius USA | IG Plus V 11.4-3 Delta [240V] | 11401 W, 240 Vac 3-Phase Utility Interactive Inverter | 11.4 | 240 | 96 | Y | N |  | 1.2 | 11.4 | 1.2 | 230 | 390 | 480 | 1.14 | 2.28 | 3.42 | 5.7 | 8.55 | 11.4 | 94.67 | 95.44 | 95.75 | 95.82 | 95.47 | 94.68 | 95.5 | 94.49 | 95.79 | 96.03 | 96.25 | 96.15 | 95.75 | 96.05 | 94.01 | 95.42 | 95.54 | 95.83 | 95.87 | 95.65 | 95.71
Fronius USA | Fronius Symo 12.0-3 208-240 [208V] | 11.995 kW, 208 Vac Utility Interactive Inverter | 12 | 208 | 96.5 | Y | N |  | 0.61 |  |  | 300 | 350 | 480 | 1.2 | 2.4 | 3.6 | 6 | 9 | 12 | 95.4 | 96.2 | 96.3 | 96.2 | 95.9 | 95.4 | 95.9 | 96.3 | 96.9 | 96.9 | 96.8 | 96.5 | 96.2 | 96.6 | 94.7 | 96.1 | 96.4 | 96.4 | 96.3 | 96 | 96.2
Fronius USA | Fronius Symo 12.0-3 208-240 [240V] | 11.995 kW, 240 Vac Utility Interactive Inverter | 12 | 240 | 96.5 | Y | N |  | 0.81 |  |  | 300 | 370 | 480 | 1.2 | 2.4 | 3.6 | 6 | 9 | 12 | 94.4 | 95.9 | 96.2 | 96.3 | 96.1 | 95.8 | 96.1 | 96 | 96.9 | 97.1 | 97.1 | 97 | 96.8 | 97 | 95.2 | 96.6 | 96.8 | 96.9 | 96.8 | 96.6 | 96.7
Fronius USA | IG Plus 12.0-3 WYE [277V] | 12000 W, 3-phase WYE 277 Vac Utility Interactive Inverter | 12 | 277 | 96 | Y | N |  | 1 |  |  | 240 | 330 | 480 | 1.2 | 2.4 | 3.6 | 6 | 9 | 12 | 94.7 | 95.5 | 95.9 | 96 | 95.8 | 95.1 | 95.8 | 94.7 | 95.9 | 96.1 | 96.3 | 96.3 | 95.8 | 96.2 | 94.3 | 95.7 | 95.8 | 96 | 96.2 | 96 | 96
Fronius USA | IG Plus A 12.0-3 WYE [277V] | 12000 W, 3-phase WYE 277 Vac Utility Interactive Inverter, Same as Series V with arc detector | 12 | 277 | 96 | Y | N |  | 0.5 | 12 | 0.5 | 240 | 330 | 480 | 1.2 | 2.4 | 3.6 | 6 | 9 | 12 | 92.6 | 95.2 | 96.2 | 96.3 | 96.1 | 95.4 | 95.9 | 92.5 | 95.7 | 96.2 | 96.6 | 96.5 | 96.1 | 96.2 | 94.4 | 95.6 | 95.8 | 96.2 | 96.4 | 96.3 | 96.2
Fronius USA | IG Plus V 12.0-3 WYE [277V] | 12000 W, 3-phase WYE 277 Vac Utility Interactive Inverter | 12 | 277 | 96 | Y | N |  | 0.5 | 12 | 0.5 | 240 | 330 | 480 | 1.2 | 2.4 | 3.6 | 6 | 9 | 12 | 92.62 | 95.2 | 96.16 | 96.32 | 96.05 | 95.44 | 95.91 | 92.45 | 95.69 | 96.17 | 96.56 | 96.45 | 96.06 | 96.22 | 94.43 | 95.61 | 95.78 | 96.24 | 96.43 | 96.29 | 96.19
Fronius USA | Fronius Primo 12.5-1 [208V] | 12,500W, 208 Vac Utility Interactive Inverter with arc detector | 12.5 | 208 | 96.5 | Y | N |  | 0.24 |  |  | 260 | 665 | 800 | 1.25 | 2.5 | 3.75 | 6.25 | 9.38 | 12.5 | 92.5 | 95.1 | 95.5 | 95.9 | 95.9 | 95.6 | 95.6 | 95.3 | 96.9 | 97.3 | 97.5 | 97.3 | 97.3 | 97.2 | 94.5 | 96.6 | 97 | 97.2 | 97.1 | 97.2 | 97
Fronius USA | Fronius Primo 12.5-1 [240V] | 12,500W, 240 Vac Utility Interactive Inverter with arc detector | 12.5 | 240 | 96.5 | Y | N |  | 0.32 |  |  | 260 | 660 | 800 | 1.25 | 2.5 | 3.75 | 6.25 | 9.38 | 12.5 | 92.1 | 95 | 95.4 | 95.9 | 95.9 | 95.8 | 95.6 | 93.7 | 96.2 | 96.6 | 97 | 97.1 | 97.1 | 96.8 | 95.4 | 97.2 | 97.3 | 97.5 | 97.6 | 97.7 | 97.5
Fronius USA | Fronius Symo 12.5-3 480 [480V] | 12.495 kW, 480 Vac Utility Interactive Inverter | 12.5 | 480 | 97 | Y | N |  | 0.94 |  |  | 350 | 685 | 800 | 1.25 | 2.5 | 3.75 | 6.25 | 9.37 | 12.5 | 92.5 | 94.9 | 95.6 | 96 | 96.4 | 96.5 | 96 | 94.4 | 96.5 | 97 | 97.3 | 97.5 | 97.5 | 97.2 | 95.6 | 97.3 | 97.7 | 97.9 | 98 | 98 | 97.8
Fronius USA | Fronius Primo 15.0-1 [208V] | 13,750W, 208 Vac Utility Interactive Inverter with arc detector | 13.75 | 208 | 97 | Y | N |  | 0.24 |  |  | 320 | 680 | 800 | 1.38 | 2.75 | 4.13 | 6.88 | 10.31 | 13.75 | 93.3 | 95.7 | 96 | 96.3 | 96.2 | 96 | 96 | 95.9 | 97.1 | 97.4 | 97.4 | 97.4 | 97.2 | 97.3 | 95.1 | 96.8 | 97.1 | 97.2 | 97.2 | 97.1 | 97.1
Fronius USA | Fronius Primo 15.0-1 [240V] | 15,000W, 240 Vac Utility Interactive Inverter with arc detector | 15 | 240 | 97 | Y | N |  | 0.32 |  |  | 320 | 680 | 800 | 1.5 | 3 | 4.5 | 7.5 | 11.25 | 15 | 93.5 | 95.5 | 96 | 96.3 | 96.3 | 96.1 | 96.1 | 94.5 | 96.5 | 96.9 | 97.2 | 97.2 | 97 | 97 | 95.7 | 97.2 | 97.5 | 97.6 | 97.6 | 97.4 | 97.5
Fronius USA | Fronius Symo 15.0-3 [208V] | 15,000W, 208 Vac Utility Interactive Inverter with arc detector | 15 | 208 | 96.5 | Y | N |  | 0.43 |  |  | 325 | 445 | 800 | 1.5 | 3 | 4.5 | 7.5 | 11.25 | 15 | 96.1 | 97 | 97.1 | 97.1 | 96.9 | 96.7 | 96.9 | 95.3 | 96.4 | 96.6 | 96.7 | 96.5 | 96.2 | 96.5 | 92.7 | 94.9 | 95.4 | 95.6 | 95.5 | 95.3 | 95.4
Fronius USA | Fronius Symo 15.0-3 480 [480V] | 14.995 kW, 480 Vac Utility Interactive Inverter | 15 | 480 | 97 | Y | N |  | 1.03 |  |  | 350 | 685 | 800 | 1.5 | 3 | 4.5 | 7.5 | 11.25 | 15 | 92 | 94.9 | 95.6 | 96.2 | 96.5 | 96.4 | 96.1 | 93.5 | 96 | 96.7 | 97.2 | 97.4 | 97.4 | 97.1 | 94.6 | 96.8 | 97.4 | 97.8 | 97.9 | 97.9 | 97.6
Fronius USA | Fronius Symo 17.5-3 480 [480V] | 17.495 kW, 480 Vac Utility Interactive Inverter | 17.5 | 480 | 97.5 | Y | N |  | 1.03 |  |  | 400 | 700 | 800 | 1.75 | 3.5 | 5.25 | 8.75 | 13.12 | 17.5 | 92.7 | 95.3 | 95.8 | 96.5 | 96.6 | 96.7 | 96.3 | 95.7 | 97.4 | 97.8 | 98.1 | 98.1 | 98.2 | 98 | 94.8 | 96.9 | 97.4 | 97.7 | 97.8 | 97.8 | 97.6
Fronius USA | Fronius Symo 20.0-3 480 [480V] | 19995 W, 480 Vac Utility Interactive Inverter with arc detector and meter | 20 | 480 | 97 | Y | N |  | 1.03 |  |  | 450 | 712 | 800 | 2 | 4 | 6 | 10 | 15 | 20 | 93.1 | 95.5 | 96.1 | 96.7 | 96.8 | 96.8 | 96.5 | 95.1 | 97 | 97.5 | 97.9 | 98 | 98 | 97.7 | 94.5 | 96.7 | 97.3 | 97.7 | 97.7 | 97.8 | 97.5
Fronius USA | Fronius Symo 22.7-3 480 [480V] | 22.727 kW, 480 Vac Utility Interactive Inverter | 22.73 | 480 | 97.5 | Y | N |  | 1.03 |  |  | 500 | 720 | 800 | 2.27 | 4.55 | 6.82 | 11.36 | 17.05 | 22.73 | 94.3 | 96.2 | 96.7 | 97 | 97 | 96.9 | 96.8 | 96.4 | 97.6 | 97.8 | 98 | 98 | 98 | 97.9 | 95.9 | 97.3 | 97.7 | 97.8 | 97.9 | 97.8 | 97.7
Fronius USA | Fronius Symo 24.0-3 480 [480V] | 23.995 kW, 480 Vac Utility Interactive Inverter | 24 | 480 | 97.5 | Y | N |  | 1.03 |  |  | 500 | 725 | 800 | 2.4 | 4.8 | 7.2 | 12 | 18 | 24 | 94.3 | 96.1 | 96.6 | 97 | 97 | 97 | 96.8 | 96.2 | 97.5 | 97.8 | 98 | 98 | 97.9 | 97.9 | 95.8 | 97.2 | 97.6 | 97.8 | 97.8 | 97.7 | 97.7
Fronius USA | CL 33.3 Delta [208V] | 33.3 kW, 208 Vac Delta Utility Interactive Inverter | 33.3 | 208 | 94.5 | Y | N |  | 2.85 |  |  | 230 | 366 | 480 | 3.33 | 6.66 | 9.99 | 16.65 | 24.98 | 33.3 | 93.57 | 93.75 | 94.54 | 94.56 | 94.04 | 93.04 | 94.12 | 94.11 | 94.65 | 95.17 | 95.28 | 94.96 | 94.25 | 94.96 | 93.36 | 94.22 | 94.57 | 94.81 | 94.68 | 94.16 | 94.59
Fronius USA | CL 33.3 Delta [240V] | 33.3 kW, 240 Vac Delta Utility Interactive Inverter | 33.3 | 240 | 95 | Y | N |  | 3.53 |  |  | 230 | 390 | 480 | 3.33 | 6.66 | 9.99 | 16.65 | 24.98 | 33.3 | 94.09 | 94.75 | 95.13 | 95.25 | 94.86 | 94.11 | 94.9 | 94.44 | 95.29 | 95.54 | 95.76 | 95.61 | 95.14 | 95.55 | 93.81 | 95.15 | 95.03 | 95.41 | 95.29 | 95.02 | 95.21
Fronius USA | CL 36.0 Wye [277V] | 36 kW, 277 Vac Wye Utility Interactive Inverter | 36 | 277 | 95.5 | Y | N |  | 4.03 |  |  | 240 | 330 | 480 | 3.6 | 7.2 | 10.8 | 18 | 27 | 36 | 94.33 | 95.14 | 95.48 | 95.74 | 95.49 | 94.88 | 95.45 | 94.51 | 95.53 | 95.5 | 95.98 | 95.89 | 95.51 | 95.77 | 94.15 | 95.46 | 95.12 | 95.79 | 95.88 | 95.73 | 95.67
Fronius USA | CL 44.4 Delta [208V] | 44.4 kW, 208 Vac Delta Utility Interactive Inverter | 44.4 | 208 | 94.5 | Y | N |  | 3.14 |  |  | 230 | 365 | 480 | 4.44 | 8.88 | 13.32 | 22.2 | 33.3 | 44.4 | 92.73 | 94.37 | 94.63 | 94.45 | 93.92 | 92.81 | 94.03 | 93.73 | 94.78 | 95.01 | 95.19 | 94.85 | 94.13 | 94.85 | 92.87 | 94.02 | 94.29 | 94.72 | 94.55 | 94.02 | 94.43
Fronius USA | CL 44.4 Delta [240V] | 44.4 kW, 240 Vac Delta Utility Interactive Inverter | 44.4 | 240 | 95 | Y | N |  | 3.92 |  |  | 230 | 390 | 480 | 4.44 | 8.88 | 13.32 | 22.2 | 33.3 | 44.4 | 93.3 | 94.89 | 95.14 | 95.15 | 94.8 | 93.98 | 94.82 | 93.82 | 95 | 95.26 | 95.61 | 95.46 | 95.06 | 95.36 | 93.25 | 94.4 | 94.67 | 95.2 | 95.14 | 94.94 | 94.97
Fronius USA | CL 48.0 Wye [277V] | 48 kW, 277 Vac Wye Utility Interactive Inverter | 48 | 277 | 95.5 | Y | N |  | 4.56 |  |  | 240 | 330 | 480 | 4.8 | 9.6 | 14.4 | 24 | 36 | 48 | 94.69 | 95.2 | 95.52 | 95.74 | 95.49 | 94.89 | 95.47 | 94.8 | 95.23 | 95.54 | 96 | 95.91 | 95.52 | 95.79 | 94.4 | 94.97 | 95.17 | 95.82 | 95.92 | 95.72 | 95.69
Fronius USA | CL 55.5 Delta [208V] | 55.5 kW, 208 Vac Delta Utility Interactive Inverter | 55.5 | 208 | 94.5 | Y | N |  | 3.43 |  |  | 230 | 365 | 480 | 5.55 | 11.1 | 16.65 | 27.75 | 41.63 | 55.5 | 93.21 | 94.5 | 94.73 | 94.4 | 93.82 | 92.79 | 94.01 | 93.81 | 94.64 | 94.98 | 95.13 | 94.8 | 94.05 | 94.8 | 93.05 | 93.94 | 94.1 | 94.68 | 94.53 | 93.95 | 94.39
Fronius USA | CL 55.5 Delta [240V] | 55.5 kW, 240 Vac Delta Utility Interactive Inverter | 55.5 | 240 | 95 | Y | N |  | 4.32 |  |  | 230 | 390 | 480 | 5.55 | 11.1 | 16.65 | 27.75 | 41.63 | 55.5 | 93.87 | 94.76 | 95.08 | 95.07 | 94.67 | 93.94 | 94.74 | 94 | 94.94 | 95.11 | 95.48 | 95.38 | 94.97 | 95.27 | 93.37 | 93.96 | 94.42 | 95.12 | 95.05 | 94.89 | 94.86
Fronius USA | CL 60.0 Wye [277V] | 60 kW, 277 Vac Wye Utility Interactive Inverter | 60 | 277 | 95.5 | Y | N |  | 5.08 |  |  | 240 | 330 | 480 | 6 | 12 | 18 | 30 | 45 | 60 | 95.12 | 95.2 | 95.58 | 95.75 | 95.48 | 94.86 | 95.49 | 95.12 | 95.22 | 95.6 | 96.02 | 95.91 | 95.51 | 95.81 | 94.65 | 95.04 | 95.2 | 95.84 | 95.92 | 95.73 | 95.71
FSP Group | FSP600PV-NA-208 [208V] | 500W, 208 Vac Utility Interactive Inverter | 0.5 | 208 | 95 | N | Y |  | 0.16 |  |  | 27 | 36 | 45 | 0.05 | 0.1 | 0.15 | 0.25 | 0.38 | 0.5 | 93.3 | 94.3 | 94.8 | 94.9 | 94.1 | 93 | 94.3 | 93.4 | 94.1 | 94.8 | 95.4 | 95.1 | 94.3 | 95 | 92.4 | 92.9 | 94.5 | 95.6 | 95.5 | 95.1 | 95.1 | 2017-05 | 2017-08-15
FSP Group | FSP600PV-NA-240 [240V] | 500W, 240 Vac Utility Interactive Inverter | 0.5 | 240 | 95 | N | Y |  | 0.16 |  |  | 27 | 36 | 45 | 0.05 | 0.1 | 0.15 | 0.25 | 0.38 | 0.5 | 93.6 | 94.7 | 95.1 | 95.1 | 94.5 | 93.5 | 94.6 | 94.5 | 94.5 | 95.1 | 95.4 | 95.2 | 94.6 | 95.1 | 94.1 | 94.1 | 94.6 | 95.6 | 95.6 | 95.3 | 95.4 | 2017-05 | 2017-08-15
FSP Group | FSP600PV-NA-277 [277V] | 500W, 277 Vac Utility Interactive Inverter | 0.5 | 277 | 95 | N | Y |  | 0.22 |  |  | 36 | 40.5 | 45 | 0.05 | 0.1 | 0.15 | 0.25 | 0.38 | 0.5 | 94.5 | 93.8 | 95.1 | 95.4 | 95.4 | 95 | 95.2 | 94.1 | 93.5 | 94.9 | 95.5 | 95.6 | 95.4 | 95.3 | 93.5 | 93.4 | 94.6 | 95.6 | 95.8 | 95.7 | 95.4 | 2017-05 | 2017-08-15
GAF | RIAC 1000 [208V] | 300 W, 208 Vac Utility Interactive Inverter | 0.3 | 208 | 96 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.05 |  |  | 30 | 40 | 50 | 30 | 60 | 90 | 150 | 225 | 300 | 91.7 | 94.8 | 95.8 | 96 | 96.1 | 96 | 95.8 | 92 | 94.8 | 95.7 | 96.3 | 96.4 | 96.4 | 96 | 91.6 | 94.7 | 95.6 | 96.3 | 96.4 | 96.5 | 96
GAF | RIAC 1000 [240V] | 300 W, 240 Vac Utility Interactive Inverter | 0.3 | 240 | 96 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.05 |  |  | 30 | 40 | 50 | 30 | 60 | 90 | 150 | 225 | 300 | 91.7 | 94.8 | 95.8 | 96 | 96.1 | 96 | 95.8 | 92 | 94.8 | 95.7 | 96.3 | 96.4 | 96.4 | 96 | 91.6 | 94.7 | 95.6 | 96.3 | 96.4 | 96.5 | 96
GE Energy | GEPVe-1100-NA-120 [120V] | 1100 W, 120 Vac Utility Interactive Inverter with PV System Disconnect | 1.1 | 120 | 90.5 | Y | N |  | 3.6 |  |  | 100 | 182 | 380 | 0.11 | 0.22 | 0.33 | 0.55 | 0.83 | 1.1 | 81.8 | 89 | 90.9 | 92.1 | 92.4 | 92.5 | 91.6 | 79.9 | 88 | 90.1 | 91.7 | 92.2 | 92.3 | 91.1 | 74.8 | 84.7 | 87.8 | 90 | 90.8 | 91.1 | 89.3
GE Energy | GEPVe-2000-NA-240 [240V] | 2000 W, 240 Vac Utility Interactive Inverter with PV System Disconnect | 2 | 240 | 92 | Y | N |  | 3.6 |  |  | 100 | 199 | 380 | 0.2 | 0.4 | 0.6 | 1 | 1.5 | 2 | 87.3 | 91.7 | 92.6 | 93.5 | 93.2 | 93 | 92.9 | 85.7 | 90.8 | 92.1 | 92.9 | 92.9 | 92.6 | 92.4 | 82.4 | 88.8 | 90.5 | 91.6 | 91.8 | 91.6 | 91.1
GE Energy | GEPVb-2500-NA-240 [240V] | 2500 W, 240 Vac Utility Interactive Inverter with PV System Disconnect | 2.5 | 240 | 94 | Y | N |  | 1 | 2.5 | 1 | 100 | 266 | 480 | 0.25 | 0.5 | 0.75 | 1.25 | 1.88 | 2.5 | 88.5 | 92.7 | 94.1 | 94.8 | 94.8 | 94.5 | 94.4 | 87.7 | 92.3 | 93.7 | 94.5 | 94.6 | 94.4 | 94.1 | 86.3 | 90.9 | 92.6 | 93.8 | 94 | 93.8 | 93.3
GE Energy | GEPVe-2500-NA-240 [240V] | 2500 W, 240 Vac Utility Interactive Inverter with PV System Disconnect | 2.5 | 240 | 94.5 | Y | N |  | 3.9 |  |  | 100 | 218 | 400 | 0.25 | 0.5 | 0.75 | 1.25 | 1.88 | 2.5 | 87.1 | 93.3 | 94.9 | 95.8 | 95.8 | 95.6 | 95.2 | 85.2 | 92.4 | 93.8 | 95.2 | 95.4 | 95.1 | 94.6 | 80.4 | 90 | 91.7 | 93.7 | 94.5 | 93.8 | 93.2
GE Energy | GEPVb-2800-NA-240/208-02 [208V] | 2.7 kW, 208 Vac, 195-600 Vdc Grid Tie Inverter | 2.7 | 208 | 93.5 | Y | N |  | 1 | 2.7 | 1 | 100 | 266 | 480 | 0.27 | 0.54 | 0.81 | 1.35 | 2.025 | 2.7 | 88.7 | 93.1 | 94.1 | 94.6 | 94.5 | 94 | 94.1 | 88 | 92.8 | 93.8 | 94.4 | 94.3 | 93.8 | 93.9 | 84.6 | 90.6 | 92.3 | 93.4 | 93.4 | 92.5 | 92.7
GE Energy | GEPVb-2800-NA-240/208-02 [240V] | 2.8 kW, 240 Vac, 195-600 Vdc Grid Tie Inverter | 2.8 | 240 | 94 | Y | N |  | 1.3 | 2.8 | 1.3 | 100 | 266 | 480 | 0.28 | 0.56 | 0.84 | 1.4 | 2.1 | 2.8 | 89.3 | 93.5 | 94.4 | 95 | 94.8 | 94.4 | 94.5 | 88.6 | 93.1 | 94.2 | 94.7 | 94.6 | 94.2 | 94.3 | 85.3 | 91 | 92.7 | 93.8 | 93.7 | 92.7 | 93.1
GE Energy | GEPVe-2800-NA-208 [208V] | 2800 W, 208 Vac Utility Interactive Inverter with PV System Disconnect | 2.8 | 208 | 92 | Y | N |  | 3.85 |  |  | 100 | 230 | 380 | 0.28 | 0.56 | 0.84 | 1.4 | 2.1 | 2.8 | 81.5 | 89.7 | 91.6 | 92.9 | 93.1 | 93 | 92.2 | 80.8 | 89.3 | 91.3 | 92.7 | 92.9 | 92.8 | 92 | 78.3 | 87.9 | 90.2 | 91.9 | 92.2 | 92.1 | 91.1
GE Energy | GEPVb-3000-NA-240 [240V] | 3.0 kW Brilliance - DC Disconnect - Display | 3 | 240 | 94.5 | Y | N |  | 1 | 3 | 1 | 100 | 266 | 480 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 90.2 | 93.7 | 94.6 | 95 | 95 | 94.6 | 94.7 | 89.5 | 93.7 | 94.5 | 95 | 95 | 94.6 | 94.6 | 88.7 | 92.6 | 94 | 94.6 | 94.6 | 94.3 | 94.2
GE Energy | GEPVe-3000-NA-240 [240V] | 3000 W, 240 Vac Utility Interactive Inverter with PV System Disconnect | 3 | 240 | 93.5 | Y | N |  | 3.63 |  |  | 100 | 222.5 | 380 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 88.9 | 92.9 | 93.8 | 94.3 | 94.2 | 93.9 | 93.9 | 87.9 | 92.5 | 93.5 | 94.1 | 94 | 93.8 | 93.7 | 84.9 | 90.9 | 92.4 | 93.3 | 93.2 | 93 | 92.7
GE Energy | GEPVb-3300-NA-240/208-02 [208V] | 3.1 kW, 208 Vac, 195-600 Vdc Grid Tie Inverter | 3.1 | 208 | 95 | Y | N |  | 1.24 | 3.1 | 1.24 | 100 | 250 | 400 | 0.31 | 0.62 | 0.93 | 1.55 | 2.325 | 3.1 | 91.4 | 94.7 | 95.4 | 95.6 | 95.5 | 95.1 | 95.3 | 90.9 | 94.4 | 95.2 | 95.6 | 95.4 | 95.1 | 95.2 | 89.3 | 93.4 | 94.5 | 95.2 | 95.2 | 94.9 | 94.7
GE Energy | GEPVb-3300-NA-208 [208V] | 3.3 kW Brilliance - DC Disconnect - Display | 3.3 | 208 | 94 | Y | N |  | 1 | 3.3 | 1 | 100 | 266 | 480 | 0.33 | 0.66 | 0.99 | 1.65 | 2.48 | 3.3 | 90.1 | 93.3 | 94.2 | 94.6 | 94.3 | 93.6 | 94.1 | 89.5 | 93.2 | 94.1 | 94.6 | 94.3 | 93.6 | 94.1 | 87.2 | 91.7 | 93.2 | 93.9 | 93.7 | 93.1 | 93.3
GE Energy | GEPVb-3300-NA-240 [240V] | 3.3 kW Brilliance - DC Disconnect - Display | 3.3 | 240 | 94.5 | Y | N |  | 1 | 3.3 | 1 | 100 | 266 | 480 | 0.33 | 0.66 | 0.99 | 1.65 | 2.48 | 3.3 | 90.6 | 93.8 | 94.9 | 95.3 | 95.1 | 94.6 | 94.9 | 90.1 | 93.7 | 94.6 | 95.1 | 95 | 94.4 | 94.7 | 87.2 | 91.9 | 93.4 | 94.4 | 94.3 | 93.8 | 93.8
GE Energy | GEPVb-3300-NA-240/208-02 [240V] | 3.3 kW, 240 Vac, 195-600 Vdc Grid Tie Inverter | 3.3 | 240 | 95.5 | Y | N |  | 1.52 | 3.3 | 1.52 | 100 | 250 | 400 | 0.33 | 0.66 | 0.99 | 1.65 | 2.475 | 3.3 | 91.9 | 95 | 95.7 | 95.9 | 95.9 | 95.5 | 95.6 | 91.4 | 94.7 | 95.5 | 95.9 | 95.7 | 95.4 | 95.5 | 89.8 | 93.6 | 94.8 | 95.4 | 95.3 | 95.2 | 95
GE Energy | GEPVe-3500-NA-240 [240V] | 3500 W, 240 Vac Utility Interactive Inverter with PV System Disconnect | 3.5 | 240 | 95.5 | Y | N |  | 3.86 |  |  | 100 | 263 | 400 | 0.35 | 0.7 | 1.05 | 1.75 | 2.63 | 3.5 | 87.2 | 93.1 | 95.4 | 96.5 | 96.7 | 96.6 | 95.9 | 85.7 | 92.2 | 94.9 | 96.2 | 96.4 | 96.3 | 95.5 | 82.1 | 90.2 | 93.6 | 95.4 | 95.7 | 95.6 | 94.5
GE Energy | GEPVb-3800-NA-240 [240V] | 3.8 kW Brilliance - DC Disconnect - Display | 3.8 | 240 | 95 | Y | N |  | 1 | 3.8 | 1 | 100 | 266 | 480 | 0.38 | 0.76 | 1.14 | 1.9 | 2.85 | 3.8 | 93 | 95.2 | 95.7 | 95.7 | 95.4 | 94.5 | 95.3 | 92.3 | 95 | 95.5 | 95.6 | 95.3 | 94.6 | 95.2 | 91.2 | 94.2 | 94.8 | 95.1 | 95 | 94.3 | 94.7
GE Energy | GEPVb-4000-NA-240/208-02 [208V] | 3.8 kW, 208 Vac, 195-600 Vdc Grid Tie Inverter | 3.8 | 208 | 95 | Y | N |  | 0.99 | 3.8 | 0.99 | 100 | 300 | 480 | 0.38 | 0.76 | 1.14 | 1.9 | 2.85 | 3.8 | 91.7 | 94.8 | 95.5 | 95.7 | 95.4 | 95.1 | 95.3 | 91 | 94.6 | 95.3 | 95.6 | 95.4 | 94.9 | 95.2 | 90.2 | 93.6 | 94.7 | 95.1 | 95.1 | 94.7 | 94.7
GE Energy | GEPVb-4000-NA-240/208-02 [240V] | 4.0 kW, 240 Vac, 195-600 Vdc Grid Tie Inverter | 4 | 240 | 95.5 | Y | N |  | 1.1 | 4 | 1.1 | 100 | 300 | 480 | 0.4 | 0.8 | 1.2 | 2 | 3 | 4 | 92.2 | 95.1 | 95.8 | 96 | 95.8 | 95.5 | 95.7 | 91.6 | 94.9 | 95.7 | 95.9 | 95.8 | 95.3 | 95.5 | 90.7 | 94.2 | 95 | 95.5 | 95.4 | 95.1 | 95.1
GE Energy | GEPVb-5000-NA-240/208-02 [208V] | 5.0 kW, 208 Vac, 195-600 Vdc Grid Tie Inverter | 4.5 | 208 | 95 | Y | N |  | 1 | 4.5 | 1 | 100 | 300 | 480 | 0.45 | 0.9 | 1.35 | 2.25 | 3.375 | 4.5 | 92.1 | 94.9 | 95.5 | 95.5 | 94.9 | 94.3 | 95 | 91.8 | 94.7 | 95.3 | 95.4 | 94.9 | 94.3 | 94.9 | 90.5 | 93.9 | 94.6 | 95 | 94.7 | 94.2 | 94.5
GE Energy | GEPVe-4600-NA-208 [208V] | 4600 W, 208 Vac Utility Interactive Inverter with PV System Disconnect | 4.6 | 208 | 95.5 | Y | N |  | 4 | 4.6 | 4 | 100 | 254 | 400 | 0.46 | 0.92 | 1.38 | 2.3 | 3.45 | 4.6 | 90.3 | 94.8 | 95.9 | 96.5 | 96.5 | 96.2 | 96.1 | 89.2 | 94.3 | 95.6 | 96.3 | 96.4 | 96.1 | 95.9 | 86.5 | 92.9 | 94.7 | 95.6 | 95.7 | 95.4 | 95
GE Energy | GEPVe-4800-NA-240 [240V] | 4800 W, 240 Vac Utility Interactive Inverter with PV System Disconnect | 4.8 | 240 | 96 | Y | N |  | 4.1 |  |  | 100 | 263 | 400 | 0.48 | 0.96 | 1.44 | 2.4 | 3.6 | 4.8 | 86.8 | 93.5 | 95.5 | 97 | 97.2 | 97.1 | 96.4 | 85.5 | 92.9 | 95 | 96.7 | 96.9 | 96.8 | 96 | 84.5 | 91.5 | 93.9 | 95.9 | 96.2 | 96.1 | 95.1
GE Energy | GEPVb-5000-NA-240/208-02 [240V] | 5.0 kW, 240 Vac, 195-600 Vdc Grid Tie Inverter | 5 | 240 | 95.5 | Y | N |  | 1 | 5 | 1 | 100 | 300 | 480 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 93.2 | 95.5 | 95.9 | 95.9 | 95.5 | 94.8 | 95.5 | 92.7 | 95.3 | 95.8 | 95.8 | 95.4 | 94.8 | 95.4 | 91.5 | 94.6 | 95.3 | 95.4 | 95.1 | 94.5 | 95
GE Energy | GEPVb-5000-NA-240-01 [240V] | 5.0 kW, 240 Vac, 195-600 Vdc Grid Tie Inverter | 5 | 240 | 95.5 | Y | N |  | 1 | 5 | 1 | 100 | 300 | 480 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 93.6 | 95.7 | 96 | 96.1 | 95.5 | 94.8 | 95.6 | 93.2 | 95.6 | 95.9 | 95.9 | 95.5 | 94.8 | 95.5 | 92.3 | 94.8 | 95.5 | 95.6 | 95.2 | 94.6 | 95.2
GE Energy | GEPVe-5200-NA-240 [240V] | 5200 W, 240 Vac Utility Interactive Inverter with PV System Disconnect | 5.2 | 240 | 96 | Y | N |  | 4 | 5.2 | 4 | 100 | 280 | 400 | 0.52 | 1.04 | 1.56 | 2.6 | 3.9 | 5.2 | 89.4 | 94.8 | 96 | 96.8 | 97 | 96.8 | 96.4 | 88.6 | 94.4 | 95.7 | 96.7 | 96.8 | 96.6 | 96.2 | 87.7 | 93.1 | 94.8 | 96.1 | 96.3 | 96.1 | 95.5
Gefran | APV 1700-2M-TL-US [208V] | 1.5 kW, 208 Vac Utility Interactive Inverter | 1.5 | 208 | 96 | Y | N |  | 0.07 |  |  | 100 | 330 | 360 | 0.15 | 0.3 | 0.45 | 0.75 | 1.125 | 1.5 | 91.07 | 94.89 | 95.98 | 96.37 | 96.19 | 96.01 | 95.92 | 91.74 | 95.48 | 96.48 | 96.85 | 96.7 | 96.5 | 96.43 | 91.45 | 95.19 | 96.25 | 96.74 | 96.65 | 96.46 | 96.33
Gefran | APV 1700-2M-TL-US [240V] | 1.65 kW, 240 Vac Utility Interactive Inverter | 1.65 | 240 | 96 | Y | N |  | 0.11 |  |  | 100 | 330 | 360 | 0.165 | 0.33 | 0.495 | 0.825 | 1.238 | 1.65 | 89.51 | 94.23 | 95.46 | 96.29 | 96.25 | 96.03 | 95.78 | 90.24 | 94.71 | 95.95 | 96.58 | 96.64 | 96.51 | 96.19 | 91.3 | 95.36 | 96.46 | 97.02 | 96.99 | 96.82 | 96.62
Gefran | APV 1700-2M-TL-US [277V] | 1.65 kW, 277 Vac Utility Interactive Inverter | 1.65 | 277 | 96 | Y | N |  | 0.13 |  |  | 100 | 330 | 360 | 0.165 | 0.33 | 0.495 | 0.825 | 1.238 | 1.65 | 89.17 | 93.51 | 95.04 | 96.07 | 96.22 | 96.15 | 95.63 | 89.3 | 94.02 | 95.58 | 96.43 | 96.61 | 96.65 | 96.03 | 89.26 | 94.34 | 95.7 | 96.59 | 96.77 | 96.78 | 96.18
Gefran | APV 2300-2M-TL-US [208V] | 1.8 kW, 208 Vac Utility Interactive Inverter | 1.8 | 208 | 96.5 | Y | N |  | 0.09 |  |  | 100 | 360 | 400 | 0.18 | 0.36 | 0.54 | 0.9 | 1.35 | 1.8 | 92.27 | 95.4 | 95.99 | 96.41 | 96.32 | 96.02 | 96.08 | 92.84 | 95.99 | 96.57 | 96.79 | 96.62 | 96.44 | 96.46 | 92.68 | 95.67 | 96.26 | 96.6 | 96.48 | 96.33 | 96.28
Gefran | APV 2300-2M-TL-US [240V] | 2 kW, 240 Vac Utility Interactive Inverter | 2 | 240 | 96.5 | Y | N |  | 0.1 |  |  | 100 | 360 | 400 | 0.2 | 0.4 | 0.6 | 1 | 1.5 | 2 | 91.42 | 94.6 | 95.68 | 96.3 | 96.38 | 96.07 | 95.98 | 92.9 | 96.12 | 96.85 | 97.12 | 97.11 | 96.87 | 96.85 | 92.27 | 95.76 | 96.57 | 96.93 | 96.97 | 96.82 | 96.66
Gefran | APV 2300-2M-TL-US [277V] | 2 kW, 277 Vac Utility Interactive Inverter | 2 | 277 | 96.5 | Y | N |  | 0.14 |  |  | 100 | 360 | 400 | 0.2 | 0.4 | 0.6 | 1 | 1.5 | 2 | 89.3 | 93.72 | 95.09 | 96.02 | 96.31 | 96.13 | 95.68 | 91.06 | 94.84 | 95.88 | 96.54 | 96.85 | 96.78 | 96.33 | 92.92 | 96.05 | 96.89 | 97.32 | 97.43 | 97.31 | 97.09
Gefran | APV 3100-2M-TL-US [208V] | 2.5 kW, 208 Vac Utility Interactive Inverter | 2.5 | 208 | 96.5 | Y | N |  | 0.1 |  |  | 100 | 360 | 400 | 0.25 | 0.5 | 0.75 | 1.25 | 1.875 | 2.5 | 92.33 | 95.42 | 96.2 | 96.47 | 96.18 | 95.79 | 96.03 | 93.86 | 96.24 | 96.83 | 97.02 | 96.76 | 96.38 | 96.66 | 92.7 | 95.78 | 96.5 | 96.82 | 96.64 | 96.3 | 96.44
Gefran | APV 3100-2M-TL-US [240V] | 2.8 kW, 240 Vac Utility Interactive Inverter | 2.8 | 240 | 96.5 | Y | N |  | 0.15 |  |  | 100 | 360 | 400 | 0.28 | 0.56 | 0.84 | 1.4 | 2.1 | 2.8 | 90.95 | 94.37 | 95.55 | 96.42 | 96.44 | 96.11 | 95.99 | 93.99 | 96.56 | 97.1 | 97.54 | 97.41 | 97.03 | 97.2 | 93.25 | 96.15 | 96.83 | 97.38 | 97.27 | 96.98 | 97.01 |  | 2018-03-15
Gefran | APV 3100-2M-TL-US [277V] | 2.8 kW, 277 Vac Utility Interactive Inverter | 2.8 | 277 | 96.5 | Y | N |  | 0.19 |  |  | 100 | 360 | 400 | 0.28 | 0.56 | 0.84 | 1.4 | 2.1 | 2.8 | 89.39 | 93.38 | 94.83 | 95.93 | 96.17 | 96.03 | 95.54 | 91.61 | 95.23 | 96.26 | 96.9 | 96.98 | 96.79 | 96.56 | 94.07 | 96.64 | 97.32 | 97.65 | 97.64 | 97.41 | 97.4
Gefran | APV 3800-2M-TL-US [208V] | 3.6 kW, 208 Vac Utility Interactive Inverter | 3.6 | 208 | 97 | Y | N |  | 0.23 |  |  | 100 | 375 | 450 | 0.36 | 0.72 | 1.08 | 1.8 | 2.7 | 3.6 | 91.95 | 94.55 | 95.5 | 96.38 | 96.5 | 96.35 | 96.07 | 94.47 | 96.66 | 97.32 | 97.56 | 97.44 | 97.18 | 97.28 | 93.04 | 96.01 | 96.85 | 97.31 | 97.29 | 97.09 | 97
Gefran | APV 3800-2M-TL-US [240V] | 3.6 kW, 240 Vac Utility Interactive Inverter | 3.6 | 240 | 97 | Y | N |  | 0.31 |  |  | 100 | 375 | 450 | 0.36 | 0.72 | 1.08 | 1.8 | 2.7 | 3.6 | 92.36 | 94.62 | 95.52 | 96.5 | 96.72 | 96.66 | 96.25 | 95.3 | 97.14 | 97.54 | 97.79 | 97.75 | 97.54 | 97.59 | 94.21 | 96.53 | 97.06 | 97.5 | 97.57 | 97.44 | 97.3
Gefran | APV 3800-2M-TL-US [277V] | 3.6 kW, 277 Vac Utility Interactive Inverter | 3.6 | 277 | 97 | Y | N |  | 0.4 |  |  | 100 | 375 | 450 | 0.36 | 0.72 | 1.08 | 1.8 | 2.7 | 3.6 | 91.24 | 93.86 | 94.75 | 96.11 | 96.57 | 96.63 | 95.91 | 93.37 | 96.01 | 96.64 | 97.42 | 97.53 | 97.48 | 97.15 | 94.54 | 96.85 | 97.37 | 97.89 | 97.97 | 97.87 | 97.68
Gefran | APV 4400-2M-TL-US [208V] | 4.2 kW, 208 Vac Utility Interactive Inverter | 4.2 | 208 | 97 | Y | N |  | 0.25 |  |  | 100 | 375 | 450 | 0.42 | 0.84 | 1.26 | 2.1 | 3.15 | 4.2 | 91.58 | 94.43 | 95.52 | 96.63 | 96.81 | 96.73 | 96.29 | 94.13 | 96.46 | 97.09 | 97.28 | 97.07 | 96.73 | 96.95 | 93.57 | 96.16 | 96.78 | 97.22 | 97.46 | 97.15 | 97.09
Gefran | APV 4400-2M-TL-US [240V] | 4.2 kW, 240 Vac Utility Interactive Inverter | 4.2 | 240 | 97 | Y | N |  | 0.33 |  |  | 100 | 375 | 450 | 0.42 | 0.84 | 1.26 | 2.1 | 3.15 | 4.2 | 92.36 | 94.62 | 95.52 | 96.5 | 96.72 | 96.66 | 96.25 | 95.3 | 97.14 | 97.54 | 97.79 | 97.75 | 97.54 | 97.59 | 94.21 | 96.53 | 97.06 | 97.5 | 97.57 | 97.44 | 97.3
Gefran | APV 4400-2M-TL-US [277V] | 4.2 kW, 277 Vac Utility Interactive Inverter | 4.2 | 277 | 97 | Y | N |  | 0.4 |  |  | 100 | 375 | 450 | 0.42 | 0.84 | 1.26 | 2.1 | 3.15 | 4.2 | 91.38 | 94.39 | 96.04 | 96.56 | 96.84 | 96.56 | 96.33 | 92.15 | 95.2 | 96.3 | 97.27 | 97.57 | 97.13 | 97 | 93.64 | 96.31 | 97.2 | 97.62 | 97.64 | 97.61 | 97.36
Gefran | APV 5200-2M-TL-US [208V] | 4.6 kW, 208 Vac Utility Interactive Inverter | 4.6 | 208 | 97 | Y | N |  | 0.26 |  |  | 100 | 375 | 450 | 0.46 | 0.92 | 1.38 | 2.3 | 3.45 | 4.6 | 94.65 | 96.46 | 96.83 | 96.95 | 96.5 | 96.03 | 96.54 | 95.44 | 97.01 | 97.33 | 97.37 | 97 | 96.5 | 97.03 | 94.29 | 96.39 | 96.89 | 97.14 | 96.96 | 96.47 | 96.83
Gefran | APV 5200-2M-TL-US [240V] | 4.6 kW, 240 Vac Utility Interactive Inverter | 4.6 | 240 | 97 | Y | N |  | 0.36 |  |  | 100 | 375 | 450 | 0.46 | 0.92 | 1.38 | 2.3 | 3.45 | 4.6 | 92.79 | 95.19 | 96.01 | 96.67 | 96.65 | 96.4 | 96.34 | 95.85 | 97.33 | 97.67 | 97.76 | 97.48 | 97.08 | 97.47 | 96.66 | 96.66 | 97.2 | 97.53 | 97.37 | 97.08 | 97.3
Gefran | APV 5200-2M-TL-US [277V] | 4.6 kW, 277 Vac Utility Interactive Inverter | 4.6 | 277 | 97 | Y | N |  | 0.43 |  |  | 100 | 375 | 450 | 0.46 | 0.92 | 1.38 | 2.3 | 3.45 | 4.6 | 92.24 | 94.93 | 95.62 | 96.64 | 96.82 | 96.76 | 96.36 | 94.63 | 96.69 | 97.2 | 97.63 | 97.57 | 97.41 | 97.37 | 95.39 | 97.11 | 97.55 | 97.86 | 97.82 | 97.65 | 97.66
General Electric | PVIA2000NA1240 [240V] | 2110 W, 240 Vac Utility Interactive Inverter | 2.11 | 240 | 94.5 | Y | N |  | 0.25 |  |  | 100 | 375 | 400 | 0.21 | 0.42 | 0.63 | 1.06 | 1.58 | 2.11 | 85.3 | 91.6 | 92.9 | 94.3 | 94.6 | 94.5 | 93.8 | 82.1 | 91.9 | 94.2 | 95.6 | 96.1 | 96.4 | 95 | 82.2 | 91.5 | 93.8 | 95.6 | 96.1 | 96.3 | 95
General Electric | PVIA3000NA1240 [240V] | 3180 W, 240 Vac Utility Interactive Inverter | 3.18 | 240 | 95 | Y | N |  | 0.25 |  |  | 100 | 375 | 400 | 0.32 | 0.64 | 0.95 | 1.59 | 2.39 | 3.18 | 88.8 | 92.9 | 94.1 | 94.6 | 94.3 | 94 | 94 | 88.8 | 94.4 | 95.3 | 96.2 | 96.3 | 95.9 | 95.7 | 89.5 | 93.7 | 95.3 | 96.2 | 96.3 | 96.1 | 95.7
General Electric | PVIA4000NA1240 [240V] | 4160 W, 240 Vac Utility Interactive Inverter | 4.16 | 240 | 95.5 | Y | N |  | 0.2 |  |  | 100 | 380 | 400 | 0.42 | 0.83 | 1.25 | 2.08 | 3.12 | 4.16 | 90.6 | 93.8 | 94.5 | 94.8 | 94.6 | 94.2 | 94.4 | 91.4 | 95 | 95.7 | 96.1 | 96.2 | 95.9 | 95.9 | 90.7 | 94.7 | 95.5 | 96.1 | 96.1 | 95.9 | 95.7
General Electric | PVIA5000NA1240 [240V] | 5000 W, 240 Vac Utility Interactive Inverter | 5.24 | 240 | 95.5 | Y | N |  | 0.2 |  |  | 100 | 380 | 400 | 0.52 | 1.05 | 1.57 | 2.62 | 3.93 | 5.24 | 91.8 | 94.1 | 94.6 | 94.7 | 94.3 | 93.5 | 94.3 | 92.5 | 95.1 | 96.1 | 96.2 | 95.9 | 95.6 | 95.8 | 92.3 | 95.3 | 95.8 | 96.1 | 95.9 | 95.5 | 95.8
Geoprotek Technology | GS-1000 [208V] | 1.5 kW, 208 Vac Utility Interactive Inverter | 1.55 | 208 | 94.5 | Y | N |  | 0.21 |  |  | 100 | 325 | 360 | 0.16 | 0.31 | 0.47 | 0.78 | 1.16 | 1.55 | 84.5 | 90.5 | 92.5 | 94.3 | 94.9 | 95 | 93.9 | 85 | 91 | 93.2 | 94.8 | 95.4 | 95.5 | 94.4 | 85.3 | 91.2 | 93.5 | 95 | 95.6 | 95.8 | 94.6
Geoprotek Technology | GS-1000 [240V] | 1.5 kW, 240 Vac Utility Interactive Inverter | 1.55 | 240 | 94.5 | Y | N |  | 0.32 |  |  | 100 | 325 | 360 | 0.16 | 0.31 | 0.47 | 0.78 | 1.16 | 1.55 | 84.6 | 90.5 | 92.6 | 94.4 | 95.1 | 95.3 | 94 | 84.9 | 91 | 93 | 94.8 | 95.5 | 95.7 | 94.4 | 85.2 | 91.4 | 93.4 | 95.1 | 95.7 | 95.9 | 94.7
Geoprotek Technology | GS-1500 [208V] | 1.5 kW, 208 Vac Utility Interactive Inverter | 1.55 | 208 | 94.5 | Y | N |  | 0.21 |  |  | 100 | 325 | 360 | 0.16 | 0.31 | 0.47 | 0.78 | 1.16 | 1.55 | 84.5 | 90.5 | 92.5 | 94.3 | 94.9 | 95 | 93.9 | 85 | 91 | 93.2 | 94.8 | 95.4 | 95.5 | 94.4 | 85.3 | 91.2 | 93.5 | 95 | 95.6 | 95.8 | 94.6
Geoprotek Technology | GS-1500 [240V] | 1.5 kW, 240 Vac Utility Interactive Inverter | 1.55 | 240 | 94.5 | Y | N |  | 0.32 |  |  | 100 | 325 | 360 | 0.16 | 0.31 | 0.47 | 0.78 | 1.16 | 1.55 | 84.6 | 90.5 | 92.6 | 94.4 | 95.1 | 95.3 | 94 | 84.9 | 91 | 93 | 94.8 | 95.5 | 95.7 | 94.4 | 85.2 | 91.4 | 93.4 | 95.1 | 95.7 | 95.9 | 94.7
Geoprotek Technology | GS-2000 [208V] | 2 kW, 208 Vac Utility Interactive Inverter | 2.06 | 208 | 95.5 | Y | N |  | 0.29 |  |  | 100 | 325 | 360 | 0.21 | 0.41 | 0.62 | 1.03 | 1.55 | 2.06 | 88.3 | 93.1 | 94.4 | 95.3 | 95.4 | 95.4 | 94.9 | 89.6 | 93.7 | 94.9 | 95.7 | 95.8 | 95.8 | 95.3 | 89.7 | 94 | 95.1 | 96.1 | 96.4 | 96.1 | 95.8
Geoprotek Technology | GS-2000 [240V] | 2 kW, 240 Vac Utility Interactive Inverter | 2.06 | 240 | 95 | Y | N |  | 0.36 |  |  | 100 | 325 | 360 | 0.21 | 0.41 | 0.62 | 1.03 | 1.55 | 2.06 | 86.9 | 92.1 | 93.8 | 94.9 | 95.3 | 95.4 | 94.6 | 87.8 | 92.9 | 94.3 | 95.6 | 95.8 | 95.7 | 95.1 | 88.1 | 93.1 | 94.4 | 95.7 | 96 | 95.9 | 95.3
Geoprotek Technology | GS-3000 [208V] | 3 kW, 208 Vac Utility Interactive Inverter | 3 | 208 | 95.5 | Y | N |  | 0.18 |  |  | 100 | 325 | 360 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 91.6 | 94.4 | 95.2 | 95.5 | 95.3 | 94.6 | 95.1 | 92.1 | 94.9 | 95.6 | 95.9 | 95.8 | 95.4 | 95.6 | 92.2 | 95.2 | 95.8 | 96.2 | 95.9 | 95.8 | 95.8
Geoprotek Technology | GS-3000 [240V] | 3 kW, 240 Vac Utility Interactive Inverter | 3.01 | 240 | 95.5 | Y | N |  | 0.25 |  |  | 100 | 325 | 360 | 0.3 | 0.6 | 0.9 | 1.51 | 2.26 | 3.01 | 90 | 93.9 | 94.9 | 95.4 | 95.3 | 94.8 | 95 | 90.6 | 94.3 | 95.3 | 95.8 | 95.9 | 95.6 | 95.5 | 91 | 94.6 | 95.4 | 96 | 96 | 95.8 | 95.7
Green Power Technologies | PV500U + MVT | 500 kW, 3-phase, Utility Interactive Inverter with Medium Voltage NEMA TP1 transformer | 500 |  | 96 | Y | N |  | 140.4 |  |  | 325 | 395 | 600 | 50 | 100 | 150 | 250 | 375 | 500 | 94.5 | 96.4 | 96.8 | 96.6 | 96.3 | 95.7 | 96.3 | 93.7 | 95.9 | 96.5 | 96.5 | 96.1 | 95.5 | 96.1 | 91.8 | 94.9 | 95.7 | 95.9 | 95.6 | 95.1 | 95.5
Green Power Technologies | PV500WD | Photovoltaic Inverter | 600 |  | 96 | N | N |  | 154.4 |  |  | 395 | 503 | 825 | 60 | 12 | 180 | 300 | 450 | 600 | 95.5 | 96.9 | 97.1 | 97 | 96.5 | 96 | 96.6 | 95.1 | 96.6 | 96.9 | 96.6 | 96.2 | 95.6 | 96.3 | 94 | 95.7 | 96.2 | 96.1 | 95.6 | 95.1 | 95.7
Green Power Technologies | PV630WD | Photovoltaic Inverter | 750 |  | 96.5 | N | N |  | 155.7 |  |  | 495 | 578 | 825 | 75 | 150 | 225 | 375 | 563 | 750 | 95.5 | 97 | 97.3 | 97.1 | 96.7 | 96.2 | 96.8 | 95.1 | 96.8 | 97 | 97 | 96.5 | 95.9 | 96.6 | 94.5 | 96.2 | 96.7 | 96.7 | 96.2 | 95.6 | 96.2
Green Power Technologies | PV750WD | Photovoltaic Inverter | 890 |  | 97 | N | N |  | 154.1 |  |  | 585 | 646 | 825 | 89 | 178 | 267 | 445 | 667.5 | 890 | 95.8 | 97.2 | 97.4 | 97.3 | 96.8 | 96.3 | 96.9 | 95.3 | 96.9 | 97.2 | 97.1 | 96.7 | 96.2 | 96.8 | 95.1 | 96.8 | 97 | 97 | 96.5 | 95.9 | 96.6
Green Power Technologies | 940WD3-LV400 [400V] | 933 kW, 400 Vac Utility Interactive Inverter | 935.55 | 400 | 97 | N | N | Efficiency data inclusive of transformer effect based on 1500 kVA Liquid-Immeresed Distribution Transformers Table in DOE2016. | 274.29 |  |  | 593 | 682 | 880 | 93.56 | 187.11 | 280.67 | 467.78 | 701.66 | 935.55 | 96.07 | 97.25 | 97.52 | 97.52 | 97.2 | 96.72 | 97.24 | 95.86 | 97.18 | 97.48 | 97.48 | 97.11 | 96.55 | 97.16 | 95.21 | 96.8 | 97.2 | 97.27 | 96.94 | 96.4 | 96.94 | 2017-04-01 | 2018-06-01
Green Power Technologies | PV900WD | Photovoltaic Inverter | 1080 |  | 97 | N | N |  | 155.7 |  |  | 705 | 736 | 825 | 108 | 216 | 324 | 540 | 810 | 1080 | 95.7 | 97.2 | 97.5 | 97.4 | 97 | 96.5 | 97.1 | 95.6 | 97.1 | 97.4 | 97.4 | 97 | 96.4 | 97 | 95.4 | 97 | 97.3 | 97.3 | 96.9 | 96.3 | 96.9
Green Power Technologies | 1170WD3-LV500 [500V] | 1135 kW, 500 Vac Utility Interactive Inverter | 1135.968 | 500 | 97.5 | N | N | Efficiency data inclusive of transformer effect based on 2000 kVA Liquid-Immeresed Distribution Transformers Table in DOE2016. | 269.45 |  |  | 741 | 793 | 880 | 113.6 | 227.19 | 340.79 | 567.98 | 851.98 | 1136 | 96.3243 | 97.4929 | 97.7506 | 97.7916 | 97.5104 | 97.093 | 97.5291 | 96.1979 | 97.4382 | 97.7225 | 97.7484 | 97.4418 | 96.9627 | 97.466 | 95.9161 | 97.2976 | 97.6014 | 97.6776 | 97.3821 | 96.9105 | 97.384 | 2017-04-01 | 2018-06-01
Green Power Technologies | 1140WD3-HV560 [560V] | 1130 kW, 560 Vac Utility Interactive Inverter | 1154.944 | 560 | 97.5 | N | N | Efficiency data inclusive of transformer effect based on 2000 kVA Liquid-Immeresed Distribution Transformers Table in DOE2016. | 279.91 |  |  | 801 | 913 | 1200 | 115.49 | 230.99 | 346.48 | 577.47 | 866.21 | 1154.9 | 96.2 | 97.56 | 97.89 | 98.03 | 97.84 | 97.49 | 97.79 | 95.7 | 97.27 | 97.65 | 97.81 | 97.6 | 97.2 | 97.54 | 94.73 | 96.69 | 97.22 | 97.51 | 97.33 | 96.97 | 97.2 | 2017-04-01 | 2018-06-01
Green Power Technologies | 1260WD3-HV620 [620V] | 1205 kW, 620 Vac Utility Interactive Inverter | 1205.298 | 620 | 97.5 | N | N | Efficiency data inclusive of transformer effect based on 2000 kVA Liquid-Immeresed Distribution Transformers Table in DOE2016. | 263.99 |  |  | 887 | 978 | 1200 | 120.53 | 241.06 | 361.59 | 602.65 | 903.97 | 1205.3 | 96.11 | 97.53 | 97.85 | 98 | 97.87 | 97.51 | 97.79 | 95.73 | 97.35 | 97.71 | 97.87 | 97.71 | 97.34 | 97.63 | 94.98 | 96.91 | 97.38 | 97.65 | 97.51 | 97.16 | 97.37 | 2017-04-01 | 2018-06-01
Green Power Technologies | 1400WD3-HV690 [690V] | 1350 kW, 690 Vac Utility Interactive Inverter | 1350.426 | 690 | 98 | N | N | Efficiency data inclusive of transformer effect based on 2500 kVA Liquid-Immeresed Distribution Transformers Table in DOE2016. | 275.89 |  |  | 987 | 1053 | 1200 | 135.04 | 270.09 | 405.13 | 675.21 | 1012.82 | 1350.4 | 96.17 | 97.67 | 98 | 98.16 | 98.05 | 97.71 | 97.95 | 95.8 | 97.46 | 97.81 | 97.97 | 97.81 | 97.48 | 97.73 | 95.2 | 97.18 | 97.6 | 97.83 | 97.7 | 97.37 | 97.57 | 2017-04-01 | 2018-06-01
GreenVolts | GV-SCP001 [480V] | 16 kW, 480 Vac Utility Interactive Inverter | 16 | 480 | 96 | Y | N |  | 85 |  |  | 760 | 810 | 960 | 1.6 | 3.2 | 4.8 | 8 | 12 | 16 | 93 | 95.7 | 96.4 | 96.8 | 96.7 | 96.5 | 96.5 | 92.8 | 95.4 | 96.2 | 96.5 | 96.6 | 96.4 | 96.3 | 92.2 | 94.9 | 95.9 | 96.3 | 96.3 | 96.1 | 96
GridPoint | Connect C36 | 3600 W, 48 Vdc Utility Interactive with battery backup | 3.037 |  | 91 | N | N |  | 0 |  |  | 40 | 51.2 | 60 | 0.3037 | 0.6075 | 0.9112 | 1.519 | 2.278 | 3.037 | 88 | 92.2 | 93.2 | 94 | 93 | 91.3 | 92.9 | 82.1 | 88.5 | 90.7 | 91.8 | 91.6 | 89.7 | 90.9 | 80.4 | 86.1 | 87.9 | 90.3 | 90.5 | 88.4 | 89.4
Hansol Technics | HSPV-A250 | 250 W Utility Interactive Inverter | 0.25 |  | 93 | N | N |  | 0.2 |  |  | 27 | 30 | 36 | 0.02 | 0.05 | 0.07 | 0.12 | 0.19 | 0.25 | 85.9 | 90.6 | 91.4 | 93 | 93.4 | 93.2 | 92.6 | 86.1 | 90.6 | 91.5 | 93.2 | 93.7 | 93.3 | 92.8 | 85.6 | 90.5 | 91.6 | 93.1 | 93.9 | 93.8 | 93
Heart Transverter | HT2000 | Utility Interactive Inverter | 1.97 |  | 89 | Y | N |  | 15.7 |  |  | 20 | 30 | 40 | 0.2 | 0.39 | 0.59 | 0.99 | 1.48 | 1.97 | 88.6 | 89.1 | 90.6 | 89.1 | 87.4 | 85.6 | 88.2 | 85.4 | 89.6 | 91.5 | 89.8 | 88.6 | 86.7 | 89 | 87.6 | 89.7 | 91 | 90.4 | 89.2 | 87.7 | 89.5
Helios USA | 6TA [120V] | 212W, 120Vac Inverter | 0.21 | 120 | 94.5 | N | N | This component is specific to ACPV modules and is not available as an individual unit. | 0 |  |  | 36 | 50 | 55 | 0.02 | 0.04 | 0.06 | 0.11 | 0.16 | 0.21 | 87.9 | 94.4 | 95.8 | 95.7 | 94.8 | 93.5 | 94.8 | 85.2 | 92.5 | 94.6 | 95.3 | 95.1 | 94.2 | 94.5 | 83.6 | 92 | 94.3 | 94.9 | 94.9 | 93.9 | 94.2
HiQ Solar | Mini3500-US | 3.5 kW Utility Interactive Inverter | 3.5 |  | 94.5 | N | N |  | 3.74 |  |  | 100 | 160 | 170 | 0.35 | 0.7 | 1.05 | 1.75 | 2.63 | 3.5 | 87.5 | 92.4 | 94 | 95.2 | 95.4 | 94.9 | 94.7 | 87.2 | 92.6 | 94.1 | 95.3 | 95.4 | 95 | 94.7 | 87.4 | 92.5 | 94.2 | 95.3 | 95.5 | 95.1 | 94.8
HiQ Solar | TS208-5k75 [208V] | 5.75 kW, 208 Vac, 3-phase Utility Interactive Inverter | 5.75 | 208 | 97 | Y | N |  | 3.5 |  |  | 325 | 380 | 525 | 0.58 | 1.15 | 1.73 | 2.88 | 4.31 | 5.75 | 95.7 | 97.3 | 97.7 | 97.8 | 97.5 | 97.1 | 97.5 | 94.8 | 97.1 | 97.5 | 97.7 | 97.5 | 97.1 | 97.4 | 92.4 | 95.8 | 96.7 | 97.1 | 97.2 | 97 | 96.9
HiQ Solar | TS480-8k [480V] | 8 kW, 480 Vac, Utility Interactive Inverter, 3-phase dual MPPT | 8 | 480 | 98 | Y | N |  | 4 |  |  | 100 | 740 | 800 | 0.8 | 1.6 | 2.4 | 4 | 6 | 8 | 93.6 | 96.6 | 97.4 | 97.7 | 97.9 | 97.9 | 97.6 | 95.3 | 97.5 | 98 | 98.4 | 98.5 | 98.5 | 98.3 | 94.6 | 97.2 | 97.9 | 98.4 | 98.6 | 98.6 | 98.2
HiQ Solar | TSXL480-10k [480V] | 9.975 kW, 480 Vac Utility Interactive Inverter | 9.975 | 480 | 97.5 | N | N | Multiple Listing of ONE SUN, MEXICO S.A. DE C.V., 1S480-10k and OutBack Power Technologies, Inc., PHXL480-10k. |  |  |  | 450 | 750 | 850 | 0.9975 | 1.995 | 2.9925 | 4.9875 | 7.4812 | 9.975 | 94.1157 | 96.7771 | 97.3429 | 97.7271 | 97.6957 | 97.5171 | 97.4619 | 94.11 | 96.8457 | 97.6443 | 98.1614 | 98.22 | 98.14 | 97.9015 | 93.1871 | 96.46 | 97.4557 | 98.1029 | 98.2386 | 98.2 | 97.8232 | 2019-02-01 | 2019-02-15
HiSEL Power | HiSEL-K 1500 [208V] | 1.5 kW, 208 Vac Utility Interactive Inverter | 1.5 | 208 | 95 | Y | N |  | 0.1 |  |  | 100 | 300 | 360 | 0.15 | 0.3 | 0.45 | 0.75 | 1.13 | 1.5 | 86.5 | 91.8 | 93.5 | 95 | 94.9 | 95.1 | 94.3 | 88.8 | 93.4 | 94.7 | 95.7 | 95.9 | 95.8 | 95.3 | 90.7 | 94.2 | 95.6 | 96.4 | 96.3 | 96.4 | 95.9
HiSEL Power | HiSEL-K 1500 [240V] | 1.5 kW, 240 Vac Utility Interactive Inverter | 1.5 | 240 | 95 | Y | N |  | 0.13 |  |  | 100 | 300 | 360 | 0.15 | 0.3 | 0.45 | 0.75 | 1.13 | 1.5 | 85.9 | 91.4 | 93.2 | 94.8 | 95 | 95.2 | 94.2 | 87.5 | 92.8 | 94.3 | 95.6 | 96 | 96 | 95.2 | 90.4 | 94 | 95 | 96 | 96.4 | 96.4 | 95.8
HiSEL Power | HiSEL-K 2000 [208V] | 2 kW, 208 Vac Utility Interactive Inverter | 2 | 208 | 95.5 | Y | N |  | 0.13 |  |  | 100 | 350 | 400 | 0.2 | 0.4 | 0.6 | 1 | 1.5 | 2 | 90.1 | 93.6 | 94.7 | 95.3 | 95.4 | 95.2 | 95 | 92.6 | 95 | 96 | 96.1 | 96.2 | 96 | 95.9 | 91.6 | 94.7 | 95.4 | 95.9 | 96.2 | 95.8 | 95.7
HiSEL Power | HiSEL-K 2000 [240V] | 2.8 kW, 240 Vac Utility Interactive Inverter | 2 | 240 | 96 | Y | N |  | 0.17 |  |  | 100 | 380 | 400 | 0.2 | 0.4 | 0.6 | 1 | 1.5 | 2 | 89.6 | 93.2 | 94.5 | 95.3 | 95.6 | 95.5 | 95 | 92.2 | 94.7 | 96 | 96.5 | 96.7 | 96.4 | 96.3 | 94.1 | 95.4 | 96.2 | 96.5 | 96.5 | 96.4 | 96.3
HiSEL Power | HiSEL-K 3000 [208V] | 2.8 kW, 208 Vac Utility Interactive Inverter | 2.8 | 208 | 96 | Y | N |  | 0.11 |  |  | 100 | 350 | 400 | 0.28 | 0.56 | 0.84 | 1.4 | 2.1 | 2.8 | 90.3 | 93.4 | 94.8 | 95.6 | 95.6 | 95.6 | 95.2 | 93.1 | 95.7 | 96.3 | 96.7 | 96.5 | 95.9 | 96.3 | 92 | 95 | 95.9 | 96.5 | 96.4 | 96 | 96.1
HiSEL Power | HiSEL-K 3000 [240V] | 4 kW, 240 Vac Utility Interactive Inverter | 2.8 | 240 | 96 | Y | N |  | 0.15 |  |  | 100 | 380 | 440 | 0.28 | 0.56 | 0.84 | 1.4 | 2.1 | 2.8 | 89.1 | 93 | 94.5 | 95.5 | 95.8 | 95.8 | 95.2 | 93.1 | 95.9 | 96.3 | 96.9 | 96.9 | 96.9 | 96.7 | 92.7 | 95.6 | 96.7 | 96.9 | 96.9 | 96.9 | 96.6
HiSEL Power | HiSEL-K 4000 [208V] | 4 kW, 208 Vac Utility Interactive Inverter | 4 | 208 | 97 | Y | N |  | 0.07 |  |  | 100 | 350 | 440 | 0.4 | 0.8 | 1.2 | 2 | 3 | 4 | 93.7 | 96.1 | 96.8 | 97.2 | 97.1 | 96.8 | 96.9 | 95.4 | 97.1 | 97.5 | 97.6 | 97.4 | 97.2 | 97.4 | 94 | 96.3 | 97 | 97.4 | 97.3 | 97.1 | 97.1
HiSEL Power | HiSEL-K 4000 [240V] | 4.6 kW, 240 Vac Utility Interactive Inverter | 4 | 240 | 97.5 | Y | N |  | 0.11 |  |  | 100 | 380 | 440 | 0.4 | 0.8 | 1.2 | 2 | 3 | 4 | 93.1 | 95.8 | 96.6 | 97.3 | 97.4 | 97.2 | 97 | 95.5 | 97.1 | 97.6 | 97.9 | 97.8 | 97.5 | 97.6 | 94.6 | 96.7 | 97.4 | 97.6 | 97.6 | 97.4 | 97.4
HiSEL Power | HiSEL-K 5000 [208V] | 4.6 kW, 208 Vac Utility Interactive Inverter | 4.6 | 208 | 97 | Y | N |  | 0.07 |  |  | 100 | 350 | 440 | 0.46 | 0.92 | 1.38 | 2.3 | 3.45 | 4.6 | 93.8 | 96.1 | 96.8 | 97.1 | 96.9 | 96.4 | 96.7 | 95.3 | 97 | 97.5 | 97.5 | 97.3 | 96.8 | 97.2 | 94 | 96.3 | 96.9 | 97.2 | 97.1 | 96.7 | 96.9
HiSEL Power | HiSEL-K 5000 [240V] | 4.6 kW, 240 Vac Utility Interactive Inverter | 4.6 | 240 | 97.5 | Y | N |  | 0.1 |  |  | 100 | 380 | 440 | 0.46 | 0.92 | 1.38 | 2.3 | 3.45 | 4.6 | 93.3 | 95.8 | 96.7 | 97.2 | 97.2 | 96.9 | 96.9 | 95.4 | 96.9 | 97.6 | 97.9 | 97.8 | 97.5 | 97.6 | 94.6 | 96.7 | 97.2 | 97.6 | 97.6 | 97.4 | 97.4
Home Director | HD-SUN-INV1100-EVR [120V] | 1100 W, 120 Vac Utility Interactive Inverter | 1.1 | 120 | 90.5 | Y | N |  | 3.6 |  |  | 100 | 182 | 380 | 0.11 | 0.22 | 0.33 | 0.55 | 0.83 | 1.1 | 81.8 | 89 | 90.9 | 92.1 | 92.4 | 92.5 | 91.6 | 79.9 | 88 | 90.1 | 91.7 | 92.2 | 92.3 | 91.1 | 74.8 | 84.7 | 87.8 | 90 | 90.8 | 91.1 | 89.3
Home Director | HD-SUN-INV2000-EVR [240V] | 2000 W, 240 Vac Utility Interactive Inverter | 2 | 240 | 92 | Y | N |  | 3.6 |  |  | 100 | 199 | 380 | 0.2 | 0.4 | 0.6 | 1 | 1.5 | 2 | 87.3 | 91.7 | 92.6 | 93.5 | 93.2 | 93 | 92.9 | 85.7 | 90.8 | 92.1 | 92.9 | 92.9 | 92.6 | 92.4 | 82.4 | 88.8 | 90.5 | 91.6 | 91.8 | 91.6 | 91.1
Home Director | HD-SUN-INV2500 [240V] | 2500 W, 240 Vac Utility Interactive Inverter | 2.5 | 240 | 94.5 | Y | N |  | 3.9 |  |  | 100 | 218 | 400 | 0.25 | 0.5 | 0.75 | 1.25 | 1.88 | 2.5 | 87.1 | 93.3 | 94.9 | 95.8 | 95.8 | 95.6 | 95.2 | 85.2 | 92.4 | 93.8 | 95.2 | 95.4 | 95.1 | 94.6 | 80.4 | 90 | 91.7 | 93.7 | 94.5 | 93.8 | 93.2
Home Director | HD-SUN-INV3000 [240V] | 3000 W, 240 Vac Utility Interactive Inverter | 3 | 240 | 93.5 | Y | N |  | 3.63 |  |  | 100 | 222.5 | 380 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 88.9 | 92.9 | 93.8 | 94.3 | 94.2 | 93.9 | 93.9 | 87.9 | 92.5 | 93.5 | 94.1 | 94 | 93.8 | 93.7 | 84.9 | 90.9 | 92.4 | 93.3 | 93.2 | 93 | 92.7
Home Director | HD-SUN-INV3500 [240V] | 3500 W, 240 Vac Utility Interactive Inverter | 3.5 | 240 | 95.5 | Y | N |  | 3.86 |  |  | 100 | 263 | 400 | 0.35 | 0.7 | 1.05 | 1.75 | 2.63 | 3.5 | 87.2 | 93.1 | 95.4 | 96.5 | 96.7 | 96.6 | 95.9 | 85.7 | 92.2 | 94.9 | 96.2 | 96.4 | 96.3 | 95.5 | 82.1 | 90.2 | 93.6 | 95.4 | 95.7 | 95.6 | 94.5
Home Director | HD-SUN-INV4600 [208V] | 4600 W, 208 Vac Utility Interactive Inverter | 4.6 | 208 | 95.5 | Y | N |  | 4 |  |  | 100 | 254 | 400 | 0.46 | 0.92 | 1.38 | 2.3 | 3.45 | 4.6 | 90.3 | 94.8 | 95.9 | 96.5 | 96.5 | 96.2 | 96.1 | 89.2 | 94.3 | 95.6 | 96.3 | 96.4 | 96.1 | 95.9 | 86.5 | 92.9 | 94.7 | 95.6 | 95.7 | 95.4 | 95
Home Director | HD-SUN-INV4800 [240V] | 4800 W, 240 Vac Utility Interactive Inverter | 4.8 | 240 | 96 | Y | N |  | 4.1 |  |  | 100 | 263 | 400 | 0.48 | 0.96 | 1.44 | 2.4 | 3.6 | 4.8 | 86.8 | 93.5 | 95.5 | 97 | 97.2 | 97.1 | 96.4 | 85.5 | 92.9 | 95 | 96.7 | 96.9 | 96.8 | 96 | 84.5 | 91.5 | 93.9 | 95.9 | 96.2 | 96.1 | 95.1
Home Director | HD-SUN-INV5200 [240V] | 5200 W, 240 Vac Utility Interactive Inverter | 5.2 | 240 | 96 | Y | N |  | 4 |  |  | 100 | 280 | 400 | 0.52 | 1.04 | 1.56 | 2.6 | 3.9 | 5.2 | 89.4 | 94.8 | 96 | 96.8 | 97 | 96.8 | 96.4 | 88.6 | 94.4 | 95.7 | 96.7 | 96.8 | 96.6 | 96.2 | 87.7 | 93.1 | 94.8 | 96.1 | 96.3 | 96.1 | 95.5
Hoymiles Converter Technology | MI-250 [240V] | 250 W, 240 Vac Utility Interactive Inverter | 0.25 | 240 | 96.5 | N | Y |  | 0.1 |  |  | 27 | 37 | 48 | 0.03 | 0.05 | 0.08 | 0.13 | 0.19 | 0.25 | 94.7 | 95.7 | 96.1 | 96.5 | 96.4 | 95.8 | 96.2 | 95.1 | 96 | 96.1 | 96.5 | 96.6 | 96.7 | 96.5 | 94.7 | 95.9 | 96 | 96.4 | 96.4 | 96.6 | 96.3
Hoymiles Converter Technology Co., Ltd. | MI-1200 [240V] | 1.2 kW, 240 Vac Utility Interactive Microinverter | 1.2132 | 240 | 96.5 | N | Y |  | 0.01461 |  |  | 32 | 40 | 48 | 0.12132 | 0.24264 | 0.36395 | 0.60659 | 0.90989 | 1.2132 | 95.813 | 96.1105 | 96.2544 | 96.6096 | 96.2797 | 95.4203 | 96.2758 | 95.8493 | 96.168 | 96.2843 | 96.5421 | 96.5331 | 96.0437 | 96.4351 | 95.3869 | 95.9598 | 96.2058 | 96.321 | 96.553 | 96.3013 | 96.3737 | 2019-01-15
Hoymiles Converter Technology Co., Ltd. | MI-1200T [240V] | 1.2 kW, 240 Vac Utility Interactive Microinverter | 1.2132 | 240 | 96.5 | N | Y |  | 0.01461 |  |  | 32 | 40 | 48 | 0.12132 | 0.24264 | 0.36395 | 0.60659 | 0.90989 | 1.2132 | 95.813 | 96.1105 | 96.2544 | 96.6096 | 96.2797 | 95.4203 | 96.2758 | 95.8493 | 96.168 | 96.2843 | 96.5421 | 96.5331 | 96.0437 | 96.4351 | 95.3869 | 95.9598 | 96.2058 | 96.321 | 96.553 | 96.3013 | 96.3737 | 2019-01-15
Huawei Technologies Co., Ltd. | SUN2000-3.8KTL-USL0 [240V] | 3.8 kW, 240 Vac 1-phase transformerless Utility Interactive Inverter | 3.8 | 240 | 99 | Y | N |  | 2.18 |  |  | 370 | 395 | 420 | 0.38 | 0.76 | 1.14 | 1.9 | 2.85 | 3.8 | 96.375 | 98.2332 | 98.6641 | 99.0028 | 99.0572 | 99.0776 | 98.8512 | 96.1637 | 98.1176 | 98.4788 | 98.9469 | 99.0231 | 99.0365 | 98.7828 | 96.0702 | 97.9945 | 98.4563 | 98.8641 | 98.9923 | 98.9967 | 98.7345 | 2018-07-16
Huawei Technologies Co., Ltd. | SUN2000-5KTL-USL0 [240V] | 5 kW, 240 Vac 1-phase transformerless Utility Interactive Inverter | 5 | 240 | 99 | Y | N |  | 2.07 |  |  | 370 | 395 | 420 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 97.0703 | 98.3856 | 98.7211 | 99.0239 | 99.0199 | 98.8703 | 98.8677 | 96.8811 | 98.3814 | 98.661 | 98.9319 | 98.966 | 98.8203 | 98.8023 | 96.6926 | 98.2929 | 98.5924 | 98.8825 | 98.8862 | 98.7742 | 98.7272 | 2018-07-16
Huawei Technologies Co., Ltd. | SUN2000-7.6KTL-USL0 [240V] | 7.6 kW, 240 Vac 1-phase transformerless Utility Interactive Inverter | 7.6 | 240 | 99 | Y | N |  | 2.06 |  |  | 370 | 395 | 420 | 0.76 | 1.52 | 2.28 | 3.8 | 5.7 | 7.6 | 98.0246 | 98.8109 | 98.9586 | 98.9973 | 98.9182 | 98.749 | 98.8901 | 97.8253 | 98.7187 | 98.917 | 98.9382 | 98.8674 | 98.7164 | 98.8316 | 97.6925 | 98.6266 | 98.8792 | 98.9113 | 98.8473 | 98.6766 | 98.7988 | 2018-07-16
Huawei Technologies Co., Ltd. | SUN2000-9KTL-USL0 [240V] | 9 kW, 240 Vac 1-phase transformerless Utility Interactive Inverter | 9 | 240 | 99 | Y | N |  | 1.97 |  |  | 370 | 395 | 420 | 0.9 | 1.8 | 2.7 | 4.5 | 6.75 | 9 | 97.6847 | 98.6455 | 98.9199 | 99.0618 | 99.0359 | 98.9738 | 98.9507 | 97.5338 | 98.5959 | 98.9052 | 99.0405 | 99.016 | 98.932 | 98.9233 | 97.5773 | 98.5984 | 98.8583 | 99.0241 | 99.0091 | 98.9183 | 98.9118 | 2018-07-16 | 2018-10-15
Huawei Technologies Co., Ltd. | SUN2000-10KTL-USL0 [240V] | 10 kW, 240 Vac 1-phase transformerless Utility Interactive Inverter | 10 | 240 | 99 | Y | N |  | 1.98 |  |  | 370 | 395 | 420 | 1 | 2 | 3 | 5 | 7.5 | 10 | 97.6401 | 98.656 | 98.9366 | 99.0483 | 99.013 | 98.9033 | 98.933 | 97.4485 | 98.548 | 98.8594 | 99.0041 | 98.9773 | 98.8792 | 98.8813 | 97.1851 | 98.4207 | 98.7677 | 98.933 | 98.9378 | 98.845 | 98.8158 | 2018-07-16 | 2018-10-15
Huawei Technologies Co., Ltd. | SUN2000-11.4KTL-USL0 [240V] | 11.4 kW, 240 Vac 1-phase transformerless Utility Interactive Inverter | 11.4 | 240 | 99 | Y | N |  | 1.97 |  |  | 370 | 395 | 420 | 1.14 | 2.28 | 3.42 | 5.7 | 8.55 | 11.4 | 97.8855 | 98.7855 | 98.9735 | 99.0471 | 98.9836 | 98.8375 | 98.9346 | 97.7154 | 98.6539 | 98.9173 | 98.9881 | 98.9407 | 98.8014 | 98.8775 | 97.5395 | 98.5822 | 98.8395 | 98.9436 | 98.9124 | 98.7749 | 98.8319 | 2018-07-16 | 2018-10-15
Huawei Technologies Co., Ltd. | SUN2000-22KTL-US | 22 kW transformerless Utility Interactive Inverter | 22.2 |  | 98 | N | N |  | 0.9 |  |  | 560 | 730 | 800 | 2.22 | 4.44 | 6.66 | 11.1 | 16.65 | 22.2 | 96 | 97.3 | 97.7 | 98 | 98 | 97.9 | 97.8 | 95.9 | 97.4 | 97.8 | 98.1 | 98.2 | 98.1 | 98 | 96.5 | 97.8 | 98.2 | 98.5 | 98.5 | 98.4 | 98.3 |  | 2018-05-01
Huawei Technologies Co., Ltd. | SUN2000-25KTL-US | 25 kW transformerless Utility Interactive Inverter | 25 |  | 98 | Y | N |  | 1 |  |  | 560 | 730 | 800 | 2.5 | 5 | 7.5 | 12.5 | 18.75 | 25 | 95.7 | 97.1 | 97.6 | 97.9 | 97.9 | 97.9 | 97.7 | 96.3 | 97.7 | 98.2 | 98.4 | 98.4 | 98.4 | 98.3 | 95.9 | 97.5 | 98 | 98.3 | 98.3 | 98.3 | 98.1 |  | 2018-05-01
Huawei Technologies Co., Ltd. | SUN2000-30KTL-US | 30 kW transformerless Utility Interactive Inverter | 30 |  | 98 | Y | N |  | 1 |  |  | 560 | 730 | 800 | 3 | 6 | 9 | 15 | 22.5 | 30 | 96.1 | 97.4 | 97.7 | 97.9 | 97.9 | 97.8 | 97.8 | 96.6 | 97.9 | 98.3 | 98.4 | 98.4 | 98.3 | 98.3 | 96.4 | 97.8 | 98.2 | 98.3 | 98.3 | 98.2 | 98.2 |  | 2018-05-01
Huawei Technologies Co., Ltd. | SUN2000-33KTL-US | 33 kW Utility Interactive Inverter | 33 |  | 98.5 | N | N |  | 1.8 |  |  | 460 | 720 | 850 | 3.3 | 6.6 | 9.9 | 16.5 | 24.75 | 33 | 95.6305 | 97.31 | 97.6239 | 97.8333 | 97.8889 | 97.7881 | 97.7211 | 97.5169 | 98.6741 | 98.8513 | 98.8841 | 98.8741 | 98.7894 | 98.8049 | 96.9145 | 98.1094 | 98.38 | 98.4576 | 98.4622 | 98.3838 | 98.3679 |  | 2018-05-01
Huawei Technologies Co., Ltd. | SUN2000-36KTL-US | 36 kW Utility Interactive Inverter | 36 |  | 98.5 | N | N |  | 1.8 |  |  | 490 | 720 | 850 | 3.6 | 7.2 | 10.8 | 18 | 27 | 36 | 96.4077 | 97.5458 | 97.8137 | 97.9912 | 97.9878 | 97.8775 | 97.8768 | 97.9739 | 98.7413 | 98.8734 | 98.8955 | 98.8578 | 98.762 | 98.8216 | 97.1101 | 98.2156 | 98.4158 | 98.4713 | 98.4443 | 98.3524 | 98.3771 |  | 2018-05-01
Huawei Technologies Co., Ltd. | SUN2000-40KTL-US | 40 kW Utility Interactive Inverter | 40 |  | 98.5 | N | N |  | 1.8 |  |  | 530 | 720 | 850 | 4 | 8 | 12 | 20 | 30 | 40 | 96.7485 | 97.7289 | 97.9466 | 98.102 | 98.049 | 97.9087 | 97.9728 | 98.0538 | 98.7273 | 98.7781 | 98.8628 | 98.7907 | 98.8053 | 98.7724 | 97.2662 | 98.2155 | 98.3638 | 98.4571 | 98.3764 | 98.4169 | 98.3414 |  | 2018-05-01
Huawei Technologies Co., Ltd. | SUN2000-45KTL-US-HV-D0 | 45 kW transformerless Utility Interactive Inverter | 45.207 |  | 98.5 | N | N |  | 1.11 |  |  | 800 | 1000 | 1200 | 97.5 | 98.1 | 98.2 | 98.2 | 98.1 | 97.9 | 98.2 | 98.6 | 98.7 | 98.6 | 98.5 | 98.4 | 98.5 | 98.2 | 98.6 | 98.7 | 98.6 | 98.5 | 98.4 | 98.5 | 98.1 | 98.5 | 98.5 | 98.5 | 98.4 | 98.2 | 98.4 |  | 2018-05-01
Huawei Technologies Co., Ltd. | SUN2000-100KTL-USH0 [800V] | 100 kW, 800 Vac, 3-phase transformerless Utility Interactive Inverter | 100 | 800 | 98.5 | N | N |  | 2.61 |  |  | 880 | 1120 | 1200 | 10 | 20 | 30 | 50 | 75 | 100 | 97.2971 | 98.0491 | 98.3042 | 98.447 | 98.4104 | 98.3164 | 98.338 | 97.6913 | 98.412 | 98.5995 | 98.6923 | 98.6594 | 98.5739 | 98.6037 | 98.2248 | 98.7907 | 98.9363 | 98.9879 | 98.9811 | 98.631 | 98.9199 | 2018-05-01
HYOSUNG | HS-P1000GLO-U | 1000 kW Utility Interactive Inverter | 991.4 |  | 98 | N | N |  | 177.45 |  |  | 600 | 665 | 880 | 99.14 | 198.28 | 297.42 | 495.7 | 743.55 | 991.4 | 96.2085 | 97.7725 | 98.2235 | 98.4344 | 98.3905 | 98.213 | 98.2526 | 95.5901 | 97.4963 | 98.0225 | 98.3115 | 98.318 | 98.1791 | 98.124 | 93.7224 | 96.1179 | 96.9934 | 97.458 | 97.5495 | 97.4122 | 97.232
Ideal Power Inc | 30C [480V] | 30 kW, 480 Vac Utility Interactive Battery Charge controller | 29.99 | 480 | 95 | N | N |  | 56.8 |  |  | 550 | 700 | 850 | 3 | 6 | 9 | 15 | 22.49 | 29.99 | 92.7 | 94.3 | 94.8 | 95.2 | 95.1 | 94.8 | 94.9 | 92.2 | 94.2 | 94.6 | 95.3 | 95.4 | 95.5 | 95.1 | 89.6 | 92.8 | 93.3 | 94.8 | 95.2 | 95.4 | 94.6 | 2018-02-01 | 2018-12-01
Ideal Power Inc | 30C3 [480V] | 30 kW, 480 Vac Utility Interactive Battery Charge controller with additional Photovoltaic input | 29.99 | 480 | 95 | N | N |  | 56.8 |  |  | 550 | 700 | 850 | 3 | 6 | 9 | 15 | 22.49 | 29.99 | 92.7 | 94.3 | 94.8 | 95.2 | 95.1 | 94.8 | 94.9 | 92.2 | 94.2 | 94.6 | 95.3 | 95.4 | 95.5 | 95.1 | 89.6 | 92.8 | 93.3 | 94.8 | 95.2 | 95.4 | 94.6 | 2018-02-01 | 2018-12-01
Ideal Power Inc | 30PV | 30 kW Utility Interactive Inverter | 29.99 |  | 95 | N | N |  | 51.2 |  |  | 550 | 700 | 850 | 3 | 6 | 9 | 15 | 22.49 | 29.99 | 92.3 | 94.4 | 94.8 | 95.2 | 95.2 | 94.8 | 95 | 91.3 | 94 | 94.6 | 95.3 | 95.4 | 95.3 | 95 | 88.7 | 92.1 | 93.4 | 94.7 | 95.1 | 95.5 | 94.4 | 2017-05 | 2018-08-15
Ideal Power Inc | 30PV+S [480V] | 30 kW, 480 Vac Utility Interactive Inverter with PV and Battery Input for ground referenced arrays and batteries | 29.99 | 480 | 95 | N | N |  | 51.2 |  |  | 550 | 700 | 850 | 3 | 6 | 9 | 15 | 22.49 | 29.99 | 92.3 | 94.4 | 94.8 | 95.2 | 95.2 | 94.8 | 95 | 91.3 | 94 | 94.6 | 95.3 | 95.4 | 95.3 | 95 | 88.7 | 92.1 | 93.4 | 94.7 | 95.1 | 95.5 | 94.4 | 2018-02-01 | 2018-12-01
Ideal Power Inc | 30PVF | 30 kW Utility Interactive Inverter | 29.99 |  | 95 | N | N |  | 51.2 |  |  | 550 | 700 | 850 | 3 | 6 | 9 | 15 | 22.49 | 29.99 | 92.3 | 94.4 | 94.8 | 95.2 | 95.2 | 94.8 | 95 | 91.3 | 94 | 94.6 | 95.3 | 95.4 | 95.3 | 95 | 88.7 | 92.1 | 93.4 | 94.7 | 95.1 | 95.5 | 94.4 | 2017-05 | 2018-08-15
Ideal Power Inc | 30PVF+S [480V] | 30 kW, 480 Vac Utility Interactive Inverter with PV and Battery Input for floating ground referenced arrays and batteries | 29.99 | 480 | 95 | N | N |  | 51.2 |  |  | 550 | 700 | 850 | 3 | 6 | 9 | 15 | 22.49 | 29.99 | 92.3 | 94.4 | 94.8 | 95.2 | 95.2 | 94.8 | 95 | 91.3 | 94 | 94.6 | 95.3 | 95.4 | 95.3 | 95 | 88.7 | 92.1 | 93.4 | 94.7 | 95.1 | 95.5 | 94.4 | 2018-02-01 | 2018-10-15
Ideal Power Inc | IPV-30 kW-480 [480V] | 30 kW, 480 Vac, 3-Phase Utility Interactive Inverter | 30.07 | 480 | 96.5 | Y | N |  | 9.83 |  |  | 600 | 800 | 900 | 3.01 | 6.01 | 9.02 | 15.04 | 22.56 | 30.07 | 95.2 | 96 | 96.3 | 96.5 | 96.5 | 96.2 | 96.4 | 95.1 | 96.1 | 96.4 | 96.7 | 96.6 | 96.3 | 96.5 | 94.2 | 95.6 | 96.1 | 96.5 | 96.5 | 96.2 | 96.3 |  | 2018-08-15
i-Energy | GT260 [240V] | 210 W, 240 Vac Utility Interactive Inverter | 0.23 | 240 | 92 | N | N |  | 0.15 |  |  | 30 | 40 | 49 | 0.02 | 0.05 | 0.07 | 0.12 | 0.17 | 0.23 | 85.9 | 90.8 | 90.4 | 92.7 | 93.4 | 93.4 | 92.5 | 84.7 | 89.2 | 89.7 | 92.5 | 93.7 | 93.6 | 92.4 | 83 | 87.4 | 89.9 | 90.8 | 92.7 | 93.6 | 91.4
INGETEAM POWER TECHNOLOGY S.A | INGECON SUN 1140TL U B410 [410V] | 1136 kVA, 410 Vac Utility Interactive Inverter for PV and Battery Applications. | 1027.752 | 410 | 97.5 | N | N | Overall efficiency includes Ingeteam transformer packaged with product. Per SGS, revision I of ABK 1000 was tested per UL 1741 SA. Revisions J, K, and L were considered with no influence regarding grid support compliance. | 2550.2775 |  |  | 595 | 668 | 800 | 102.7752 | 205.5504 | 308.3256 | 513.876 | 770.814 | 1027.752 | 95.8625 | 97.4417 | 97.8113 | 97.8912 | 97.7441 | 97.3829 | 97.6746 | 95.6736 | 97.3781 | 97.7557 | 97.8606 | 97.7193 | 97.3781 | 97.6374 | 95.14 | 97.0801 | 97.524 | 97.6897 | 97.5561 | 97.213 | 97.4427 | 2019-05-01
INGETEAM POWER TECHNOLOGY S.A | INGECON SUN 1245TL U B480 [480V] | 1247 kVA, 480 Vac Utility Interactive Inverter for PV and Battery Applications. | 1042.22 | 480 | 97.5 | N | N | Overall efficiency includes Ingeteam transformer packaged with product. Per SGS, revision I of ABK 1000 was tested per UL 1741 SA. Revisions J, K, and L were considered with no influence regarding grid support compliance. | 459.0724 |  |  | 697 | 949 | 1200 | 104.222 | 208.444 | 312.666 | 521.11 | 781.665 | 1042.22 | 96.9037 | 97.6188 | 97.803 | 97.7395 | 97.5015 | 97.1174 | 97.5504 | 96.4047 | 97.431 | 97.5993 | 97.4719 | 97.2822 | 96.859 | 97.3113 | 96.026 | 97.0747 | 97.3979 | 97.2268 | 96.9903 | 96.5138 | 97.0307 | 2019-05-01
INGETEAM POWER TECHNOLOGY S.A | INGECON SUN 1190TL U B430 [430V] | 1192 kVA, 430 Vac Utility Interactive Inverter for PV and Battery Applications. | 1048.594 | 430 | 97.5 | N | N | Overall efficiency includes Ingeteam transformer packaged with product. Per SGS, revision I of ABK 1000 was tested per UL 1741 SA. Revisions J, K, and L were considered with no influence regarding grid support compliance. | 2550.2775 |  |  | 624 | 682 | 800 | 104.8594 | 209.7188 | 314.5782 | 524.297 | 786.4455 | 1048.594 | 96.0041 | 97.4811 | 97.8373 | 97.9231 | 97.7893 | 97.4138 | 97.7176 | 95.8692 | 97.4303 | 97.7966 | 97.9039 | 97.781 | 97.4506 | 97.6982 | 95.3825 | 97.1832 | 97.5935 | 97.7411 | 97.6496 | 97.3174 | 97.5314 | 2019-05-01
INGETEAM POWER TECHNOLOGY S.A | INGECON SUN 1220TL U B440 [440V] | 1217 kVA, 440 Vac Utility Interactive Inverter for PV and Battery Applications. | 1099.306 | 440 | 97.5 | N | N | Overall efficiency includes Ingeteam transformer packaged with product. Per SGS, revision I of ABK 1000 was tested per UL 1741 SA. Revisions J, K, and L were considered with no influence regarding grid support compliance. | 2550.2775 |  |  | 638 | 689 | 800 | 109.9306 | 219.8612 | 329.7918 | 549.653 | 824.4795 | 1099.306 | 95.932 | 97.4927 | 97.868 | 97.9487 | 97.8105 | 97.4537 | 97.7375 | 95.8363 | 97.4652 | 97.8509 | 97.9442 | 97.8039 | 97.4677 | 97.7266 | 95.4261 | 97.2395 | 97.6478 | 97.8037 | 97.6832 | 97.3514 | 97.5752 | 2019-05-01
INGETEAM POWER TECHNOLOGY S.A | INGECON SUN 1250TL U B450 [450V] | 1247 kVA, 450 Vac Utility Interactive Inverter for PV and Battery Applications. | 1114.104 | 450 | 97.5 | N | N | Overall efficiency includes Ingeteam transformer packaged with product. Per SGS, revision I of ABK 1000 was tested per UL 1741 SA. Revisions J, K, and L were considered with no influence regarding grid support compliance. | 2550.2775 |  |  | 652 | 696 | 800 | 111.4104 | 222.8208 | 334.2312 | 557.052 | 835.578 | 1114.104 | 95.9706 | 97.5016 | 97.8688 | 97.9364 | 97.8103 | 97.4968 | 97.7391 | 95.9001 | 97.4837 | 97.855 | 97.9743 | 97.8316 | 97.5204 | 97.7542 | 95.5073 | 97.2604 | 97.6982 | 97.8443 | 97.7172 | 97.4132 | 97.6152 | 2019-05-01
INGETEAM POWER TECHNOLOGY S.A | INGECON SUN 1275TL U B460 [460V] | 1275 kVA, 460 Vac Utility Interactive Inverter for PV and Battery Applications. | 1128.476 | 460 | 97.5 | N | N | Overall efficiency includes Ingeteam transformer packaged with product. Per SGS, revision I of ABK 1000 was tested per UL 1741 SA. Revisions J, K, and L were considered with no influence regarding grid support compliance. | 2550.2775 |  |  | 666 | 703 | 800 | 112.8476 | 225.6952 | 338.5428 | 564.238 | 846.357 | 1128.476 | 95.9938 | 97.508 | 97.8617 | 97.9706 | 97.8442 | 97.6278 | 97.7712 | 95.8888 | 97.4823 | 97.8709 | 97.9916 | 97.8671 | 97.5597 | 97.7799 | 95.5429 | 97.3202 | 97.7334 | 97.9123 | 97.7635 | 97.4905 | 97.6665 | 2019-05-01
INGETEAM POWER TECHNOLOGY S.A | INGECON SUN 1740TL U B670 [670V] | 1741 kVA, 670 Vac Utility Interactive Inverter for PV and Battery Applications. | 1272.412 | 670 | 97.5 | N | N | Overall efficiency includes Ingeteam transformer packaged with product. Per SGS, revision I of ABK 1000 was tested per UL 1741 SA. Revisions J, K, and L were considered with no influence regarding grid support compliance. | 459.0724 |  |  | 962 | 1081 | 1200 | 127.2412 | 254.4824 | 381.7236 | 636.206 | 954.309 | 1272.412 | 95.9646 | 97.3748 | 97.6902 | 97.7604 | 97.6287 | 97.348 | 97.5704 | 95.7313 | 97.2879 | 97.5573 | 97.697 | 97.5442 | 97.223 | 97.4764 | 95.3778 | 97.1365 | 97.419 | 97.506 | 97.402 | 97.144 | 97.3188 | 2019-05-01
INGETEAM POWER TECHNOLOGY S.A | INGECON SUN 1800TL U B690 [690V] | 1793 kVA, 690 Vac Utility Interactive Inverter for PV and Battery Applications. | 1300.644 | 690 | 97.5 | N | N | Overall efficiency includes Ingeteam transformer packaged with product. Per SGS, revision I of ABK 1000 was tested per UL 1741 SA. Revisions J, K, and L were considered with no influence regarding grid support compliance. | 459.0724 |  |  | 962 | 1081 | 1200 | 130.0644 | 260.1288 | 390.1932 | 650.322 | 975.483 | 1300.644 | 96.6717 | 97.6652 | 97.8788 | 97.9021 | 97.7538 | 97.399 | 97.7345 | 96.4722 | 97.5961 | 97.804 | 97.828 | 97.6778 | 97.3356 | 97.6551 | 96.3335 | 97.5145 | 97.7082 | 97.7346 | 97.5625 | 97.2579 | 97.5493 | 2019-05-01
INGETEAM POWER TECHNOLOGY S.A | INGECON SUN 1665TL U B640 [640V] | 1663 kVA, 640 Vac Utility Interactive Inverter for PV and Battery Applications. | 1367.076 | 640 | 97.5 | N | N | Overall efficiency includes Ingeteam transformer packaged with product. Per SGS, revision I of ABK 1000 was tested per UL 1741 SA. Revisions J, K, and L were considered with no influence regarding grid support compliance. | 459.0724 |  |  | 919 | 1060 | 1200 | 136.7076 | 273.4152 | 410.1228 | 683.538 | 1025.307 | 1367.076 | 96.2495 | 97.4423 | 97.7204 | 97.755 | 97.6184 | 97.3123 | 97.5805 | 95.9772 | 97.3141 | 97.5906 | 97.6697 | 97.5061 | 97.1929 | 97.4642 | 95.5155 | 97.1401 | 97.4064 | 97.4529 | 97.3426 | 97.0371 | 97.2749 | 2019-05-01
INGETEAM POWER TECHNOLOGY S.A | INGECON SUN 1690TL U B650 [650V] | 1689 kVA, 650 Vac Utility Interactive Inverter for PV and Battery Applications. | 1375.282 | 650 | 97.5 | N | N | Overall efficiency includes Ingeteam transformer packaged with product. Per SGS, revision I of ABK 1000 was tested per UL 1741 SA. Revisions J, K, and L were considered with no influence regarding grid support compliance. | 459.0724 |  |  | 933 | 1067 | 1200 | 137.5282 | 275.0564 | 412.5846 | 687.641 | 1031.4615 | 1375.282 | 96.2881 | 97.5051 | 97.7757 | 97.8183 | 97.6619 | 97.3581 | 97.6304 | 96.0008 | 97.4016 | 97.6638 | 97.7405 | 97.5736 | 97.2501 | 97.5318 | 95.6676 | 97.2627 | 97.5419 | 97.5575 | 97.4238 | 97.0851 | 97.3708 | 2019-05-01
INGETEAM POWER TECHNOLOGY S.A | INGECON SUN 1715TL U B660 [660V] | 1715 kVA, 660 Vac Utility Interactive Inverter for PV and Battery Applications. | 1390.614 | 660 | 97.5 | N | N | Overall efficiency includes Ingeteam transformer packaged with product. Per SGS, revision I of ABK 1000 was tested per UL 1741 SA. Revisions J, K, and L were considered with no influence regarding grid support compliance. | 459.0724 |  |  | 948 | 1074 | 1200 | 139.0614 | 278.1228 | 417.1842 | 695.307 | 1042.9605 | 1390.614 | 96.0622 | 97.4034 | 97.6863 | 97.7536 | 97.622 | 97.3392 | 97.5699 | 95.8419 | 97.2707 | 97.5502 | 97.7009 | 97.5384 | 97.2305 | 97.4773 | 95.3647 | 97.1092 | 97.4005 | 97.5253 | 97.4034 | 97.0865 | 97.3166 | 2019-05-01
INGETEAM POWER TECHNOLOGY S.A. | Ingecon Sun 2.8 HF U 208 Vac [208V] | 2.8 kW, 208 Vac, 1-phase, Indoor/Outdoor Utility Interactive Inverter | 2.8 | 208 | 95 | Y | N |  | 0.5 |  |  | 100 | 371 | 500 | 0.28 | 0.56 | 0.84 | 1.4 | 2.1 | 2.8 | 88.8 | 93.2 | 94.1 | 94.7 | 94.3 | 93.8 | 94.1 | 91.2 | 94.8 | 95.8 | 96.1 | 95.9 | 95.3 | 95.6 | 87.8 | 92.5 | 94.9 | 95.9 | 96 | 95.7 | 95.3 |  | 2018-05-15
INGETEAM POWER TECHNOLOGY S.A. | Ingecon Sun 2.8 HF U 240 Vac [240V] | 2.8 kW, 240 Vac, 1-phase, Indoor/Outdoor Utility Interactive Inverter | 2.8 | 240 | 95.5 | Y | N |  | 0.5 |  |  | 100 | 371 | 500 | 0.28 | 0.56 | 0.84 | 1.4 | 2.1 | 2.8 | 87.3 | 92.7 | 93.9 | 94.7 | 94.7 | 94.6 | 94.2 | 90.3 | 94.7 | 95.7 | 96.5 | 96.4 | 96.1 | 96 | 88.5 | 93.8 | 95.1 | 96.2 | 96.4 | 96.2 | 95.8 |  | 2018-05-15
INGETEAM POWER TECHNOLOGY S.A. | Ingecon Sun 2.8 HF U 277Vac [277V] | 2.8 kW, 277 Vac, 1-phase, Indoor/Outdoor Utility Interactive Inverter | 2.8 | 277 | 95.5 | Y | N |  | 0.5 |  |  | 100 | 371 | 500 | 0.28 | 0.56 | 0.84 | 1.4 | 2.1 | 2.8 | 85.2 | 91.9 | 93.6 | 94.6 | 94.7 | 94.6 | 94 | 88.8 | 94.1 | 95.6 | 96.6 | 96.5 | 96.7 | 96 | 88.3 | 94 | 95.3 | 96.5 | 96.7 | 96.7 | 96 |  | 2018-05-15
INGETEAM POWER TECHNOLOGY S.A. | Ingecon Sun 2.8 TL U M 208 Vac [208V] | 2.8 kW, 208 Vac, 1-phase, Indoor/Outdoor Utility Interactive Inverter | 2.8 | 208 | 97 | Y | N |  | 0.5 |  |  | 100 | 600 | 750 | 0.28 | 0.56 | 0.84 | 1.4 | 2.1 | 2.8 | 90.1 | 95 | 96 | 96.3 | 95.7 | 95.2 | 95.6 | 94.2 | 97.3 | 97.9 | 98.2 | 98.5 | 98.4 | 98.2 | 93.4 | 96.5 | 97.4 | 97.9 | 98 | 98 | 97.7 |  | 2018-05-15
INGETEAM POWER TECHNOLOGY S.A. | Ingecon Sun 2.8 TL U M 240 Vac [240V] | 2.8 kW, 240 Vac, 1-phase, Indoor/Outdoor Utility Interactive Inverter | 2.8 | 240 | 97 | Y | N |  | 0.5 |  |  | 100 | 600 | 750 | 0.28 | 0.56 | 0.84 | 1.4 | 2.1 | 2.8 | 88.6 | 94.2 | 95.5 | 96 | 95.5 | 94.9 | 95.2 | 92.9 | 97 | 97.9 | 98.4 | 98.6 | 98.5 | 98.1 | 93.2 | 96.6 | 97.6 | 98.3 | 98.4 | 98.4 | 98 |  | 2018-05-15
INGETEAM POWER TECHNOLOGY S.A. | Ingecon Sun 3.3 HF U 208 Vac [208V] | 3.3 kW, 208 Vac, 1-phase, Indoor/Outdoor Utility Interactive Inverter | 3.3 | 208 | 95 | Y | N |  | 0.5 |  |  | 100 | 371 | 500 | 0.33 | 0.66 | 0.99 | 1.65 | 2.47 | 3.3 | 89.1 | 93.5 | 94.3 | 94.5 | 94.1 | 93.6 | 94 | 92.2 | 95.3 | 95.9 | 96 | 95.6 | 95.2 | 95.6 | 89.8 | 94.2 | 95.3 | 96 | 96 | 95.7 | 95.6 |  | 2018-05-15
INGETEAM POWER TECHNOLOGY S.A. | Ingecon Sun 3.3 HF U 240 Vac [240V] | 3.3 kW, 240 Vac, 1-phase, Indoor/Outdoor Utility Interactive Inverter | 3.3 | 240 | 95.5 | Y | N |  | 0.5 |  |  | 100 | 427 | 500 | 0.33 | 0.66 | 0.99 | 1.65 | 2.47 | 3.3 | 88.5 | 92.9 | 94.2 | 94.6 | 94.4 | 94.1 | 94.1 | 91.3 | 95.1 | 96 | 96.5 | 96.3 | 96.1 | 96 | 88.8 | 94.3 | 95.6 | 96.3 | 96.4 | 96.2 | 95.9 |  | 2018-05-15
INGETEAM POWER TECHNOLOGY S.A. | Ingecon Sun 3.3 HF U 277Vac [277V] | 3.3 kW, 277 Vac, 1-phase, Indoor/Outdoor Utility Interactive Inverter | 3.3 | 277 | 95.5 | Y | N |  | 0.5 |  |  | 100 | 482 | 500 | 0.33 | 0.66 | 0.99 | 1.65 | 2.47 | 3.3 | 86.1 | 92.4 | 93.7 | 94.7 | 94.5 | 94.2 | 94 | 87.8 | 94.3 | 95.7 | 96.8 | 96.9 | 97 | 96.2 | 88.8 | 94.5 | 95.6 | 96.5 | 96.6 | 96.5 | 96.1 |  | 2018-05-15
INGETEAM POWER TECHNOLOGY S.A. | Ingecon Sun 3.3 TL U M 208 Vac [208V] | 3.3 kW, 208 Vac, 1-phase, Indoor/Outdoor Utility Interactive Inverter | 3.3 | 208 | 97.5 | Y | N |  | 0.5 |  |  | 100 | 600 | 750 | 0.33 | 0.66 | 0.99 | 1.65 | 2.47 | 3.3 | 90.4 | 95.8 | 96.3 | 96.7 | 96.1 | 95.3 | 96 | 94.9 | 97.6 | 98.1 | 98.4 | 98.3 | 98 | 98.1 | 94 | 96.8 | 97.7 | 98 | 98 | 97.9 | 97.8 |  | 2018-05-15
INGETEAM POWER TECHNOLOGY S.A. | Ingecon Sun 3.3 TL U M 240 Vac [240V] | 3.3 kW, 240 Vac, 1-phase, Indoor/Outdoor Utility Interactive Inverter | 3.3 | 240 | 97.5 | Y | N |  | 0.5 |  |  | 100 | 690 | 750 | 0.33 | 0.66 | 0.99 | 1.65 | 2.47 | 3.3 | 89.4 | 95 | 96.1 | 96.4 | 96 | 95.3 | 95.7 | 94.3 | 97.5 | 98.1 | 98.5 | 98.5 | 98.4 | 98.2 | 93.9 | 97.2 | 98 | 98.3 | 98.4 | 98.4 | 98.1 |  | 2018-05-15
INGETEAM POWER TECHNOLOGY S.A. | INGECON SUN 3.6TL U 208V [208V] | 3.6 kW, 208 Vac, 1-phase Utility Interactive Inverter | 3.6 | 208 | 96 | Y | N |  | 0.5 |  |  | 100 | 300 | 450 | 0.36 | 0.72 | 1.08 | 1.8 | 2.7 | 3.6 | 91.6 | 95.4 | 96.1 | 96.5 | 96.3 | 96 | 96.1 | 92.8 | 96.1 | 96.8 | 97.2 | 97.2 | 96.9 | 96.9 | 85.4 | 92.9 | 94.5 | 95.7 | 96 | 95.9 | 95.1 |  | 2018-05-15
INGETEAM POWER TECHNOLOGY S.A. | INGECON SUN 3.6TL U 240V [240V] | 3.6 kW, 240 Vac, 1-phase Utility Interactive Inverter | 3.6 | 240 | 96.5 | Y | N |  | 0.5 |  |  | 100 | 380 | 450 | 0.36 | 0.72 | 1.08 | 1.8 | 2.7 | 3.6 | 90.5 | 94.6 | 95.7 | 96.4 | 96.5 | 96.3 | 96 | 91.9 | 95.7 | 96.7 | 97.4 | 97.6 | 97.5 | 97.1 | 87.5 | 93.4 | 95.1 | 96.4 | 96.8 | 96.8 | 96 |  | 2018-05-15
INGETEAM POWER TECHNOLOGY S.A. | INGECON SUN 3.6TL U 277 [277V] | 3.6 kW, 277 Vac, 1-phase Utility Interactive Inverter | 3.6 | 277 | 96.5 | Y | N |  | 50 |  |  | 100 | 380 | 450 | 0.36 | 0.72 | 1.08 | 1.8 | 2.7 | 3.6 | 89 | 93.7 | 95.1 | 96.2 | 96.4 | 96.3 | 95.7 | 91.2 | 95.8 | 97 | 97.7 | 98 | 98 | 97.4 | 88 | 94.2 | 95.7 | 96.9 | 97.3 | 97.4 | 96.5 |  | 2018-05-15
INGETEAM POWER TECHNOLOGY S.A. | Ingecon Sun 5 HF U 208 Vac [208V] | 5 kW, 208 Vac, 1-phase, Indoor/Outdoor Utility Interactive Inverter | 5 | 208 | 95 | Y | N |  | 0.5 |  |  | 100 | 376 | 500 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 92.3 | 94.8 | 95.1 | 94.7 | 93.9 | 93.7 | 94.2 | 94.3 | 95.9 | 96 | 95.4 | 94.4 | 93.9 | 94.9 | 92.5 | 95.3 | 95.9 | 95.8 | 95.2 | 94.5 | 95.3 |  | 2018-05-15
INGETEAM POWER TECHNOLOGY S.A. | Ingecon Sun 5 HF U 240 Vac [240V] | 5 kW, 240 Vac, 1-phase, Indoor/Outdoor Utility Interactive Inverter | 5 | 240 | 96 | Y | N |  | 0.5 |  |  | 100 | 427 | 500 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 92.1 | 95 | 95.7 | 95.5 | 94.8 | 94.3 | 94.9 | 94.7 | 96.9 | 97.3 | 97.1 | 96.9 | 96.8 | 96.9 | 93.1 | 96 | 96.6 | 96.7 | 96.1 | 95.8 | 96.2 |  | 2018-05-15
INGETEAM POWER TECHNOLOGY S.A. | Ingecon Sun 5 HF U 277Vac [277V] | 5 kW, 277 Vac, 1-phase, Indoor/Outdoor Utility Interactive Inverter | 5 | 277 | 95.5 | Y | N |  | 0.5 |  |  | 100 | 482 | 500 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 90.2 | 93.5 | 94.5 | 94.6 | 94.4 | 94 | 94.2 | 92.3 | 95.4 | 96 | 96.3 | 96 | 95.5 | 95.8 | 92.8 | 95.3 | 96 | 96.2 | 95.9 | 95.5 | 95.8 |  | 2018-05-15
INGETEAM POWER TECHNOLOGY S.A. | Ingecon Sun 5 TL U M 208 Vac [208V] | 5 kW, 208 Vac, 1-phase, Indoor/Outdoor Utility Interactive Inverter | 5 | 208 | 97.5 | Y | N |  | 0.5 |  |  | 100 | 600 | 750 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 93 | 96.4 | 97.1 | 97.1 | 96.4 | 95.6 | 96.5 | 96.2 | 98 | 98.2 | 98.1 | 97.9 | 97.6 | 97.9 | 95.3 | 97.4 | 97.7 | 97.8 | 97.5 | 97.2 | 97.5 |  | 2018-05-15
INGETEAM POWER TECHNOLOGY S.A. | Ingecon Sun 5 TL U M 240 Vac [240V] | 5 kW, 240 Vac, 1-phase, Indoor/Outdoor Utility Interactive Inverter | 5 | 240 | 97.5 | Y | N |  | 0.5 |  |  | 100 | 690 | 750 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 92.4 | 96 | 96.9 | 97.1 | 96.6 | 96 | 96.5 | 95.9 | 98 | 98.3 | 98.4 | 98.3 | 98 | 98.2 | 95.5 | 97.6 | 98.1 | 98.3 | 98.1 | 97.9 | 98 |  | 2018-05-15
INGETEAM POWER TECHNOLOGY S.A. | Ingecon Sun 5TL U [208V] | 5 kW, 208 Vac, 1-phase Utility Interactive Inverter | 5 | 208 | 96 | Y | N |  | 0.5 |  |  | 100 | 300 | 450 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 90.2 | 94.4 | 95.3 | 95.6 | 95.5 | 95.2 | 95.2 | 93.1 | 95.6 | 96.4 | 96.9 | 96.8 | 96.7 | 96.5 | 90.3 | 94.3 | 95.3 | 96 | 96.1 | 96 | 95.6 |  | 2018-05-15
INGETEAM POWER TECHNOLOGY S.A. | Ingecon Sun 5TL U [240V] | 5 kW, 240 Vac, 1-phase Utility Interactive Inverter | 5 | 240 | 96 | Y | N |  | 0.5 |  |  | 100 | 340 | 450 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 90.2 | 94.4 | 95.3 | 95.6 | 95.5 | 95.2 | 95.2 | 93.1 | 95.6 | 96.4 | 96.9 | 96.8 | 96.7 | 96.5 | 90.3 | 94.3 | 95.3 | 96 | 96.1 | 96 | 95.6 |  | 2018-05-15
INGETEAM POWER TECHNOLOGY S.A. | Ingecon Sun 5TL U [277V] | 5 kW, 277 Vac, 1-phase Utility Interactive Inverter | 5 | 277 | 96 | Y | N |  | 0.5 |  |  | 100 | 380 | 450 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 90.2 | 93.7 | 94.9 | 95.5 | 95.5 | 95.4 | 95.1 | 93 | 95.5 | 96.7 | 97.1 | 97.2 | 97.1 | 96.8 | 90.8 | 94.7 | 95.8 | 96.5 | 96.6 | 96.6 | 96.1 |  | 2018-05-15
INGETEAM POWER TECHNOLOGY S.A. | Ingecon Sun 5U [208V] | 5 kW, 208 Vac, 1-phase Utility Interactive Inverter | 5 | 208 | 95 | Y | N |  | 0.5 |  |  | 100 | 300 | 450 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 90.92 | 94.34 | 94.85 | 94.82 | 94.15 | 93.29 | 94.21 | 93.12 | 95.21 | 95.86 | 95.76 | 95.18 | 94.44 | 95.27 | 91.62 | 94.8 | 95.35 | 95.43 | 94.98 | 94.25 | 94.94 |  | 2018-05-15
INGETEAM POWER TECHNOLOGY S.A. | Ingecon Sun 5U [240V] | 5 kW, 240 Vac, 1-phase Utility Interactive Inverter | 5 | 240 | 95 | Y | N |  | 0.5 |  |  | 100 | 340 | 450 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 90 | 93.7 | 94.5 | 94.8 | 94.5 | 93.9 | 94.3 | 92.2 | 95.1 | 96.1 | 96.3 | 96 | 95.6 | 95.8 | 91.6 | 94.9 | 95.7 | 95.9 | 95.7 | 95.3 | 95.5 |  | 2018-05-15
INGETEAM POWER TECHNOLOGY S.A. | Ingecon Sun 5U [277V] | 5 kW, 277 Vac, 1-phase Utility Interactive Inverter | 5 | 277 | 95.5 | Y | N |  | 0.5 |  |  | 100 | 380 | 450 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 88 | 92.7 | 94 | 94.5 | 94.5 | 94.1 | 94.1 | 91.4 | 94.9 | 96 | 96.5 | 96.4 | 96.2 | 96.1 | 90.8 | 94.8 | 95.7 | 96.2 | 96.2 | 96 | 95.9 |  | 2018-05-15
INGETEAM POWER TECHNOLOGY S.A. | Ingecon Sun 6 HF U 240 Vac [240V] | 6 kW, 240 Vac, 1-phase, Indoor/Outdoor Utility Interactive Inverter | 6 | 240 | 95.5 | Y | N |  | 0.5 |  |  | 100 | 427 | 500 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 92.6 | 95 | 95.1 | 95 | 94.1 | 94.5 | 94.4 | 94.6 | 96.1 | 96.2 | 96.3 | 95.9 | 95.5 | 96 | 93.7 | 95.8 | 96.2 | 96 | 95.3 | 94.5 | 95.5 |  | 2018-05-15
INGETEAM POWER TECHNOLOGY S.A. | Ingecon Sun 6 HF U 277Vac [277V] | 6 kW, 277 Vac, 1-phase, Indoor/Outdoor Utility Interactive Inverter | 6 | 277 | 95 | Y | N |  | 0.5 |  |  | 100 | 482 | 500 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 91.5 | 94.1 | 94.6 | 94.9 | 94.3 | 93.7 | 94.3 | 93.8 | 95.7 | 96.2 | 96.1 | 95.7 | 95.2 | 95.7 | 93.9 | 95.7 | 96.2 | 96.1 | 95.7 | 95.1 | 95.7 |  | 2018-05-15
INGETEAM POWER TECHNOLOGY S.A. | Ingecon Sun 6 TL U M 240 Vac [240V] | 6 kW, 240 Vac, 1-phase, Indoor/Outdoor Utility Interactive Inverter | 6 | 240 | 98 | Y | N |  | 0.5 |  |  | 100 | 690 | 750 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 94 | 97 | 97.6 | 97.6 | 97.2 | 96.6 | 97.2 | 96.9 | 98.6 | 98.9 | 98.8 | 98.6 | 98.3 | 98.6 | 96.4 | 98.4 | 98.6 | 98.6 | 98.4 | 98.1 | 98.4 |  | 2018-05-15
INGETEAM POWER TECHNOLOGY S.A. | INGECON SUN 6TL U 240 [240V] | 6 kW, 240 Vac, 1-phase Utility Interactive Inverter | 6 | 240 | 96.5 | Y | N |  | 0.5 |  |  | 100 | 240 | 450 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 92.6 | 95.3 | 95.9 | 96.1 | 95.9 | 95.4 | 95.8 | 94.7 | 96.9 | 97.3 | 97.5 | 97.4 | 97.2 | 97.3 | 91.8 | 95.1 | 95.9 | 96.4 | 96.5 | 96.3 | 96.1 |  | 2018-05-15
INGETEAM POWER TECHNOLOGY S.A. | INGECON SUN 6TL U 277V [277V] | 6 kW, 277 Vac, 1-phase Utility Interactive Inverter | 6 | 277 | 97 | Y | N |  | 0.5 |  |  | 100 | 277 | 450 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 92 | 94.9 | 95.7 | 96.1 | 96 | 95.6 | 95.7 | 94.6 | 97 | 97.5 | 97.7 | 97.7 | 97.5 | 97.5 | 91.9 | 95.6 | 96.5 | 96.9 | 97.1 | 97 | 96.7 |  | 2018-05-15
INGETEAM POWER TECHNOLOGY S.A. | INGECON SUN 7.5TL U 208 [208V] | 7.5 kW, 208 Vac, 1-phase Utility Interactive Inverter | 7.5 | 208 | 96.5 | Y | N |  | 0.5 |  |  | 100 | 300 | 450 | 0.75 | 1.5 | 2.25 | 3.75 | 5.63 | 7.5 | 94.3 | 96.3 | 96.6 | 96.5 | 96.2 | 95.6 | 96.2 | 94.8 | 96.9 | 97.3 | 97.3 | 97.2 | 96.6 | 97.1 | 90.1 | 94.6 | 95.5 | 96.1 | 96.1 | 95.8 | 95.7 |  | 2018-05-15
INGETEAM POWER TECHNOLOGY S.A. | INGECON SUN 7.5TL U 240 [240V] | 7.5 kW, 240 Vac, 1-phase Utility Interactive Inverter | 7.5 | 240 | 96.5 | Y | N |  | 0.5 |  |  | 100 | 400 | 450 | 0.75 | 1.5 | 2.25 | 3.75 | 5.625 | 7.5 | 93.3 | 96 | 96.5 | 96.6 | 96.4 | 96.1 | 96.3 | 92.6 | 95.9 | 96.6 | 97.1 | 97 | 96.8 | 96.7 | 90.8 | 95.2 | 96.1 | 96.7 | 96.7 | 96.5 | 96.3 |  | 2018-05-15
INGETEAM POWER TECHNOLOGY S.A. | INGECON SUN 7.5TL U 277 [277V] | 7.5 kW, 277 Vac, 1-phase Utility Interactive Inverter | 7.5 | 277 | 97 | Y | N |  | 0.5 |  |  | 100 | 400 | 450 | 0.75 | 1.5 | 2.25 | 3.75 | 5.625 | 7.5 | 91.7 | 95.3 | 96.1 | 96.4 | 96.3 | 96 | 96.1 | 93.3 | 96.6 | 97.3 | 97.8 | 97.8 | 97.8 | 97.5 | 91.3 | 95.7 | 96.6 | 97.2 | 97.3 | 97.3 | 96.9 |  | 2018-05-15
INGETEAM POWER TECHNOLOGY S.A. | INGECON SUN 8.6TL U 240 [240V] | 8.6 kW, 240 Vac, 1-phase Utility Interactive Inverter | 8.6 | 240 | 96.5 | Y | N |  | 0.5 |  |  | 100 | 400 | 450 | 0.86 | 1.72 | 2.58 | 4.3 | 6.45 | 8.6 | 94 | 96.3 | 96.7 | 96.7 | 96.5 | 96 | 96.4 | 93 | 96 | 96.8 | 97 | 96.9 | 96.6 | 96.7 | 91.9 | 95.6 | 96.3 | 96.7 | 96.7 | 96.5 | 96.4 |  | 2018-05-15
INGETEAM POWER TECHNOLOGY S.A. | INGECON SUN 8.6TL U 277 [277V] | 8.6 kW, 277 Vac, 1-phase Utility Interactive Inverter | 8.6 | 277 | 97 | Y | N |  | 0.5 |  |  | 100 | 400 | 450 | 0.86 | 1.72 | 2.58 | 4.3 | 6.45 | 8.6 | 93 | 95.7 | 96.4 | 96.6 | 96.4 | 96 | 96.3 | 94.2 | 96.9 | 97.4 | 97.8 | 97.7 | 97.6 | 97.5 | 92.6 | 96.1 | 96.8 | 97.3 | 97.3 | 97.1 | 97 |  | 2018-05-15
INGETEAM POWER TECHNOLOGY S.A. | INGECON SUN 10TL U [277V] | 10 kW, 277 Vac, 1-phase Utility Interactive Inverter | 10 | 277 | 97 | Y | N |  | 0.5 |  |  | 100 | 400 | 450 | 1 | 2 | 3 | 5 | 7.5 | 10 | 93.9 | 96.4 | 96.9 | 97.1 | 96.8 | 96.4 | 96.7 | 94.9 | 97.1 | 97.6 | 97.8 | 97.7 | 97.5 | 97.5 | 93.6 | 96.4 | 97 | 97.3 | 97.2 | 97 | 97 |  | 2018-05-15
INGETEAM POWER TECHNOLOGY S.A. | Ingecon Sun 15U [208V] | 15 kW, 208 Vac, 3-phase Utility Interactive Inverter | 15 | 208 | 95 | Y | N |  | 2 | 15 | 2 | 300 | 350 | 480 | 1.5 | 3 | 4.5 | 7.5 | 11.25 | 15 | 90.17 | 94.59 | 95.28 | 95.55 | 95.43 | 95.02 | 95.16 | 89.77 | 94.46 | 95.07 | 95.41 | 95.3 | 94.95 | 95.01 | 88.88 | 94.01 | 94.62 | 95 | 94.95 | 94.66 | 94.62 |  | 2018-05-15
INGETEAM POWER TECHNOLOGY S.A. | Ingecon Sun 15U [480V] | 15 kW, 480 Vac, 3-phase Utility Interactive Inverter | 15 | 480 | 95 | Y | N |  | 4 | 15 | 4 | 300 | 350 | 480 | 1.5 | 3 | 4.5 | 7.5 | 11.25 | 15 | 89.89 | 93.84 | 94.85 | 95.66 | 95.6 | 95.28 | 95.19 | 89.52 | 93.58 | 94.69 | 95.53 | 95.51 | 95.24 | 95.07 | 88.3 | 92.84 | 94.15 | 95.13 | 95.08 | 94.92 | 94.59 |  | 2018-05-15
INGETEAM POWER TECHNOLOGY S.A. | Ingecon Sun 18 TL U M [480V] | 18 kW, 480 Vac, 3-phase transformerless, Indoor/Outdoor Utility Interactive Inverter | 18 | 480 | 98 | Y | N |  | 10 |  |  | 375 | 700 | 820 | 1.8 | 3.6 | 5.4 | 9 | 13.5 | 18 | 93.9 | 96.1 | 96.4 | 96.8 | 96.8 | 96.7 | 96.6 | 96.7 | 98.2 | 98.5 | 98.7 | 98.7 | 98.6 | 98.6 | 95.8 | 97.8 | 98.2 | 98.5 | 98.5 | 98.5 | 98.3 |  | 2018-05-15
INGETEAM POWER TECHNOLOGY S.A. | Ingecon Sun 24 TL U M [480V] | 24 kW, 480 Vac, 3-phase transformerless, Indoor/Outdoor Utility Interactive Inverter | 24 | 480 | 98 | Y | N |  | 10 |  |  | 460 | 700 | 820 | 2.4 | 4.8 | 7.2 | 12 | 18 | 24 | 95.7 | 97.1 | 97.2 | 97.3 | 97.2 | 97 | 97.1 | 97.8 | 98.6 | 98.7 | 98.7 | 98.6 | 98.5 | 98.6 | 97.2 | 98.2 | 98.5 | 98.5 | 98.4 | 98.3 | 98.4 |  | 2018-05-15
INGETEAM POWER TECHNOLOGY S.A. | Ingecon Sun 25U [208V] | 25 kW, 208 Vac, 3-phase Utility Interactive Inverter | 25 | 208 | 95.5 | Y | N |  | 2 | 25 | 2 | 300 | 350 | 480 | 2.5 | 5 | 7.5 | 12.5 | 18.75 | 25 | 91.45 | 94.79 | 95.72 | 96.09 | 95.92 | 95.5 | 95.67 | 90.99 | 94.59 | 95.53 | 95.99 | 95.9 | 95.48 | 95.59 | 90.34 | 94.03 | 95.14 | 95.67 | 95.58 | 95.05 | 95.23 |  | 2018-05-15
INGETEAM POWER TECHNOLOGY S.A. | Ingecon Sun 25U [480V] | 25 kW, 480 Vac, 3-phase Utility Interactive Inverter | 25 | 480 | 95.5 | Y | N |  | 4 | 25 | 4 | 300 | 350 | 480 | 2.5 | 5 | 7.5 | 12.5 | 18.75 | 25 | 90.88 | 94.57 | 95.53 | 95.95 | 95.8 | 95.33 | 95.52 | 90.47 | 94.45 | 95.44 | 95.91 | 95.77 | 95.34 | 95.46 | 89.83 | 93.95 | 95.01 | 95.52 | 95.43 | 95.02 | 95.08 |  | 2018-05-15
INGETEAM POWER TECHNOLOGY S.A. | Ingecon Sun 40TL U M [480V] | 40 kW, 480 Vac, 3-phase, Indoor/Outdoor Utility Interactive Inverter | 39.95 | 480 | 98 | Y | N |  | 10 |  |  | 520 | 700 | 820 | 3.9 | 8 | 12.1 | 19.2 | 30.1 | 40.1 | 96.74 | 97.78 | 97.76 | 97.55 | 97.15 | 96.61 | 97.28 | 97.69 | 98.32 | 98.48 | 98.29 | 97.95 | 97.68 | 98.08 | 96.93 | 97.91 | 98.14 | 98.11 | 97.86 | 97.51 | 97.9 |  | 2018-05-15
INGETEAM POWER TECHNOLOGY S.A. | Ingecon Sun 100U [208V] | 100 kW, 208 Vac, 3-phase Utility Interactive Inverter | 100 | 208 | 94.5 | Y | N |  | 1 |  |  | 300 | 350 | 480 | 10 | 20 | 30 | 50 | 75 | 100 | 90.82 | 94.01 | 94.82 | 95.34 | 95.08 | 93.88 | 94.82 | 90.27 | 93.75 | 94.58 | 95.15 | 95.04 | 93.75 | 94.69 | 89.04 | 92.9 | 93.9 | 94.75 | 94.31 | 93.33 | 94.02 |  | 2018-05-15
INGETEAM POWER TECHNOLOGY S.A. | Ingecon Sun 100U [240V] | 100 kW, 240 Vac, 3-phase Utility Interactive Inverter | 100 | 240 | 94.5 | Y | N |  | 3 |  |  | 300 | 350 | 480 | 10 | 20 | 30 | 50 | 75 | 100 | 90.85 | 94.14 | 94.86 | 95.17 | 95.09 | 93.98 | 94.81 | 90.33 | 93.83 | 94.68 | 95.05 | 94.99 | 93.86 | 94.66 | 88.99 | 92.99 | 93.99 | 94.61 | 94.41 | 93.54 | 94.07 |  | 2018-05-15
INGETEAM POWER TECHNOLOGY S.A. | Ingecon Sun 100UP [208V] | 100 kW, 208 Vac, 3-phase Utility Interactive Inverter | 100 | 208 | 95 | Y | N |  | 1 | 100 | 1 | 300 | 350 | 480 | 10 | 20 | 30 | 50 | 75 | 100 | 91.53 | 94.8 | 95.45 | 95.79 | 95.69 | 94.57 | 95.41 | 91.06 | 94.55 | 95.25 | 95.65 | 95.55 | 94.67 | 95.26 | 89.83 | 93.76 | 94.6 | 95.2 | 95.16 | 94.4 | 94.78 |  | 2018-05-15
INGETEAM POWER TECHNOLOGY S.A. | Ingecon Sun 100UP [480V] | 100 kW, 480 Vac, 3-phase Utility Interactive Inverter | 100 | 480 | 95.5 | Y | N |  | 2 | 100 | 2 | 300 | 350 | 480 | 10 | 20 | 30 | 50 | 75 | 100 | 91.91 | 95.03 | 95.69 | 95.95 | 95.84 | 94.83 | 95.6 | 91.44 | 94.7 | 95.5 | 95.81 | 95.71 | 94.7 | 95.43 | 90.22 | 94 | 94.91 | 95.38 | 95.33 | 94.33 | 94.97 |  | 2018-05-15
INGETEAM POWER TECHNOLOGY S.A. | INGECON SUN 125 TL U 208 Outdoor [208V] | 125 kW, 208 Vac, 3-phase Utility Interactive Inverter | 125 | 208 | 96.5 | Y | N |  | 1 |  |  | 350 | 550 | 750 | 12.5 | 25 | 37.5 | 62.5 | 93.75 | 125 | 93.9 | 96.5 | 96.9 | 97 | 96.7 | 96 | 96.6 | 92.4 | 95.7 | 96.4 | 96.7 | 96.4 | 95.8 | 96.3 | 91 | 95.1 | 95.9 | 96.3 | 96.1 | 95.8 | 95.9 |  | 2018-05-15
INGETEAM POWER TECHNOLOGY S.A. | INGECON SUN 125 U 208 Outdoor [208V] | 125 kW, 208 Vac, 3-phase Utility Interactive Inverter | 125 | 208 | 96.5 | Y | N |  | 1 |  |  | 350 | 550 | 750 | 12.5 | 25 | 37.5 | 62.5 | 93.75 | 125 | 93.7 | 96.4 | 97 | 97.2 | 96.7 | 96.5 | 96.7 | 92.3 | 95.6 | 96.4 | 96.6 | 96.3 | 96.2 | 96.2 | 91.2 | 94.9 | 96 | 96.6 | 96 | 95.9 | 95.9 |  | 2018-10-15
INGETEAM POWER TECHNOLOGY S.A. | INGECON SUN 125 U 480 Outdoor [480V] | 125 kW, 480 Vac, 3-phase Utility Interactive Inverter | 125 | 480 | 96.5 | Y | N |  | 1 |  |  | 350 | 550 | 750 | 12.5 | 25 | 37.5 | 62.5 | 93.75 | 125 | 93.8 | 96.5 | 97.1 | 97.3 | 97.1 | 96.7 | 97 | 92.4 | 95.8 | 96.5 | 96.8 | 96.8 | 96.4 | 96.5 | 91.1 | 95 | 95.9 | 96.3 | 96.4 | 96.1 | 96 |  | 2018-05-15
INGETEAM POWER TECHNOLOGY S.A. | INGECON SUN 165 TL U 275 Outdoor [275V] | 165 kW, 275Vac, 3-phase Utility Interactive Inverter | 165 | 275 | 97 | Y | N |  | 1 |  |  | 460 | 605 | 750 | 16.5 | 33 | 49.5 | 82.5 | 123.8 | 165 | 94 | 96.7 | 97.2 | 97.4 | 97.1 | 96.5 | 97 | 93.2 | 96.2 | 96.9 | 97.2 | 96.9 | 96.5 | 96.7 | 92.4 | 95.9 | 96.6 | 96.9 | 96.7 | 96.3 | 96.5 |  | 2018-05-15
INGETEAM POWER TECHNOLOGY S.A. | INGECON SUN 200 TL U 330 Outdoor [330V] | 200 kW, 330Vac, 3-phase Utility Interactive Inverter | 200 | 330 | 97.5 | Y | N |  | 1 |  |  | 550 | 650 | 750 | 20 | 40 | 60 | 100 | 150 | 200 | 94.5 | 97 | 97.5 | 97.7 | 97.5 | 97 | 97.4 | 94 | 96.7 | 97.3 | 97.6 | 97.4 | 97 | 97.2 | 93.5 | 96.6 | 97.2 | 97.5 | 97.3 | 96.9 | 97.1 |  | 2018-05-15
INGETEAM POWER TECHNOLOGY S.A. | INGECON SUN 220 TL U 360 Outdoor [360V] | 220 kW, 360Vac, 3-phase Utility Interactive Inverter | 220 | 360 | 97.5 | Y | N |  | 1 |  |  | 600 | 675 | 750 | 22 | 44 | 66 | 110 | 165 | 220 | 94.2 | 96.9 | 97.5 | 97.6 | 97.5 | 97 | 97.33 | 93.8 | 96.7 | 97.3 | 97.5 | 97.4 | 97 | 97.22 | 93.8 | 96.7 | 97.1 | 97.5 | 97.4 | 96.9 | 97.21 |  | 2018-05-15
INGETEAM POWER TECHNOLOGY S.A. | INGECON SUN 375TL X208 Indoor [208V] | 375 kW, 208 Vac, 3-phase Utility Interactive Inverter | 375 | 208 | 96.5 | Y | N |  | 90 |  |  | 350 | 550 | 750 | 37.5 | 75 | 112.5 | 187.5 | 281.3 | 375 | 96 | 96.7 | 96.7 | 97 | 96.7 | 95.7 | 96.7 | 95.2 | 96.1 | 96.3 | 96.6 | 96.4 | 95.7 | 96.4 | 94.6 | 95.6 | 95.9 | 96.2 | 96.1 | 95.4 | 96 |  | 2018-05-15
INGETEAM POWER TECHNOLOGY S.A. | INGECON SUN 375TL X208 Outdoor [208V] | 375 kW, 208 Vac, 3-phase Utility Interactive Inverter | 375 | 208 | 96.5 | Y | N |  | 90 |  |  | 350 | 550 | 750 | 37.5 | 75 | 112.5 | 187.5 | 281.3 | 375 | 96 | 96.7 | 96.7 | 97 | 96.7 | 95.7 | 96.7 | 95.2 | 96.1 | 96.3 | 96.6 | 96.4 | 95.7 | 96.4 | 94.6 | 95.6 | 95.9 | 96.2 | 96.1 | 95.4 | 96 |  | 2018-05-15
INGETEAM POWER TECHNOLOGY S.A. | INGECON SUN 500T U X480 Indoor [208V] | 500 kW, 208 Vac, 3-phase Utility Interactive Inverter | 500 | 208 | 96.5 | Y | N | Discontinued | 120 |  |  | 350 | 550 | 750 | 50 | 100 | 150 | 250 | 375 | 500 | 95.3 | 96.8 | 97.2 | 97.1 | 96.6 | 95.8 | 96.7 | 94.8 | 96.3 | 96.7 | 96.7 | 96.3 | 95.7 | 96.4 | 94.3 | 95.7 | 96.1 | 96.3 | 96 | 95.4 | 96 |  | 2018-05-15
INGETEAM POWER TECHNOLOGY S.A. | INGECON SUN 500T U X480 Outdoor [208V] | 500 kW, 208 Vac, 3-phase Utility Interactive Inverter | 500 | 208 | 96.5 | Y | N | Discontinued | 120 |  |  | 350 | 550 | 750 | 50 | 100 | 150 | 250 | 375 | 500 | 95.3 | 96.8 | 97.2 | 97.1 | 96.6 | 95.8 | 96.7 | 94.8 | 96.3 | 96.7 | 96.7 | 96.3 | 95.7 | 96.4 | 94.3 | 95.7 | 96.1 | 96.3 | 96 | 95.4 | 96 |  | 2018-05-15
INGETEAM POWER TECHNOLOGY S.A. | INGECON SUN 500TL U X208 Indoor [208V] | 500 kW, 208 Vac, 3-phase Utility Interactive Inverter | 500 | 208 | 96.5 | Y | N |  | 120 |  |  | 350 | 550 | 750 | 50 | 100 | 150 | 250 | 375 | 500 | 96.2 | 96.6 | 96.8 | 96.9 | 96.6 | 95.9 | 96.6 | 95.5 | 96 | 96.2 | 96.5 | 96.4 | 95.9 | 96.3 | 95 | 95.4 | 95.6 | 96.1 | 96.1 | 95.5 | 95.9 |  | 2018-05-15
INGETEAM POWER TECHNOLOGY S.A. | INGECON SUN 500TL U X208 Outdoor [208V] | 500 kW, 208 Vac, 3-phase Utility Interactive Inverter | 500 | 208 | 96.5 | Y | N |  | 120 |  |  | 350 | 550 | 750 | 50 | 100 | 150 | 250 | 375 | 500 | 96.2 | 96.6 | 96.8 | 96.9 | 96.6 | 95.9 | 96.6 | 95.5 | 96 | 96.2 | 96.5 | 96.4 | 95.9 | 96.3 | 95 | 95.4 | 95.6 | 96.1 | 96.1 | 95.5 | 95.9 |  | 2018-05-15
INGETEAM POWER TECHNOLOGY S.A. | INGECON SUN 500TL U X275 Indoor [275V] | 500 kW, 3-phase, 275 Vac indoor, grid-tie photovoltaic Inverter | 500 | 275 | 97 | Y | N |  | 90 |  |  | 460 | 605 | 750 | 50 | 100 | 150 | 250 | 375 | 500 | 96.1 | 96.9 | 97 | 97.4 | 97.2 | 96.5 | 97.2 | 95.8 | 96.6 | 96.8 | 97.2 | 97.1 | 96.4 | 97 | 95.3 | 96.2 | 96.5 | 96.9 | 96.9 | 96.3 | 96.7 |  | 2018-05-15
INGETEAM POWER TECHNOLOGY S.A. | INGECON SUN 600TL U X330 Indoor [330V] | 600 kW, 3-phase, 330 Vac indoor, grid-tie photovoltaic Inverter | 600 | 330 | 97 | Y | N |  | 90 |  |  | 550 | 650 | 750 | 60 | 120 | 180 | 300 | 450 | 600 | 96.2 | 97 | 97.2 | 97.6 | 97.5 | 96.9 | 97.4 | 95.9 | 96.7 | 97 | 97.5 | 97.4 | 96.8 | 97.2 | 95.7 | 96.5 | 96.9 | 97.3 | 97.3 | 96.7 | 97.1 |  | 2018-05-15
INGETEAM POWER TECHNOLOGY S.A. | INGECON SUN 600TL U X330 Outdoor [330V] | 600 kW, 3-phase, 330 Vac outdoor, grid-tie photovoltaic Inverter | 600 | 330 | 97 | Y | N |  | 90 |  |  | 550 | 650 | 750 | 60 | 120 | 180 | 300 | 450 | 600 | 96.2 | 97 | 97.2 | 97.6 | 97.5 | 96.9 | 97.4 | 95.9 | 96.7 | 97 | 97.5 | 97.4 | 96.8 | 97.2 | 95.7 | 96.5 | 96.9 | 97.3 | 97.3 | 96.7 | 97.1 |  | 2018-05-15
INGETEAM POWER TECHNOLOGY S.A. | INGECON SUN 600TL X330 Outdoor [330V] | 600 kW, 330Vac, 3-phase Utility Interactive Inverter | 600 | 330 | 97 | Y | N |  | 90 |  |  | 550 | 650 | 750 | 60 | 120 | 180 | 300 | 450 | 600 | 96.2 | 97 | 97.2 | 97.6 | 97.5 | 96.9 | 97.4 | 95.9 | 96.7 | 97 | 97.5 | 97.4 | 96.8 | 97.2 | 95.7 | 96.5 | 96.9 | 97.3 | 97.3 | 96.7 | 97.1 |  | 2018-05-15
INGETEAM POWER TECHNOLOGY S.A. | Ingecon Sun 610TL U B220 Indoor [220V] | 610 kW, 220Vac, 3-phase Indoor Utility Interactive Inverter | 610 | 220 | 97.5 | N | N | Weighted efficiency includes transformer efficiency of Elettromil ABN0001ICM05/610. | 80 |  |  | 440 | 590 | 740 | 61 | 122 | 183 | 305 | 457.5 | 610 | 97.11 | 98.06 | 98.25 | 98.17 | 97.74 | 97.1 | 97.85 | 96.37 | 97.64 | 98.01 | 97.9 | 97.48 | 96.73 | 97.56 | 95.53 | 97.29 | 97.68 | 97.72 | 97.45 | 96.53 | 97.41 |  | 2018-05-15
INGETEAM POWER TECHNOLOGY S.A. | Ingecon Sun 610TL U B220 Outdoor [300V] | 610 kW, 300Vac, 3-phase Outdoor Utility Interactive Inverter | 610 | 300 | 97.5 | N | N | Weighted efficiency includes transformer efficiency of Elettromil ABN0001ICM05/610. | 80 |  |  | 440 | 590 | 740 | 61 | 122 | 183 | 305 | 457.5 | 610 | 97.11 | 98.06 | 98.25 | 98.17 | 97.74 | 97.1 | 97.85 | 96.37 | 97.64 | 98.01 | 97.9 | 97.48 | 96.73 | 97.56 | 95.53 | 97.29 | 97.68 | 97.72 | 97.45 | 96.53 | 97.41 |  | 2018-05-15
INGETEAM POWER TECHNOLOGY S.A. | INGECON SUN 660TL U X275 Indoor [275V] | 660 kW, 275Vac, 3-phase Utility Interactive Inverter | 660 | 275 | 97 | Y | N |  | 120 |  |  | 460 | 605 | 750 | 66 | 132 | 198 | 330 | 495 | 660 | 96.3 | 96.8 | 97.1 | 97.3 | 97.1 | 96.5 | 97.1 | 96 | 96.5 | 96.7 | 97 | 97 | 96.6 | 96.9 | 95.7 | 96.1 | 96.4 | 96.8 | 96.8 | 96.3 | 96.6 |  | 2018-05-15
INGETEAM POWER TECHNOLOGY S.A. | INGECON SUN 660TL U X275 Outdoor [275V] | 660 kW, 275Vac, 3-phase Utility Interactive Inverter | 660 | 275 | 97 | Y | N |  | 120 |  |  | 460 | 605 | 750 | 66 | 132 | 198 | 330 | 495 | 660 | 96.3 | 96.8 | 97.1 | 97.3 | 97.1 | 96.5 | 97.1 | 96 | 96.5 | 96.7 | 97 | 97 | 96.6 | 96.9 | 95.7 | 96.1 | 96.4 | 96.8 | 96.8 | 96.3 | 96.6 |  | 2018-05-15
INGETEAM POWER TECHNOLOGY S.A. | INGECON SUN 660TL X360 Indoor [360V] | 660 kW, 360Vac, 3-phase Utility Interactive Inverter | 660 | 360 | 97.5 | Y | N |  | 90 |  |  | 605 | 677 | 750 | 66 | 132 | 198 | 330 | 495 | 660 | 96.2 | 97 | 97.1 | 97.7 | 97.6 | 97 | 97.4 | 96.1 | 96.9 | 97.2 | 97.6 | 97.5 | 97 | 97.4 | 95.9 | 96.7 | 97.1 | 97.5 | 97.4 | 96.9 | 97.3 |  | 2018-05-15
INGETEAM POWER TECHNOLOGY S.A. | INGECON SUN 660TL X360 Outdoor [360V] | 660 kW, 360Vac, 3-phase Utility Interactive Inverter | 660 | 360 | 97.5 | Y | N |  | 90 |  |  | 605 | 677 | 750 | 66 | 132 | 198 | 330 | 495 | 660 | 96.2 | 97 | 97.1 | 97.7 | 97.6 | 97 | 97.4 | 96.1 | 96.9 | 97.2 | 97.6 | 97.5 | 97 | 97.4 | 95.9 | 96.7 | 97.1 | 97.5 | 97.4 | 96.9 | 97.3 |  | 2018-05-15
INGETEAM POWER TECHNOLOGY S.A. | INGECON SUN 800TL U X330 Indoor [330V] | 800 kW, 330Vac, 3-phase Utility Interactive Inverter | 800 | 330 | 97 | Y | N |  | 120 |  |  | 550 | 650 | 750 | 80 | 160 | 240 | 400 | 600 | 800 | 96.5 | 96.9 | 97.2 | 97.4 | 97.4 | 96.9 | 97.3 | 96.3 | 96.7 | 96.9 | 97.3 | 97.3 | 96.9 | 97.2 | 96.1 | 96.4 | 96.7 | 97.1 | 97.2 | 96.7 | 97 |  | 2018-05-15
INGETEAM POWER TECHNOLOGY S.A. | INGECON SUN 800TL U X330 Outdoor [330V] | 800 kW, 330Vac, 3-phase Utility Interactive Inverter | 800 | 330 | 97 | Y | N |  | 120 |  |  | 550 | 650 | 750 | 80 | 160 | 240 | 400 | 600 | 800 | 96.5 | 96.9 | 97.2 | 97.4 | 97.4 | 96.9 | 97.3 | 96.3 | 96.7 | 96.9 | 97.3 | 97.3 | 96.9 | 97.2 | 96.1 | 96.4 | 96.7 | 97.1 | 97.2 | 96.7 | 97 |  | 2018-05-15
INGETEAM POWER TECHNOLOGY S.A. | Ingecon Sun 830TL U B300 Indoor [300V] | 830 kW, 300Vac, 3-phase Indoor Utility Interactive Inverter | 830 | 300 | 97.5 | N | N | Weighted efficiency includes transformer efficiency of Elettromil ABN0001ICM05/830. | 80 |  |  | 440 | 590 | 740 | 83 | 166 | 249 | 415 | 622.5 | 830 | 97.21 | 98.13 | 98.27 | 98.16 | 97.74 | 97.18 | 97.86 | 96.5 | 97.77 | 97.96 | 97.92 | 97.55 | 97.06 | 97.62 | 95.7 | 97.41 | 97.7 | 97.66 | 97.36 | 96.88 | 97.38 |  | 2018-05-15
INGETEAM POWER TECHNOLOGY S.A. | Ingecon Sun 830TL U B300 Outdoor [300V] | 830 kW, 300Vac, 3-phase Outdoor Utility Interactive Inverter | 830 | 300 | 97.5 | N | N | Weighted efficiency includes transformer efficiency of Elettromil ABN0001ICM05/830. | 80 |  |  | 440 | 590 | 740 | 83 | 166 | 249 | 415 | 622.5 | 830 | 97.21 | 98.13 | 98.27 | 98.16 | 97.74 | 97.18 | 97.86 | 96.5 | 97.77 | 97.96 | 97.92 | 97.55 | 97.06 | 97.62 | 95.7 | 97.41 | 97.7 | 97.66 | 97.36 | 96.88 | 97.38 |  | 2018-05-15
INGETEAM POWER TECHNOLOGY S.A. | INGECON SUN 880TL X360 Indoor [360V] | 880 kW, 360Vac, 3-phase Utility Interactive Inverter | 880 | 360 | 97.5 | Y | N |  | 120 |  |  | 605 | 677 | 750 | 88 | 176 | 264 | 440 | 660 | 880 | 96.5 | 96.9 | 97.2 | 97.5 | 97.5 | 97 | 97.4 | 96.4 | 96.8 | 97 | 97.4 | 97.5 | 97 | 97.3 | 96.3 | 96.6 | 96.9 | 97.3 | 97.4 | 96.9 | 97.2 |  | 2018-05-15
INGETEAM POWER TECHNOLOGY S.A. | INGECON SUN 880TL X360 Outdoor [360V] | 880 kW, 360Vac, 3-phase Utility Interactive Inverter | 880 | 360 | 97.5 | Y | N |  | 120 |  |  | 605 | 677 | 750 | 88 | 176 | 264 | 440 | 660 | 880 | 96.5 | 96.9 | 97.2 | 97.5 | 97.5 | 97 | 97.4 | 96.4 | 96.8 | 97 | 97.4 | 97.5 | 97 | 97.3 | 96.3 | 96.6 | 96.9 | 97.3 | 97.4 | 96.9 | 97.2 |  | 2018-05-15
INGETEAM POWER TECHNOLOGY S.A. | Ingecon Sun 915TL U B330 Indoor [330V] | 915 kW, 330Vac, 3-phase Indoor Utility Interactive Inverter | 915 | 330 | 97.5 | N | N | Weighted efficiency includes transformer efficiency of Elettromil ABN0001ICM05/915. | 80 |  |  | 485 | 613 | 740 | 91.5 | 183 | 274.5 | 457.5 | 686.25 | 915 | 97.17 | 98.13 | 98.33 | 98.22 | 97.86 | 97.27 | 97.95 | 96.5 | 97.84 | 98.09 | 98.05 | 97.69 | 97.15 | 97.75 | 95.82 | 97.49 | 97.82 | 97.81 | 97.51 | 97.17 | 97.53 |  | 2018-05-15
INGETEAM POWER TECHNOLOGY S.A. | Ingecon Sun 915TL U B330 Outdoor [330V] | 915 kW, 330Vac, 3-phase Outdoor Utility Interactive Inverter | 915 | 330 | 97.5 | N | N | Weighted efficiency includes transformer efficiency of Elettromil ABN0001ICM05/915. | 80 |  |  | 485 | 613 | 740 | 91.5 | 183 | 274.5 | 457.5 | 686.25 | 915 | 97.17 | 98.13 | 98.33 | 98.22 | 97.86 | 97.27 | 97.95 | 96.5 | 97.84 | 98.09 | 98.05 | 97.69 | 97.15 | 97.75 | 95.82 | 97.49 | 97.82 | 97.81 | 97.51 | 97.17 | 97.53 |  | 2018-05-15
INGETEAM POWER TECHNOLOGY S.A. | Ingecon Sun 1000TL U B360 Indoor [360V] | 1000 kW, 360Vac, 3-phase Indoor Utility Interactive Inverter | 1000 | 360 | 98 | N | N | Weighted efficiency includes transformer efficiency of Elettromil ABN0001ICM05/1000. | 80 |  |  | 524 | 632 | 740 | 100 | 200 | 300 | 500 | 750 | 1000 | 97.34 | 98.14 | 98.33 | 98.21 | 97.83 | 97.31 | 97.94 | 96.84 | 97.92 | 98.13 | 98.08 | 97.7 | 97.09 | 97.78 | 96.36 | 97.64 | 97.97 | 97.94 | 97.55 | 96.97 | 97.61 |  | 2018-05-15
INGETEAM POWER TECHNOLOGY S.A. | Ingecon Sun 1000TL U B360 Outdoor [360V] | 1000 kW, 360Vac, 3-phase Outdoor Utility Interactive Inverter | 1000 | 360 | 98 | N | N | Weighted efficiency includes transformer efficiency of Elettromil ABN0001ICM05/1000. | 80 |  |  | 524 | 632 | 740 | 100 | 200 | 300 | 500 | 750 | 1000 | 97.34 | 98.14 | 98.33 | 98.21 | 97.83 | 97.31 | 97.94 | 96.84 | 97.92 | 98.13 | 98.08 | 97.7 | 97.09 | 97.78 | 96.36 | 97.64 | 97.97 | 97.94 | 97.55 | 96.97 | 97.61 |  | 2018-05-15
INGETEAM POWER TECHNOLOGY S.A. | Ingecon Sun 1110TL U B400 Indoor [400V] | 1110 kW, 400Vac, 3-phase Indoor Utility Interactive Inverter | 1110 | 400 | 98 | N | N | Weighted efficiency includes transformer efficiency of Elettromil ABN0001ICM05/1110. | 80 |  |  | 580 | 660 | 740 | 111 | 222 | 333 | 555 | 832.5 | 1110 | 97.16 | 98.08 | 98.29 | 98.27 | 97.94 | 97.39 | 98 | 96.8 | 97.93 | 98.19 | 98.25 | 97.8 | 97.32 | 97.89 | 96.54 | 97.71 | 98.06 | 98.12 | 97.67 | 97.35 | 97.75 |  | 2018-05-15
INGETEAM POWER TECHNOLOGY S.A. | Ingecon Sun 1110TL U B400 Outdoor [400V] | 1110 kW, 400Vac, 3-phase Outdoor Utility Interactive Inverter | 1110 | 400 | 98 | N | N | Weighted efficiency includes transformer efficiency of Elettromil ABN0001ICM05/1110. | 80 |  |  | 580 | 660 | 740 | 111 | 222 | 333 | 555 | 832.5 | 1110 | 97.16 | 98.08 | 98.29 | 98.27 | 97.94 | 97.39 | 98 | 96.8 | 97.93 | 98.19 | 98.25 | 97.8 | 97.32 | 97.89 | 96.54 | 97.71 | 98.06 | 98.12 | 97.67 | 97.35 | 97.75 |  | 2018-05-15
INGETEAM POWER TECHNOLOGY S.A. | Ingecon Sun 1165TL U B420 Indoor [420V] | 1165 kW, 420Vac, 3-phase Indoor Utility Interactive Inverter | 1165 | 420 | 98 | N | N | Weighted efficiency includes transformer efficiency of Elettromil ABN0001ICM05/1165. | 80 |  |  | 610 | 675 | 740 | 116.5 | 233 | 349.5 | 582.5 | 873.75 | 1165 | 97.28 | 98.08 | 98.28 | 98.26 | 98.01 | 97.47 | 98.04 | 96.99 | 97.92 | 98.18 | 98.24 | 97.91 | 97.53 | 97.95 | 96.74 | 97.75 | 98.03 | 98.15 | 97.85 | 97.42 | 97.87 |  | 2018-05-15
INGETEAM POWER TECHNOLOGY S.A. | Ingecon Sun 1165TL U B420 Outdoor [420V] | 1165 kW, 420Vac, 3-phase Outdoor Utility Interactive Inverter | 1165 | 420 | 98 | N | N | Weighted efficiency includes transformer efficiency of Elettromil ABN0001ICM05/1165. | 80 |  |  | 610 | 675 | 740 | 116.5 | 233 | 349.5 | 582.5 | 873.75 | 1165 | 97.28 | 98.08 | 98.28 | 98.26 | 98.01 | 97.47 | 98.04 | 96.99 | 97.92 | 98.18 | 98.24 | 97.91 | 97.53 | 97.95 | 96.74 | 97.75 | 98.03 | 98.15 | 97.85 | 97.42 | 97.87 |  | 2018-05-15
INGETEAM POWER TECHNOLOGY S.A. | Ingecon Sun 1170TL U B450 Indoor [450V] | 1170 kW, 450 Vac, 3-phase Indoor Utility Interactive Inverter | 1170 | 450 | 97.5 | Y | N | Weighted efficiency includes transformer efficiency of Elettromil ABN0001ICM05/1170. | 90 |  |  | 660 | 874 | 1110 | 117 | 234 | 351 | 585 | 877.5 | 1170 | 96.72 | 97.82 | 98.06 | 97.98 | 97.77 | 97.44 | 97.79 | 95.95 | 97.35 | 97.71 | 97.64 | 97.46 | 97.08 | 97.44 | 94.9 | 96.86 | 97.3 | 97.29 | 97.12 | 96.78 | 97.06 |  | 2018-05-15
INGETEAM POWER TECHNOLOGY S.A. | Ingecon Sun 1170TL U B450 Outdoor [450V] | 1170 kW, 450 Vac, 3-phase Outdoor Utility Interactive Inverter | 1170 | 450 | 97.5 | Y | N | Weighted efficiency includes transformer efficiency of Elettromil ABN0001ICM05/1170. | 90 |  |  | 660 | 874 | 1110 | 117 | 234 | 351 | 585 | 877.5 | 1170 | 96.72 | 97.82 | 98.06 | 97.98 | 97.77 | 97.44 | 97.79 | 95.95 | 97.35 | 97.71 | 97.64 | 97.46 | 97.08 | 97.44 | 94.9 | 96.86 | 97.3 | 97.29 | 97.12 | 96.78 | 97.06 |  | 2018-05-15
INGETEAM POWER TECHNOLOGY S.A. | Ingecon Sun 1400TL U B540 Indoor [450V] | 1400 kW, 450 Vac, 3-phase Indoor Utility Interactive Inverter | 1400 | 450 | 97.5 | Y | N | Weighted efficiency includes transformer efficiency of Elettromil ABN0001ICM05/1400. | 90 |  |  | 786 | 936 | 1110 | 140 | 280 | 420 | 700 | 1050 | 1400 | 96.97 | 97.87 | 98.13 | 98.03 | 97.86 | 97.59 | 97.88 | 96.48 | 97.59 | 97.88 | 97.81 | 97.65 | 97.31 | 97.65 | 95.86 | 97.26 | 97.61 | 97.58 | 97.44 | 97.11 | 97.4 |  | 2018-05-15
INGETEAM POWER TECHNOLOGY S.A. | Ingecon Sun 1400TL U B540 Outdoor [450V] | 1400 kW, 450 Vac, 3-phase Outdoor Utility Interactive Inverter | 1400 | 450 | 97.5 | Y | N | Weighted efficiency includes transformer efficiency of Elettromil ABN0001ICM05/1400. | 90 |  |  | 786 | 936 | 1110 | 140 | 280 | 420 | 700 | 1050 | 1400 | 96.97 | 97.87 | 98.13 | 98.03 | 97.86 | 97.59 | 97.88 | 96.48 | 97.59 | 97.88 | 97.81 | 97.65 | 97.31 | 97.65 | 95.86 | 97.26 | 97.61 | 97.58 | 97.44 | 97.11 | 97.4 |  | 2018-05-15
INGETEAM POWER TECHNOLOGY S.A. | Ingecon Sun 1500TL U B578 Indoor [450V] | 1500 kW, 450 Vac, 3-phase Indoor Utility Interactive Inverter | 1500 | 450 | 97.5 | Y | N | Weighted efficiency includes transformer efficiency of Elettromil ABN0001ICM05/1500. | 90 |  |  | 840 | 963 | 1110 | 150 | 300 | 450 | 750 | 1125 | 1500 | 96.86 | 97.84 | 98.1 | 98.04 | 97.87 | 97.57 | 97.88 | 96.48 | 97.64 | 97.96 | 97.91 | 97.71 | 97.39 | 97.72 | 96.06 | 97.33 | 97.77 | 97.72 | 97.56 | 97.24 | 97.53 |  | 2018-05-15
INGETEAM POWER TECHNOLOGY S.A. | Ingecon Sun 1500TL U B578 Outdoor [450V] | 1500 kW, 450 Vac, 3-phase Outdoor Utility Interactive Inverter | 1500 | 450 | 97.5 | Y | N | Weighted efficiency includes transformer efficiency of Elettromil ABN0001ICM05/1500. | 90 |  |  | 840 | 963 | 1110 | 150 | 300 | 450 | 750 | 1125 | 1500 | 96.86 | 97.84 | 98.1 | 98.04 | 97.87 | 97.57 | 97.88 | 96.48 | 97.64 | 97.96 | 97.91 | 97.71 | 97.39 | 97.72 | 96.06 | 97.33 | 97.77 | 97.72 | 97.56 | 97.24 | 97.53 |  | 2018-05-15
INGETEAM POWER TECHNOLOGY S.A. | Ingecon Sun 1560TL U B600 Indoor [450V] | 1560 kW, 450 Vac, 3-phase Indoor Utility Interactive Inverter | 1560 | 450 | 98 | Y | N | Weighted efficiency includes transformer efficiency of Elettromil ABN0001ICM05/1560. | 90 |  |  | 870 | 978 | 1110 | 156 | 312 | 468 | 780 | 1170 | 1560 | 96.67 | 97.84 | 98.13 | 98.11 | 97.98 | 97.63 | 97.95 | 96.41 | 97.69 | 98.02 | 98.01 | 97.73 | 97.44 | 97.76 | 95.96 | 97.42 | 97.85 | 97.84 | 97.57 | 97.27 | 97.57 |  | 2018-05-15
INGETEAM POWER TECHNOLOGY S.A. | Ingecon Sun 1560TL U B600 Outdoor [450V] | 1560 kW, 450 Vac, 3-phase Outdoor Utility Interactive Inverter | 1560 | 450 | 98 | Y | N | Weighted efficiency includes transformer efficiency of Elettromil ABN0001ICM05/1560. | 90 |  |  | 870 | 978 | 1110 | 156 | 312 | 468 | 780 | 1170 | 1560 | 96.67 | 97.84 | 98.13 | 98.11 | 97.98 | 97.63 | 97.95 | 96.41 | 97.69 | 98.02 | 98.01 | 97.73 | 97.44 | 97.76 | 95.96 | 97.42 | 97.85 | 97.84 | 97.57 | 97.27 | 97.57 |  | 2018-05-15
INGETEAM POWER TECHNOLOGY S.A. | Ingecon Sun 1600TL U B615 Indoor [450V] | 1600 kW, 450 Vac, 3-phase Indoor Utility Interactive Inverter | 1600 | 450 | 98 | Y | N | Weighted efficiency includes transformer efficiency of Elettromil ABN0001ICM05/1600. | 90 |  |  | 892 | 988 | 1110 | 160 | 320 | 480 | 800 | 1200 | 1600 | 96.77 | 97.81 | 98.12 | 98.17 | 97.95 | 97.6 | 97.95 | 96.47 | 97.68 | 98.01 | 98.02 | 97.81 | 97.45 | 97.8 | 96.12 | 97.43 | 97.86 | 97.87 | 97.68 | 97.31 | 97.65 |  | 2018-05-15
INGETEAM POWER TECHNOLOGY S.A. | Ingecon Sun 1600TL U B615 Outdoor [450V] | 1600 kW, 450 Vac, 3-phase Outdoor Utility Interactive Inverter | 1600 | 450 | 98 | Y | N | Weighted efficiency includes transformer efficiency of Elettromil ABN0001ICM05/1600. | 90 |  |  | 892 | 988 | 1110 | 160 | 320 | 480 | 800 | 1200 | 1600 | 96.77 | 97.81 | 98.12 | 98.17 | 97.95 | 97.6 | 97.95 | 96.47 | 97.68 | 98.01 | 98.02 | 97.81 | 97.45 | 97.8 | 96.12 | 97.43 | 97.86 | 97.87 | 97.68 | 97.31 | 97.65 |  | 2018-05-15
INGETEAM POWER TECHNOLOGY S.A. | Ingecon Sun 1640TL U B630 Indoor [450V] | 1640 kW, 450 Vac, 3-phase Indoor Utility Interactive Inverter | 1640 | 450 | 98 | Y | N | Weighted efficiency includes transformer efficiency of Elettromil ABN0001ICM05/1640. | 90 |  |  | 915 | 1000 | 1110 | 164 | 328 | 492 | 820 | 1230 | 1640 | 96.62 | 97.85 | 98.12 | 98.06 | 97.91 | 97.62 | 97.9 | 96.32 | 97.73 | 98.04 | 97.97 | 97.81 | 97.49 | 97.79 | 96.02 | 97.54 | 97.91 | 97.82 | 97.68 | 97.38 | 97.65 |  | 2018-05-15
INGETEAM POWER TECHNOLOGY S.A. | Ingecon Sun 1640TL U B630 Outdoor [450V] | 1640 kW, 450 Vac, 3-phase Outdoor Utility Interactive Inverter | 1640 | 450 | 98 | Y | N | Weighted efficiency includes transformer efficiency of Elettromil ABN0001ICM05/1640. | 90 |  |  | 915 | 1000 | 1110 | 164 | 328 | 492 | 820 | 1230 | 1640 | 96.62 | 97.85 | 98.12 | 98.06 | 97.91 | 97.62 | 97.9 | 96.32 | 97.73 | 98.04 | 97.97 | 97.81 | 97.49 | 97.79 | 96.02 | 97.54 | 97.91 | 97.82 | 97.68 | 97.38 | 97.65 |  | 2018-05-15
Involar | MAC250A-240-NA | 230W Utility Interactive Inverter | 0.23 |  | 93 | N | N |  | 0.11 |  |  | 28 | 35 | 40 | 0.02 | 0.05 | 0.07 | 0.12 | 0.17 | 0.23 | 87.6 | 90.5 | 92.8 | 93.3 | 93.7 | 93.4 | 93.1 | 86.1 | 88.9 | 92.4 | 93.8 | 94 | 94 | 93.2 | 83.9 | 87.2 | 92 | 93.9 | 93.9 | 94.2 | 92.9
Involar | MAC500-XX | 500 W Utility Interactive Inverter | 0.5 |  | 94.5 | N | Y |  | 0.114 |  |  | 30 | 35 | 40 | 0.05 | 0.1 | 0.15 | 0.25 | 0.375 | 0.5 | 92.8 | 94 | 94.4 | 94.7 | 94.6 | 93.8 | 94.5 | 93 | 94.2 | 94.5 | 94.7 | 94.8 | 94.2 | 94.6 | 92.8 | 94.2 | 94.5 | 94.7 | 94.9 | 94.4 | 94.6
iPower | SHO-1.1 [120V] | 1100W (120Vac) Utility Interactive Inverter | 1.1 | 120 | 90.5 | Y | N |  | 3.6 |  |  | 100 | 182 | 380 | 0.11 | 0.22 | 0.33 | 0.55 | 0.83 | 1.1 | 81.8 | 89 | 90.9 | 92.1 | 92.4 | 92.5 | 91.6 | 79.9 | 88 | 90.1 | 91.7 | 92.2 | 92.3 | 91.1 | 74.8 | 84.7 | 87.8 | 90 | 90.8 | 91.1 | 89.3
iPower | SHO-2.0 [240V] | 2000 W 240 Vac Utility Interactive Inverter | 2 | 240 | 92 | Y | N |  | 3.6 |  |  | 100 | 199 | 380 | 0.2 | 0.4 | 0.6 | 1 | 1.5 | 2 | 87.3 | 91.7 | 92.6 | 93.5 | 93.2 | 93 | 92.9 | 85.7 | 90.8 | 92.1 | 92.9 | 92.9 | 92.6 | 92.4 | 82.4 | 88.8 | 90.5 | 91.6 | 91.8 | 91.6 | 91.1
iPower | SHO-2.5 [240V] | 2500 W 240 Vac Utility Interactive Inverter | 2.5 | 240 | 94.5 | Y | N |  | 3.9 |  |  | 100 | 218 | 400 | 0.25 | 0.5 | 0.75 | 1.25 | 1.88 | 2.5 | 87.1 | 93.3 | 94.9 | 95.8 | 95.8 | 95.6 | 95.2 | 85.2 | 92.4 | 93.8 | 95.2 | 95.4 | 95.1 | 94.6 | 80.4 | 90 | 91.7 | 93.7 | 94.5 | 93.8 | 93.2
iPower | SHO-3.0 [240V] | 3000 W 240 Vac Utility Interactive Inverter | 3 | 240 | 93.5 | Y | N |  | 3.63 |  |  | 100 | 222.5 | 380 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 88.9 | 92.9 | 93.8 | 94.3 | 94.2 | 93.9 | 93.9 | 87.9 | 92.5 | 93.5 | 94.1 | 94 | 93.8 | 93.7 | 84.9 | 90.9 | 92.4 | 93.3 | 93.2 | 93 | 92.7
iPower | SHO-3.5 [240V] | 3500 W 240 Vac Utility Interactive Inverter | 3.5 | 240 | 95.5 | Y | N |  | 3.86 |  |  | 100 | 263 | 400 | 0.35 | 0.7 | 1.05 | 1.75 | 2.625 | 3.5 | 87.2 | 93.1 | 95.4 | 96.5 | 96.7 | 96.6 | 95.9 | 85.7 | 92.2 | 94.9 | 96.2 | 96.4 | 96.3 | 95.5 | 82.1 | 90.2 | 93.6 | 95.4 | 95.7 | 95.6 | 94.5
iPower | SHO-4.6 [208V] | 4600 W 208 Vac Utility Interactive Inverter | 4.6 | 208 | 95.5 | Y | N |  | 4 |  |  | 100 | 254 | 400 | 0.46 | 0.92 | 1.38 | 2.3 | 3.45 | 4.6 | 90.3 | 94.8 | 95.9 | 96.5 | 96.5 | 96.2 | 96.1 | 89.2 | 94.3 | 95.6 | 96.3 | 96.4 | 96.1 | 95.9 | 86.5 | 92.9 | 94.7 | 95.6 | 95.7 | 95.4 | 95
iPower | SHO-4.8 [240V] | 4800 W 240 Vac Utility Interactive Inverter | 4.8 | 240 | 96 | Y | N |  | 4.1 |  |  | 100 | 263 | 400 | 0.48 | 0.96 | 1.44 | 2.4 | 3.6 | 4.8 | 86.8 | 93.5 | 95.5 | 97 | 97.2 | 97.1 | 96.4 | 85.5 | 92.9 | 95 | 96.7 | 96.9 | 96.8 | 96 | 84.5 | 91.5 | 93.9 | 95.9 | 96.2 | 96.1 | 95.1
iPower | SHO-5.2 [240V] | 5200 W 240 Vac Utility Interactive Inverter | 5.2 | 240 | 96 | Y | N |  | 4 |  |  | 240 | 280 | 400 | 0.52 | 1.04 | 1.56 | 2.6 | 3.9 | 5.2 | 89.4 | 94.8 | 96 | 96.8 | 97 | 96.8 | 96.4 | 88.6 | 94.4 | 95.7 | 96.7 | 96.8 | 96.6 | 96.2 | 87.7 | 93.1 | 94.8 | 96.1 | 96.3 | 96.1 | 95.5
Jema Energy | JAE7140 | 100 kW Utility Interactive Inverter | 100 |  | 95.5 | N | N |  | 20.5 |  |  | 290 | 340 | 480 | 10 | 20 | 30 | 50 | 75 | 100 | 92.5 | 95.3 | 95.9 | 96.1 | 96 | 95.5 | 95.8 | 91 | 94.6 | 95.4 | 95.9 | 95.8 | 95.3 | 95.5 | 87.1 | 92.6 | 94 | 95 | 95.1 | 94.7 | 94.5
Jema Energy | JAE7141 | 100 kW Utility Interactive Inverter | 100 |  | 95 | N | N |  | 20.5 |  |  | 290 | 340 | 480 | 10 | 20 | 30 | 50 | 75 | 100 | 91.1 | 94.8 | 95.5 | 95.8 | 95.7 | 95.2 | 95.5 | 89.7 | 94 | 95 | 95.5 | 95.6 | 95 | 95.1 | 85.9 | 91.9 | 93.4 | 94.5 | 94.8 | 94.4 | 94
Jema Energy | IF500TL-UL OUTDOOR | 500 kW, 3-phase Utility Interactive Inverter with MV NEMA TP1 transformer | 500 |  | 96 | Y | N |  | 33.4 |  |  | 495 | 600 | 800 | 50 | 100 | 150 | 250 | 375 | 500 | 94.5 | 96.3 | 96.5 | 96.7 | 96.4 | 95.8 | 96.3 | 93.9 | 95.9 | 96.2 | 96.3 | 96 | 95.4 | 96 | 92.7 | 95.1 | 95.6 | 95.7 | 95.5 | 95 | 95.4
Jema Energy | IF600TL-UL OUTDOOR | 600 kW, 3-phase Utility Interactive Inverter with MV NEMA TP1 transformer | 600 |  | 96 | Y | N |  | 47 |  |  | 595 | 700 | 800 | 60 | 120 | 180 | 300 | 450 | 600 | 94.5 | 96.4 | 96.7 | 96.9 | 96.6 | 96.1 | 96.5 | 93.8 | 95.9 | 96.4 | 96.5 | 96.3 | 95.8 | 96.2 | 93.5 | 95.8 | 95.9 | 96.2 | 96.1 | 95.7 | 96
Jiangsu Zeversolar New Energy | Evershine TL3000-US-208 | 3 kW Utility Interactive Inverter | 2.98 |  | 96 | Y | N |  | 0.26 |  |  | 100 | 370 | 480 | 0.3 | 0.6 | 0.89 | 1.49 | 2.24 | 2.98 | 90.7 | 93.6 | 94.7 | 95.7 | 95.9 | 95.8 | 95.4 | 93.3 | 95.9 | 96.5 | 96.9 | 96.9 | 96.8 | 96.6 | 91.9 | 95.2 | 96 | 96.7 | 96.8 | 96.7 | 96.4
Jiangsu Zeversolar New Energy | Evershine TL3000-US-240 | 3 kW Utility Interactive Inverter | 2.98 |  | 96.5 | Y | N |  | 0.35 |  |  | 100 | 370 | 480 | 0.3 | 0.6 | 0.89 | 1.49 | 2.24 | 2.98 | 90.3 | 93.4 | 94.3 | 95.5 | 95.9 | 95.9 | 95.3 | 93.8 | 96.3 | 96.9 | 97.2 | 97.2 | 97.2 | 97 | 91.7 | 95.5 | 96.4 | 96.9 | 97.1 | 97.1 | 96.7
Jiangsu Zeversolar New Energy | Evershine TL4000-US-208 | 4 kW Utility Interactive Inverter | 3.97 |  | 96.5 | Y | N |  | 0.26 |  |  | 100 | 370 | 480 | 0.4 | 0.79 | 1.19 | 1.99 | 2.98 | 3.97 | 92.3 | 94.5 | 95.2 | 95.8 | 95.8 | 95.6 | 95.5 | 94.9 | 96.4 | 96.7 | 97 | 96.8 | 96.5 | 96.7 | 93.6 | 95.8 | 96.4 | 96.8 | 96.7 | 96.5 | 96.5
Jiangsu Zeversolar New Energy | Evershine TL4000-US-240 | 4 kW Utility Interactive Inverter | 3.99 |  | 96.5 | Y | N |  | 0.35 |  |  | 100 | 370 | 480 | 0.4 | 0.79 | 1.19 | 1.99 | 2.98 | 3.97 | 90.9 | 94 | 94.9 | 95.8 | 96 | 95.8 | 95.5 | 94.5 | 96.7 | 97 | 97.3 | 97.2 | 97 | 97.1 | 93.1 | 96.1 | 96.8 | 97.2 | 97.1 | 97 | 96.9
Jiangsu Zeversolar New Energy | Evershine TL5000-US-208 | 5 kW Utility Interactive Inverter | 5 |  | 96 | Y | N |  | 0.27 |  |  | 100 | 370 | 480 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 91.7 | 94.4 | 95.3 | 95.7 | 95.7 | 95.4 | 95.4 | 94 | 96.1 | 96.5 | 96.7 | 96.6 | 96.2 | 96.4 | 93 | 95.2 | 96.1 | 96.5 | 96.4 | 96.2 | 96.2
Jiangsu Zeversolar New Energy | Evershine TL5000-US-240 | 5 kW Utility Interactive Inverter | 5 |  | 96.5 | Y | N |  | 0.35 |  |  | 100 | 370 | 480 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 91.7 | 94.3 | 95.3 | 96 | 96 | 95.8 | 95.6 | 94.9 | 96.7 | 97 | 97.1 | 97 | 96.7 | 96.9 | 93.3 | 95.9 | 96.5 | 96.9 | 96.9 | 96.7 | 96.7
Jiangsu Zeversolar New Energy | Evershine TL6000-US-208 | 6 kW Utility Interactive Inverter | 5.32 |  | 96 | Y | N |  | 0.27 |  |  | 100 | 370 | 480 | 0.53 | 1.06 | 1.6 | 2.66 | 3.99 | 5.32 | 92.7 | 94.8 | 95.5 | 95.7 | 95.5 | 95.1 | 95.4 | 94.9 | 96.6 | 96.8 | 96.7 | 96.4 | 95.8 | 96.4 | 93.3 | 96 | 96.4 | 96.6 | 96.2 | 95.9 | 96.2
Jiangsu Zeversolar New Energy | Evershine TL6000-US-240 | 6 kW Utility Interactive Inverter | 5.99 |  | 96.5 | Y | N |  | 0.35 |  |  | 100 | 370 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.49 | 5.99 | 92.6 | 94.9 | 95.7 | 96 | 95.9 | 95.4 | 95.7 | 95.8 | 96.9 | 97.2 | 97.1 | 96.8 | 96.4 | 96.9 | 94 | 96.5 | 96.9 | 96.9 | 96.7 | 96.4 | 96.6
Jiangyin Hareon Power | HR-240P-AC/Bb [208V] | 240 W, 208 Vac Inverter | 0.24 | 208 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6
Jiangyin Hareon Power | HR-240P-AC/Bb [240V] | 240 W, 240 Vac Inverter | 0.24 | 240 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6
Jiangyin Hareon Power | HR-240P-AC/BbP [208V] | 240 W, 208 Vac Inverter | 0.24 | 208 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6
Jiangyin Hareon Power | HR-240P-AC/BbP [240V] | 240 W, 240 Vac Inverter | 0.24 | 240 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6
Jiangyin Hareon Power | HR-245P-AC/Bb [208V] | 240 W, 208 Vac Inverter | 0.24 | 208 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6
Jiangyin Hareon Power | HR-245P-AC/Bb [240V] | 240 W, 240 Vac Inverter | 0.24 | 240 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6
Jiangyin Hareon Power | HR-245P-AC/BbP [208V] | 240 W, 208 Vac Inverter | 0.24 | 208 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6
Jiangyin Hareon Power | HR-245P-AC/BbP [240V] | 240 W, 240 Vac Inverter | 0.24 | 240 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6
Jiangyin Hareon Power | HR-250-AC/Cb [208V] | 240 W, 208 Vac Inverter | 0.24 | 208 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6
Jiangyin Hareon Power | HR-250-AC/Cb [240V] | 240 W, 240 Vac Inverter | 0.24 | 240 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6
Jiangyin Hareon Power | HR-250P-AC/Bb [208V] | 240 W, 208 Vac Inverter | 0.24 | 208 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6
Jiangyin Hareon Power | HR-250P-AC/Bb [240V] | 240 W, 240 Vac Inverter | 0.24 | 240 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6
Jiangyin Hareon Power | HR-250P-AC/BbP [208V] | 240 W, 208 Vac Inverter | 0.24 | 208 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6
Jiangyin Hareon Power | HR-250P-AC/BbP [240V] | 240 W, 240 Vac Inverter | 0.24 | 240 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6
Jiangyin Hareon Power | HR-255-AC/Cb [208V] | 240 W, 208 Vac Inverter | 0.24 | 208 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6
Jiangyin Hareon Power | HR-255-AC/Cb [240V] | 240 W, 240 Vac Inverter | 0.24 | 240 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6
Jiangyin Hareon Power | HR-255P-AC/Bb [208V] | 240 W, 208 Vac Inverter | 0.24 | 208 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6
Jiangyin Hareon Power | HR-255P-AC/Bb [240V] | 240 W, 240 Vac Inverter | 0.24 | 240 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6
Jiangyin Hareon Power | HR-255P-AC/BbP [208V] | 240 W, 208 Vac Inverter | 0.24 | 208 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6
Jiangyin Hareon Power | HR-255P-AC/BbP [240V] | 240 W, 240 Vac Inverter | 0.24 | 240 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6
Jiangyin Hareon Power | HR-260-AC/Cb [208V] | 240 W, 208 Vac Inverter | 0.24 | 208 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6
Jiangyin Hareon Power | HR-260-AC/Cb [240V] | 240 W, 208 Vac Inverter | 0.24 | 240 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6
Jiangyin Hareon Power | HR-260P-AC/Bb [208V] | 240 W, 208 Vac Inverter | 0.24 | 208 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6
Jiangyin Hareon Power | HR-260P-AC/Bb [240V] | 240 W, 240 Vac Inverter | 0.24 | 240 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6
Jiangyin Hareon Power | HR-260P-AC/BbP [208V] | 240 W, 208 Vac Inverter | 0.24 | 208 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6
Jiangyin Hareon Power | HR-260P-AC/BbP [240V] | 240 W, 240 Vac Inverter | 0.24 | 240 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6
Jiangyin Hareon Power | HR-265-AC/Cb [208V] | 240 W, 208 Vac Inverter | 0.24 | 208 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6
Jiangyin Hareon Power | HR-265-AC/Cb [240V] | 240 W, 240 Vac Inverter | 0.24 | 240 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6
Jiangyin Hareon Power | HR-270-AC/Cb [208V] | 240 W, 208 Vac Inverter | 0.24 | 208 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6
Jiangyin Hareon Power | HR-270-AC/Cb [240V] | 240 W, 240 Vac Inverter | 0.24 | 240 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6
Jinko Solar Co., Ltd. | JKMS300M-60BL-EP [208V] | 300 W, 208 Vac, Utility Interactive, monocrystalline ACPV Module, black substrate. DC Module: JKM300M-60BL. Microinverter: IQ7-60-ACM-US [208V]. | 0.24 | 208 | 97 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.025 |  |  | 27 | 32 | 37 | 0.024 | 0.048 | 0.072 | 0.12 | 0.18 | 0.24 | 94.2043 | 96.2264 | 97.0215 | 97.5539 | 97.4142 | 96.9598 | 97.1859 | 93.3248 | 95.7344 | 96.7563 | 97.4639 | 97.4153 | 97.0564 | 97.0808 | 92.4192 | 95.0959 | 96.5384 | 97.3538 | 97.3374 | 97.0253 | 96.9205 | 2019-07-15
Jinko Solar Co., Ltd. | JKMS300M-60BL-EP [240V] | 300 W, 240 Vac, Utility Interactive, monocrystalline ACPV Module, black substrate. DC Module: JKM300M-60BL. Microinverter: IQ7-60-ACM-US [240V]. | 0.24 | 240 | 97 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.025 |  |  | 27 | 32 | 37 | 0.024 | 0.048 | 0.072 | 0.12 | 0.18 | 0.24 | 93.9453 | 96.08 | 96.8145 | 97.4746 | 97.4192 | 97.0288 | 97.1328 | 92.9907 | 95.6588 | 96.5049 | 97.5523 | 97.615 | 97.4087 | 97.1755 | 92.0062 | 95.0264 | 96.2309 | 97.3813 | 97.5438 | 97.4107 | 96.9981 | 2019-07-15
Jinko Solar Co., Ltd. | JKMS305M-60BL-EP [208V] | 305 W, 208 Vac, Utility Interactive, monocrystalline ACPV Module, black substrate. DC Module: JKM305M-60BL. Microinverter: IQ7-60-ACM-US [208V]. | 0.24 | 208 | 97 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.025 |  |  | 27 | 32 | 37 | 0.024 | 0.048 | 0.072 | 0.12 | 0.18 | 0.24 | 94.2043 | 96.2264 | 97.0215 | 97.5539 | 97.4142 | 96.9598 | 97.1859 | 93.3248 | 95.7344 | 96.7563 | 97.4639 | 97.4153 | 97.0564 | 97.0808 | 92.4192 | 95.0959 | 96.5384 | 97.3538 | 97.3374 | 97.0253 | 96.9205 | 2019-07-15
Jinko Solar Co., Ltd. | JKMS305M-60BL-EP [240V] | 305 W, 240 Vac, Utility Interactive, monocrystalline ACPV Module, black substrate. DC Module: JKM305M-60BL. Microinverter: IQ7-60-ACM-US [240V]. | 0.24 | 240 | 97 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.025 |  |  | 27 | 32 | 37 | 0.024 | 0.048 | 0.072 | 0.12 | 0.18 | 0.24 | 93.9453 | 96.08 | 96.8145 | 97.4746 | 97.4192 | 97.0288 | 97.1328 | 92.9907 | 95.6588 | 96.5049 | 97.5523 | 97.615 | 97.4087 | 97.1755 | 92.0062 | 95.0264 | 96.2309 | 97.3813 | 97.5438 | 97.4107 | 96.9981 | 2019-07-15
Jinko Solar Co., Ltd. | JKMS305M-60L-EP [208V] | 305 W, 208 Vac, Utility Interactive, monocrystalline ACPV Module, white substrate. DC Module: JKM305M-60L. Microinverter: IQ7-60-ACM-US [208V]. | 0.24 | 208 | 97 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.025 |  |  | 27 | 32 | 37 | 0.024 | 0.048 | 0.072 | 0.12 | 0.18 | 0.24 | 94.2043 | 96.2264 | 97.0215 | 97.5539 | 97.4142 | 96.9598 | 97.1859 | 93.3248 | 95.7344 | 96.7563 | 97.4639 | 97.4153 | 97.0564 | 97.0808 | 92.4192 | 95.0959 | 96.5384 | 97.3538 | 97.3374 | 97.0253 | 96.9205 | 2019-07-15
Jinko Solar Co., Ltd. | JKMS305M-60L-EP [240V] | 305 W, 208 Vac, Utility Interactive, monocrystalline ACPV Module, white substrate. DC Module: JKM305M-60L. Microinverter: IQ7-60-ACM-US [208V]. | 0.24 | 240 | 97 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.025 |  |  | 27 | 32 | 37 | 0.024 | 0.048 | 0.072 | 0.12 | 0.18 | 0.24 | 93.9453 | 96.08 | 96.8145 | 97.4746 | 97.4192 | 97.0288 | 97.1328 | 92.9907 | 95.6588 | 96.5049 | 97.5523 | 97.615 | 97.4087 | 97.1755 | 92.0062 | 95.0264 | 96.2309 | 97.3813 | 97.5438 | 97.4107 | 96.9981 | 2019-07-15
Jinko Solar Co., Ltd. | JKMS310M-60BL-EP [208V] | 310 W, 208 Vac, Utility Interactive, monocrystalline ACPV Module, black substrate. DC Module: JKM310M-60BL. Microinverter: IQ7-60-ACM-US [208V]. | 0.24 | 208 | 97 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.025 |  |  | 27 | 32 | 37 | 0.024 | 0.048 | 0.072 | 0.12 | 0.18 | 0.24 | 94.2043 | 96.2264 | 97.0215 | 97.5539 | 97.4142 | 96.9598 | 97.1859 | 93.3248 | 95.7344 | 96.7563 | 97.4639 | 97.4153 | 97.0564 | 97.0808 | 92.4192 | 95.0959 | 96.5384 | 97.3538 | 97.3374 | 97.0253 | 96.9205 | 2019-07-15
Jinko Solar Co., Ltd. | JKMS310M-60BL-EP [240V] | 310 W, 240 Vac, Utility Interactive, monocrystalline ACPV Module, black substrate. DC Module: JKM310M-60BL. Microinverter: IQ7-60-ACM-US [240V]. | 0.24 | 240 | 97 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.025 |  |  | 27 | 32 | 37 | 0.024 | 0.048 | 0.072 | 0.12 | 0.18 | 0.24 | 93.9453 | 96.08 | 96.8145 | 97.4746 | 97.4192 | 97.0288 | 97.1328 | 92.9907 | 95.6588 | 96.5049 | 97.5523 | 97.615 | 97.4087 | 97.1755 | 92.0062 | 95.0264 | 96.2309 | 97.3813 | 97.5438 | 97.4107 | 96.9981 | 2019-07-15
Jinko Solar Co., Ltd. | JKMS310M-60L-EP [208V] | 310 W, 208 Vac, Utility Interactive, monocrystalline ACPV Module, white substrate. DC Module: JKM310M-60L. Microinverter: IQ7-60-ACM-US [208V]. | 0.24 | 208 | 97 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.025 |  |  | 27 | 32 | 37 | 0.024 | 0.048 | 0.072 | 0.12 | 0.18 | 0.24 | 94.2043 | 96.2264 | 97.0215 | 97.5539 | 97.4142 | 96.9598 | 97.1859 | 93.3248 | 95.7344 | 96.7563 | 97.4639 | 97.4153 | 97.0564 | 97.0808 | 92.4192 | 95.0959 | 96.5384 | 97.3538 | 97.3374 | 97.0253 | 96.9205 | 2019-07-15
Jinko Solar Co., Ltd. | JKMS310M-60L-EP [240V] | 310 W, 208 Vac, Utility Interactive, monocrystalline ACPV Module, white substrate. DC Module: JKM310M-60L. Microinverter: IQ7-60-ACM-US [240V]. | 0.24 | 240 | 97 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.025 |  |  | 27 | 32 | 37 | 0.024 | 0.048 | 0.072 | 0.12 | 0.18 | 0.24 | 93.9453 | 96.08 | 96.8145 | 97.4746 | 97.4192 | 97.0288 | 97.1328 | 92.9907 | 95.6588 | 96.5049 | 97.5523 | 97.615 | 97.4087 | 97.1755 | 92.0062 | 95.0264 | 96.2309 | 97.3813 | 97.5438 | 97.4107 | 96.9981 | 2019-07-15
Jinko Solar Co., Ltd. | JKMS315M-60BL-EP [208V] | 315 W, 208 Vac, Utility Interactive, monocrystalline ACPV Module, black substrate. DC Module: JKM315M-60BL. Microinverter: IQ7-60-ACM-US [208V]. | 0.24 | 208 | 97 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.025 |  |  | 27 | 32 | 37 | 0.024 | 0.048 | 0.072 | 0.12 | 0.18 | 0.24 | 94.2043 | 96.2264 | 97.0215 | 97.5539 | 97.4142 | 96.9598 | 97.1859 | 93.3248 | 95.7344 | 96.7563 | 97.4639 | 97.4153 | 97.0564 | 97.0808 | 92.4192 | 95.0959 | 96.5384 | 97.3538 | 97.3374 | 97.0253 | 96.9205 | 2019-07-15
Jinko Solar Co., Ltd. | JKMS315M-60BL-EP [240V] | 315 W, 240 Vac, Utility Interactive, monocrystalline ACPV Module, black substrate. DC Module: JKM315M-60BL. Microinverter: IQ7-60-ACM-US [240V]. | 0.24 | 240 | 97 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.025 |  |  | 27 | 32 | 37 | 0.024 | 0.048 | 0.072 | 0.12 | 0.18 | 0.24 | 93.9453 | 96.08 | 96.8145 | 97.4746 | 97.4192 | 97.0288 | 97.1328 | 92.9907 | 95.6588 | 96.5049 | 97.5523 | 97.615 | 97.4087 | 97.1755 | 92.0062 | 95.0264 | 96.2309 | 97.3813 | 97.5438 | 97.4107 | 96.9981 | 2019-07-15
Jinko Solar Co., Ltd. | JKMS315M-60L-EP [208V] | 315 W, 208 Vac, Utility Interactive, monocrystalline ACPV Module, white substrate. DC Module: JKM315M-60L. Microinverter: IQ7-60-ACM-US [208V]. | 0.24 | 208 | 97 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.025 |  |  | 27 | 32 | 37 | 0.024 | 0.048 | 0.072 | 0.12 | 0.18 | 0.24 | 94.2043 | 96.2264 | 97.0215 | 97.5539 | 97.4142 | 96.9598 | 97.1859 | 93.3248 | 95.7344 | 96.7563 | 97.4639 | 97.4153 | 97.0564 | 97.0808 | 92.4192 | 95.0959 | 96.5384 | 97.3538 | 97.3374 | 97.0253 | 96.9205 | 2019-07-15
Jinko Solar Co., Ltd. | JKMS315M-60L-EP [240V] | 315 W, 208 Vac, Utility Interactive, monocrystalline ACPV Module, white substrate. DC Module: JKM315M-60L. Microinverter: IQ7-60-ACM-US [240V]. | 0.24 | 240 | 97 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.025 |  |  | 27 | 32 | 37 | 0.024 | 0.048 | 0.072 | 0.12 | 0.18 | 0.24 | 93.9453 | 96.08 | 96.8145 | 97.4746 | 97.4192 | 97.0288 | 97.1328 | 92.9907 | 95.6588 | 96.5049 | 97.5523 | 97.615 | 97.4087 | 97.1755 | 92.0062 | 95.0264 | 96.2309 | 97.3813 | 97.5438 | 97.4107 | 96.9981 | 2019-07-15
Jinko Solar Co., Ltd. | JKMS320M-60BL-EP [208V] | 320 W, 208 Vac, Utility Interactive, monocrystalline ACPV Module, black substrate. DC Module: JKM320M-60BL. Microinverter: IQ7-60-ACM-US [208V]. | 0.24 | 208 | 97 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.025 |  |  | 27 | 32 | 37 | 0.024 | 0.048 | 0.072 | 0.12 | 0.18 | 0.24 | 94.2043 | 96.2264 | 97.0215 | 97.5539 | 97.4142 | 96.9598 | 97.1859 | 93.3248 | 95.7344 | 96.7563 | 97.4639 | 97.4153 | 97.0564 | 97.0808 | 92.4192 | 95.0959 | 96.5384 | 97.3538 | 97.3374 | 97.0253 | 96.9205 | 2019-07-15
Jinko Solar Co., Ltd. | JKMS320M-60BL-EP [240V] | 320 W, 240 Vac, Utility Interactive, monocrystalline ACPV Module, black substrate. DC Module: JKM320M-60BL. Microinverter: IQ7-60-ACM-US [240V]. | 0.24 | 240 | 97 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.025 |  |  | 27 | 32 | 37 | 0.024 | 0.048 | 0.072 | 0.12 | 0.18 | 0.24 | 93.9453 | 96.08 | 96.8145 | 97.4746 | 97.4192 | 97.0288 | 97.1328 | 92.9907 | 95.6588 | 96.5049 | 97.5523 | 97.615 | 97.4087 | 97.1755 | 92.0062 | 95.0264 | 96.2309 | 97.3813 | 97.5438 | 97.4107 | 96.9981 | 2019-07-15
Jinko Solar Co., Ltd. | JKMS320M-60L-EP [208V] | 320 W, 208 Vac, Utility Interactive, monocrystalline ACPV Module, white substrate. DC Module: JKM320M-60L. Microinverter: IQ7-60-ACM-US [208V]. | 0.24 | 208 | 97 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.025 |  |  | 27 | 32 | 37 | 0.024 | 0.048 | 0.072 | 0.12 | 0.18 | 0.24 | 94.2043 | 96.2264 | 97.0215 | 97.5539 | 97.4142 | 96.9598 | 97.1859 | 93.3248 | 95.7344 | 96.7563 | 97.4639 | 97.4153 | 97.0564 | 97.0808 | 92.4192 | 95.0959 | 96.5384 | 97.3538 | 97.3374 | 97.0253 | 96.9205 | 2019-07-15
Jinko Solar Co., Ltd. | JKMS320M-60L-EP [240V] | 320 W, 208 Vac, Utility Interactive, monocrystalline ACPV Module, white substrate. DC Module: JKM320M-60L. Microinverter: IQ7-60-ACM-US [240V]. | 0.24 | 240 | 97 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.025 |  |  | 27 | 32 | 37 | 0.024 | 0.048 | 0.072 | 0.12 | 0.18 | 0.24 | 93.9453 | 96.08 | 96.8145 | 97.4746 | 97.4192 | 97.0288 | 97.1328 | 92.9907 | 95.6588 | 96.5049 | 97.5523 | 97.615 | 97.4087 | 97.1755 | 92.0062 | 95.0264 | 96.2309 | 97.3813 | 97.5438 | 97.4107 | 96.9981 | 2019-07-15
Jinko Solar Co., Ltd. | JKMS325M-60BL-EP [208V] | 325 W, 208 Vac, Utility Interactive, monocrystalline ACPV Module, black substrate. DC Module: JKM325M-60BL. Microinverter: IQ7-60-ACM-US [208V]. | 0.24 | 208 | 97 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.025 |  |  | 27 | 32 | 37 | 0.024 | 0.048 | 0.072 | 0.12 | 0.18 | 0.24 | 94.2043 | 96.2264 | 97.0215 | 97.5539 | 97.4142 | 96.9598 | 97.1859 | 93.3248 | 95.7344 | 96.7563 | 97.4639 | 97.4153 | 97.0564 | 97.0808 | 92.4192 | 95.0959 | 96.5384 | 97.3538 | 97.3374 | 97.0253 | 96.9205 | 2019-07-15
Jinko Solar Co., Ltd. | JKMS325M-60BL-EP [240V] | 325 W, 240 Vac, Utility Interactive, monocrystalline ACPV Module, black substrate. DC Module: JKM325M-60BL. Microinverter: IQ7-60-ACM-US [240V]. | 0.24 | 240 | 97 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.025 |  |  | 27 | 32 | 37 | 0.024 | 0.048 | 0.072 | 0.12 | 0.18 | 0.24 | 93.9453 | 96.08 | 96.8145 | 97.4746 | 97.4192 | 97.0288 | 97.1328 | 92.9907 | 95.6588 | 96.5049 | 97.5523 | 97.615 | 97.4087 | 97.1755 | 92.0062 | 95.0264 | 96.2309 | 97.3813 | 97.5438 | 97.4107 | 96.9981 | 2019-07-15
Jinko Solar Co., Ltd. | JKMS325M-60L-EP [208V] | 325 W, 208 Vac, Utility Interactive, monocrystalline ACPV Module, white substrate. DC Module: JKM325M-60L. Microinverter: IQ7-60-ACM-US [208V]. | 0.24 | 208 | 97 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.025 |  |  | 27 | 32 | 37 | 0.024 | 0.048 | 0.072 | 0.12 | 0.18 | 0.24 | 94.2043 | 96.2264 | 97.0215 | 97.5539 | 97.4142 | 96.9598 | 97.1859 | 93.3248 | 95.7344 | 96.7563 | 97.4639 | 97.4153 | 97.0564 | 97.0808 | 92.4192 | 95.0959 | 96.5384 | 97.3538 | 97.3374 | 97.0253 | 96.9205 | 2019-07-15
Jinko Solar Co., Ltd. | JKMS325M-60L-EP [240V] | 325 W, 208 Vac, Utility Interactive, monocrystalline ACPV Module, white substrate. DC Module: JKM325M-60L. Microinverter: IQ7-60-ACM-US [240V]. | 0.24 | 240 | 97 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.025 |  |  | 27 | 32 | 37 | 0.024 | 0.048 | 0.072 | 0.12 | 0.18 | 0.24 | 93.9453 | 96.08 | 96.8145 | 97.4746 | 97.4192 | 97.0288 | 97.1328 | 92.9907 | 95.6588 | 96.5049 | 97.5523 | 97.615 | 97.4087 | 97.1755 | 92.0062 | 95.0264 | 96.2309 | 97.3813 | 97.5438 | 97.4107 | 96.9981 | 2019-07-15
Jinko Solar Co., Ltd. | JKMS330M-60L-EP [208V] | 330 W, 208 Vac, Utility Interactive, monocrystalline ACPV Module, white substrate. DC Module: JKM330M-60L. Microinverter: IQ7-60-ACM-US [208V]. | 0.24 | 208 | 97 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.025 |  |  | 27 | 32 | 37 | 0.024 | 0.048 | 0.072 | 0.12 | 0.18 | 0.24 | 94.2043 | 96.2264 | 97.0215 | 97.5539 | 97.4142 | 96.9598 | 97.1859 | 93.3248 | 95.7344 | 96.7563 | 97.4639 | 97.4153 | 97.0564 | 97.0808 | 92.4192 | 95.0959 | 96.5384 | 97.3538 | 97.3374 | 97.0253 | 96.9205 | 2019-07-15
Jinko Solar Co., Ltd. | JKMS330M-60L-EP [240V] | 330 W, 208 Vac, Utility Interactive, monocrystalline ACPV Module, white substrate. DC Module: JKM330M-60L. Microinverter: IQ7-60-ACM-US [240V]. | 0.24 | 240 | 97 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.025 |  |  | 27 | 32 | 37 | 0.024 | 0.048 | 0.072 | 0.12 | 0.18 | 0.24 | 93.9453 | 96.08 | 96.8145 | 97.4746 | 97.4192 | 97.0288 | 97.1328 | 92.9907 | 95.6588 | 96.5049 | 97.5523 | 97.615 | 97.4087 | 97.1755 | 92.0062 | 95.0264 | 96.2309 | 97.3813 | 97.5438 | 97.4107 | 96.9981 | 2019-07-15
KACO | blueplanet Ultraverter 250 | 250 W Utility Interactive Inverter with the Ultraverter system from 2 to 9 kW | 0.25 |  | 97.5 | N | Y |  | 0 |  |  | 29 | 35 | 45 | 0.03 | 0.05 | 0.08 | 0.13 | 0.19 | 0.25 | 92.1 | 96.2 | 97 | 97.4 | 97.2 | 96.8 | 97 | 93.1 | 96.4 | 97.3 | 97.7 | 97.6 | 97.3 | 97.3 | 93 | 96.6 | 97.6 | 98 | 97.9 | 97.7 | 97.6
KACO | blueplanet 1501xi [240V] | 1.5 kW, 240 Vac, 125-400 Vdc Utility Interactive Inverter | 1.5 | 240 | 95 | Y | N |  | 0.29 |  |  | 100 | 195 | 400 | 0.15 | 0.3 | 0.45 | 0.75 | 1.125 | 1.5 | 92.6 | 95.1 | 95.5 | 95.5 | 95.2 | 94.4 | 95.1 | 92.4 | 94.7 | 95.1 | 95.3 | 94.9 | 94.2 | 94.9 | 93.5 | 94.6 | 94.7 | 94.8 | 94.5 | 93.8 | 94.5
KACO | blueplanet 1502x [208V] | 1.5 kW, 208 Vac, Utility Interactive Inverter | 1.5 | 208 | 95.5 | Y | N |  | 0.39 |  |  | 100 | 195 | 400 | 0.15 | 0.3 | 0.45 | 0.75 | 1.125 | 1.5 | 92.6 | 95.3 | 95.8 | 95.9 | 95.5 | 95 | 95.5 | 93.2 | 95 | 95.6 | 95.7 | 95.4 | 94.9 | 95.4 | 93.4 | 94.7 | 95.1 | 95.3 | 95 | 94.5 | 95
KACO | blueplanet 1502xi [208V] | 1.5 kW, 208 Vac, 125-500 Vdc Utility Interactive Inverter | 1.5 | 208 | 95.5 | Y | N |  | 0.39 |  |  | 100 | 195 | 400 | 0.15 | 0.3 | 0.45 | 0.75 | 1.125 | 1.5 | 92.6 | 95.3 | 95.8 | 95.9 | 95.5 | 95 | 95.5 | 93.2 | 95 | 95.6 | 95.7 | 95.4 | 94.9 | 95.4 | 93.4 | 94.7 | 95.1 | 95.3 | 95 | 94.5 | 95
KACO | blueplanet 1502x [240V] | 1.5 kW, 240 Vac, Utility Interactive Inverter | 1.67 | 240 | 94 | Y | N |  | 2.63 |  |  | 100 | 175 | 300 | 0.17 | 0.33 | 0.5 | 0.83 | 1.25 | 1.67 | 91.5 | 94.3 | 94.8 | 94.7 | 94.3 | 93.5 | 94.3 | 91.6 | 94.2 | 94.7 | 94.5 | 94.3 | 93.5 | 94.3 | 90.7 | 93.4 | 94.1 | 94 | 93.8 | 93.2 | 93.7
KACO | blueplanet 1502xi [240V] | 1.5 kW, 240 Vac, 125-500 Vdc Utility Interactive Inverter | 1.67 | 240 | 94 | Y | N |  | 2.63 |  |  | 100 | 175 | 300 | 0.17 | 0.33 | 0.5 | 0.83 | 1.25 | 1.67 | 91.5 | 94.3 | 94.8 | 94.7 | 94.3 | 93.5 | 94.3 | 91.6 | 94.2 | 94.7 | 94.5 | 94.3 | 93.5 | 94.3 | 90.7 | 93.4 | 94.1 | 94 | 93.8 | 93.2 | 93.7
KACO | blueplanet 2.0 TL1 M1 WM OD US3x [208V] | 2.0 kW Utility Interactive Inverter (208V), x may be 3, 8, 9, A, C or D | 2.04 | 208 | 96 | Y | N |  | 4.67 |  |  | 100 | 390 | 510 | 0.2 | 0.41 | 0.61 | 1.02 | 1.53 | 2.04 | 90.7 | 94.3 | 95.4 | 96.2 | 96.3 | 96 | 95.8 | 91.3 | 94.8 | 96.1 | 96.8 | 97 | 96.9 | 96.5 | 89.6 | 94.4 | 95.7 | 96.5 | 96.8 | 96.8 | 96.2
KACO | blueplanet 2.0 TL1 M1 WM OD US3x [240V] | 2.0 kW Utility Interactive Inverter (240V), x may be 3, 8, 9, A, C or D | 2.07 | 240 | 96.5 | Y | N |  | 4.66 |  |  | 100 | 390 | 510 | 0.21 | 0.41 | 0.62 | 1.04 | 1.55 | 2.07 | 89.7 | 94.2 | 95.3 | 96.2 | 96.4 | 96 | 95.8 | 91.4 | 95.3 | 96.2 | 97 | 97.3 | 96.5 | 96.7 | 89.6 | 94.5 | 95.8 | 96.8 | 97.1 | 97.2 | 96.5
KACO | blueplanet 2502x [208V] | 2.5 kW, 208 Vac, Utility Interactive Inverter | 2.5 | 208 | 95 | Y | N |  | 0.29 |  |  | 100 | 265 | 450 | 0.25 | 0.5 | 0.75 | 1.25 | 1.875 | 2.5 | 93.1 | 95.3 | 95.6 | 95.6 | 95.3 | 94.7 | 95.3 | 93.5 | 95 | 95.4 | 95.5 | 95.2 | 94.6 | 95.2 | 94.1 | 94.5 | 94.9 | 95 | 94.7 | 94.2 | 94.7
KACO | blueplanet 2502x [240V] | 2.5 kW, 240 Vac, Utility Interactive Inverter | 2.5 | 240 | 95.5 | Y | N |  | 0.39 |  |  | 100 | 265 | 450 | 0.25 | 0.5 | 0.75 | 1.25 | 1.875 | 2.5 | 93.2 | 95.5 | 95.9 | 95.9 | 95.6 | 95.1 | 95.6 | 93.6 | 95.2 | 95.7 | 95.8 | 95.6 | 95 | 95.5 | 94.2 | 94.7 | 95.1 | 95.3 | 95.1 | 94.6 | 95
KACO | blueplanet 2502xi [208V] | 2.5 kW, 208 Vac, 125-500 Vdc Utility Interactive Inverter | 2.5 | 208 | 95 | Y | N |  | 0.29 |  |  | 100 | 265 | 450 | 0.25 | 0.5 | 0.75 | 1.25 | 1.875 | 2.5 | 93.1 | 95.3 | 95.6 | 95.6 | 95.3 | 94.7 | 95.3 | 93.5 | 95 | 95.4 | 95.5 | 95.2 | 94.6 | 95.2 | 94.1 | 94.5 | 94.9 | 95 | 94.7 | 94.2 | 94.7
KACO | blueplanet 2502xi [240V] | 2.5 kW, 240 Vac, 125-500 Vdc Utility Interactive Inverter | 2.5 | 240 | 95.5 | Y | N |  | 0.39 |  |  | 100 | 265 | 450 | 0.25 | 0.5 | 0.75 | 1.25 | 1.875 | 2.5 | 93.2 | 95.5 | 95.9 | 95.9 | 95.6 | 95.1 | 95.6 | 93.6 | 95.2 | 95.7 | 95.8 | 95.6 | 95 | 95.5 | 94.2 | 94.7 | 95.1 | 95.3 | 95.1 | 94.6 | 95
KACO | blueplanet 2901xi [240V] | 2.9 kW, 240 Vac, 125-400 Vdc Utility Interactive Inverter | 2.86 | 240 | 94 | Y | N |  | 2.77 |  |  | 100 | 175 | 300 | 0.29 | 0.57 | 0.86 | 1.43 | 2.15 | 2.86 | 91.1 | 94.1 | 94.5 | 94.7 | 94.1 | 93.3 | 94.1 | 90.5 | 93.7 | 94.3 | 94.5 | 93.8 | 93 | 93.8 | 90.6 | 93.2 | 94.3 | 93.9 | 93.2 | 92.5 | 93.4
KACO | blueplanet 3.0 TL1 M1 WM OD US3x [208V] | 3.0 kW Utility Interactive Inverter (208V), x may be 3, 8, 9, A, C or D | 3.05 | 208 | 96 | Y | N |  | 4.42 |  |  | 100 | 390 | 510 | 0.3 | 0.61 | 0.91 | 1.52 | 2.29 | 3.05 | 92 | 94.7 | 95.6 | 95.9 | 95.7 | 95.3 | 95.5 | 93.4 | 95.9 | 96.6 | 97 | 96.9 | 96.7 | 96.7 | 92.3 | 95.5 | 96.2 | 96.7 | 96.7 | 96.5 | 96.4
KACO | blueplanet 3.0 TL1 M1 WM OD US3x [240V] | 3.0 kW Utility Interactive Inverter (240V), x may be 3, 8, 9, A, C or D | 3.12 | 240 | 96.5 | Y | N |  | 4.64 |  |  | 100 | 390 | 510 | 0.31 | 0.62 | 0.94 | 1.56 | 2.34 | 3.12 | 91.4 | 94.5 | 95.5 | 96 | 95.9 | 95.6 | 95.6 | 93.6 | 96 | 96.7 | 97.3 | 97.3 | 96.8 | 97 | 92.2 | 95.5 | 96.4 | 97 | 97.2 | 97 | 96.7
KACO | blueplanet 3502x [208V] | 3.5 kW, 208 Vac, Utility Interactive with or without integrated wireway | 3.5 | 208 | 95.5 | Y | N |  | 0.26 |  |  | 100 | 280 | 510 | 0.35 | 0.7 | 1.05 | 1.75 | 2.63 | 3.5 | 93.5 | 95.5 | 95.9 | 95.9 | 95.6 | 95.2 | 95.6 | 93 | 95.1 | 95.6 | 95.7 | 95.5 | 95 | 95.4 | 91.7 | 94.2 | 94.8 | 95.1 | 95.1 | 94.8 | 94.9
KACO | blueplanet 3502x [240V] | 3.5 kW, 240 Vac, Utility Interactive with or without integrated wireway | 3.5 | 240 | 95.5 | Y | N |  | 0.36 |  |  | 100 | 280 | 510 | 0.35 | 0.7 | 1.05 | 1.75 | 2.63 | 3.5 | 93.5 | 95.7 | 96.2 | 96.2 | 96 | 95.6 | 95.9 | 93 | 95.3 | 95.8 | 96 | 95.8 | 95.4 | 95.7 | 91.6 | 94.4 | 95.1 | 95.3 | 95.4 | 95.1 | 95.1
KACO | blueplanet 3502xi [208V] | 3.5 kW, 208 Vac, 200-600 Vdc Utility Interactive Inverter | 3.5 | 208 | 95.5 | Y | N |  | 0.26 |  |  | 100 | 280 | 510 | 0.35 | 0.7 | 1.05 | 1.75 | 2.63 | 3.5 | 93.5 | 95.5 | 95.9 | 95.9 | 95.6 | 95.2 | 95.6 | 93 | 95.1 | 95.6 | 95.7 | 95.5 | 95 | 95.4 | 91.7 | 94.2 | 94.8 | 95.1 | 95.1 | 94.8 | 94.9
KACO | blueplanet 3502xi [240V] | 3.5 kW, 240 Vac, 200-600 Vdc Utility Interactive Inverter | 3.5 | 240 | 95.5 | Y | N |  | 0.36 |  |  | 100 | 280 | 510 | 0.35 | 0.7 | 1.05 | 1.75 | 2.63 | 3.5 | 93.5 | 95.7 | 96.2 | 96.2 | 96 | 95.6 | 95.9 | 93 | 95.3 | 95.8 | 96 | 95.8 | 95.4 | 95.7 | 91.6 | 94.4 | 95.1 | 95.3 | 95.4 | 95.1 | 95.1
KACO | blueplanet 3601xi [240V] | 3.6 kW, 240 Vac, Utility Interactive Inverter | 3.6 | 240 | 93.5 | Y | N |  | 3.11 |  |  | 100 | 175 | 300 | 0.36 | 0.72 | 1.08 | 1.8 | 2.7 | 3.6 | 89.9 | 93.3 | 94.2 | 94.3 | 94 | 93.3 | 93.8 | 89.7 | 93.1 | 94.1 | 94.2 | 93.9 | 93.2 | 93.7 | 89 | 92.4 | 93.5 | 93.8 | 93.6 | 92.9 | 93.3
KACO | blueplanet 4.0 TL1 M1 WM OD US3x [208V] | 4.0 kW Utility Interactive Inverter (208V), x may be 3, 8, 9, A, C or D | 4.06 | 208 | 96.5 | Y | N |  | 4.53 |  |  | 100 | 390 | 510 | 0.41 | 0.81 | 1.22 | 2.03 | 3.05 | 4.06 | 93 | 95.4 | 96 | 96.3 | 96 | 95.6 | 95.9 | 93.7 | 96 | 96.6 | 96.9 | 96.8 | 96.5 | 96.6 | 92.5 | 95.3 | 96.1 | 96.6 | 96.6 | 96.3 | 96.3
KACO | blueplanet 4.0 TL1 M1 WM OD US3x [240V] | 4.0 kW Utility Interactive Inverter (240V), x may be 3, 8, 9, A, C or D | 4.15 | 240 | 96.5 | Y | N |  | 4.65 |  |  | 100 | 390 | 510 | 0.42 | 0.83 | 1.25 | 2.08 | 3.11 | 4.15 | 92.7 | 95.4 | 95.9 | 96.4 | 96.3 | 96 | 96 | 94.3 | 96.3 | 96.9 | 97.3 | 97.3 | 96.6 | 97 | 92.8 | 95.8 | 96.4 | 96.9 | 97 | 96.7 | 96.7
KACO | blueplanet 5.0 TL1 M1 WM OD US3x [208V] | 5.0 kW Utility Interactive Inverter (208V), x may be 3, 8, 9, A, C or D | 4.65 | 208 | 96.5 | Y | N |  | 4.58 |  |  | 100 | 390 | 510 | 0.47 | 0.93 | 1.4 | 2.33 | 3.49 | 4.65 | 93.6 | 95.8 | 96.2 | 96.4 | 96 | 95.4 | 96 | 94.4 | 96.3 | 96.8 | 96.9 | 96.6 | 96.2 | 96.6 | 93.4 | 95.7 | 96.3 | 96.6 | 96.4 | 96.1 | 96.3
KACO | blueplanet 5002x [208V] | 5 kW, 208 Vac, Utility Interactive with or without integrated wireway | 5 | 208 | 95 | Y | N |  | 0.26 |  |  | 100 | 280 | 510 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 94.3 | 95.8 | 96 | 95.7 | 95.2 | 94.4 | 95.3 | 94 | 95.5 | 95.8 | 95.6 | 95.1 | 94.3 | 95.2 | 92.7 | 94.6 | 95 | 95.2 | 94.8 | 94.1 | 94.8
KACO | blueplanet 5002x [240V] | 5 kW, 240 Vac, Utility Interactive with or without integrated wireway | 5 | 240 | 95.5 | Y | N |  | 0.36 |  |  | 100 | 280 | 510 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 94.6 | 96.2 | 96.3 | 96.1 | 95.6 | 94.9 | 95.7 | 94.4 | 95.8 | 96 | 95.9 | 95.5 | 94.9 | 95.6 | 93.2 | 94.9 | 95.3 | 95.6 | 95.2 | 94.6 | 95.2
KACO | blueplanet 5002xi [208V] | 5 kW, 208 Vac, 200-600 Vdc Utility Interactive Inverter | 5 | 208 | 95 | Y | N |  | 0.26 |  |  | 100 | 280 | 510 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 94.3 | 95.8 | 96 | 95.7 | 95.2 | 94.4 | 95.3 | 94 | 95.5 | 95.8 | 95.6 | 95.1 | 94.3 | 95.2 | 92.7 | 94.6 | 95 | 95.2 | 94.8 | 94.1 | 94.8
KACO | blueplanet 5002xi [240V] | 5 kW, 240 Vac, 200-600 Vdc Utility Interactive Inverter | 5 | 240 | 95.5 | Y | N |  | 0.36 |  |  | 100 | 280 | 510 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 94.6 | 96.2 | 96.3 | 96.1 | 95.6 | 94.9 | 95.7 | 94.4 | 95.8 | 96 | 95.9 | 95.5 | 94.9 | 95.6 | 93.2 | 94.9 | 95.3 | 95.6 | 95.2 | 94.6 | 95.2
KACO | blueplanet 5.0 TL1 M1 WM OD US3x [240V] | 5.0 kW Utility Interactive Inverter (240V), x may be 3, 8, 9, A, C or D | 5.17 | 240 | 96.5 | Y | N |  | 4.44 |  |  | 100 | 390 | 510 | 0.52 | 1.03 | 1.55 | 2.58 | 3.88 | 5.17 | 94 | 95.8 | 96.4 | 96.6 | 96.2 | 95.9 | 96.2 | 95.2 | 96.8 | 97.2 | 97.3 | 97.1 | 96.3 | 97 | 94 | 96.1 | 96.8 | 97.1 | 96.9 | 96.6 | 96.8
KACO | blueplanet 6400M [208V] | 6.4 kW 208 Vac Utility Interactive Inverter with Tigo Management Unit | 6.4 | 208 | 96.5 | Y | N |  | 0.26 |  |  | 100 | 369 | 510 | 0.64 | 1.28 | 1.92 | 3.2 | 4.8 | 6.4 | 94.4 | 96.6 | 96.9 | 97 | 96.9 | 96.6 | 96.8 | 93.5 | 96.1 | 96.5 | 96.8 | 96.7 | 96.5 | 96.5 | 89.5 | 94.3 | 95.4 | 96.1 | 96.1 | 96 | 95.7
KACO | blueplanet 6400M [240V] | 6.4 kW 240 Vac Utility Interactive Inverter with Tigo Management Unit | 6.4 | 240 | 96.5 | Y | N |  | 0.45 |  |  | 100 | 402 | 510 | 0.64 | 1.28 | 1.92 | 3.2 | 4.8 | 6.4 | 94.6 | 96.7 | 96.7 | 97.1 | 97.1 | 97 | 96.9 | 93.8 | 96.3 | 96.9 | 97.1 | 97.1 | 97 | 96.9 | 90 | 94.7 | 95.7 | 96.4 | 96.5 | 96.5 | 96.1
KACO | blueplanet 6400x [208V] | 6.4 kW, 208 Vac, Utility Interactive with or without integrated wireway | 6.4 | 208 | 96.5 | Y | N |  | 0.26 |  |  | 100 | 369 | 510 | 0.64 | 1.28 | 1.92 | 3.2 | 4.8 | 6.4 | 94.4 | 96.6 | 96.9 | 97 | 96.9 | 96.6 | 96.8 | 93.5 | 96.1 | 96.5 | 96.8 | 96.7 | 96.5 | 96.5 | 89.5 | 94.3 | 95.4 | 96.1 | 96.1 | 96 | 95.7
KACO | blueplanet 6400x [240V] | 6.4 kW, 240 Vac, Utility Interactive with or without integrated wireway | 6.4 | 240 | 96.5 | Y | N |  | 0.45 |  |  | 100 | 402 | 510 | 0.64 | 1.28 | 1.92 | 3.2 | 4.8 | 6.4 | 94.6 | 96.7 | 96.7 | 97.1 | 97.1 | 97 | 96.9 | 93.8 | 96.3 | 96.9 | 97.1 | 97.1 | 97 | 96.9 | 90 | 94.7 | 95.7 | 96.4 | 96.5 | 96.5 | 96.1
KACO | blueplanet 6400xi [208V] | 6.4 kW, 208 Vac, Utility Interactive Inverter | 6.4 | 208 | 96.5 | Y | N |  | 0.26 |  |  | 100 | 369 | 510 | 0.64 | 1.28 | 1.92 | 3.2 | 4.8 | 6.4 | 94.4 | 96.6 | 96.9 | 97 | 96.9 | 96.6 | 96.8 | 93.5 | 96.1 | 96.5 | 96.8 | 96.7 | 96.5 | 96.5 | 89.5 | 94.3 | 95.4 | 96.1 | 96.1 | 96 | 95.7
KACO | blueplanet 6400xi [240V] | 6.4 kW, 240 Vac, Utility Interactive Inverter | 6.4 | 240 | 96.5 | Y | N |  | 0.45 |  |  | 100 | 402 | 510 | 0.64 | 1.28 | 1.92 | 3.2 | 4.8 | 6.4 | 94.6 | 96.7 | 96.7 | 97.1 | 97.1 | 97 | 96.9 | 93.8 | 96.3 | 96.9 | 97.1 | 97.1 | 97 | 96.9 | 90 | 94.7 | 95.7 | 96.4 | 96.5 | 96.5 | 96.1
KACO | blueplanet 7600M [208V] | 7.6 kW 208 Vac Utility Interactive Inverter with Tigo Management Unit | 7.6 | 208 | 96.5 | Y | N |  | 0.26 |  |  | 100 | 369 | 510 | 0.76 | 1.52 | 2.28 | 3.8 | 5.7 | 7.6 | 95.1 | 96.7 | 97 | 96.9 | 96.7 | 96.4 | 96.7 | 94.3 | 96.3 | 96.7 | 96.8 | 96.6 | 96.3 | 96.5 | 90.9 | 94.9 | 95.7 | 96.1 | 96.1 | 95.8 | 95.7
KACO | blueplanet 7600M [240V] | 7.6 kW 240 Vac Utility Interactive Inverter with Tigo Management Unit | 7.6 | 240 | 96.5 | Y | N |  | 0.36 |  |  | 100 | 402 | 510 | 0.76 | 1.52 | 2.28 | 3.8 | 5.7 | 7.6 | 94.7 | 96.8 | 97.1 | 97.1 | 97 | 96.7 | 96.9 | 94 | 96.5 | 96.9 | 97 | 96.9 | 96.6 | 96.8 | 91.4 | 95.3 | 96.1 | 96.4 | 96.4 | 96.3 | 96.1
KACO | blueplanet 7600x [208V] | 7.6 kW, 208 Vac, Utility Interactive with or without integrated wireway | 7.6 | 208 | 96.5 | Y | N |  | 0.26 |  |  | 100 | 369 | 510 | 0.76 | 1.52 | 2.28 | 3.8 | 5.7 | 7.6 | 95.1 | 96.7 | 97 | 96.9 | 96.7 | 96.4 | 96.7 | 94.3 | 96.3 | 96.7 | 96.8 | 96.6 | 96.3 | 96.5 | 90.9 | 94.9 | 95.7 | 96.1 | 96.1 | 95.8 | 95.7
KACO | blueplanet 7600x [240V] | 7.6 kW, 240 Vac, Utility Interactive with or without integrated wireway | 7.6 | 240 | 96.5 | Y | N |  | 0.36 |  |  | 100 | 402 | 510 | 0.76 | 1.52 | 2.28 | 3.8 | 5.7 | 7.6 | 94.7 | 96.8 | 97.1 | 97.1 | 97 | 96.7 | 96.9 | 94 | 96.5 | 96.9 | 97 | 96.9 | 96.6 | 96.8 | 91.4 | 95.3 | 96.1 | 96.4 | 96.4 | 96.3 | 96.1
KACO | blueplanet 7600xi [208V] | 7.6 kW, 208 Vac, Utility Interactive Inverter | 7.6 | 208 | 96.5 | Y | N |  | 0.26 |  |  | 100 | 369 | 510 | 0.76 | 1.52 | 2.28 | 3.8 | 5.7 | 7.6 | 95.1 | 96.7 | 97 | 96.9 | 96.7 | 96.4 | 96.7 | 94.3 | 96.3 | 96.7 | 96.8 | 96.6 | 96.3 | 96.5 | 90.9 | 94.9 | 95.7 | 96.1 | 96.1 | 95.8 | 95.7
KACO | blueplanet 7600xi [240V] | 7.6 kW, 240 Vac, Utility Interactive Inverter | 7.6 | 240 | 96.5 | Y | N |  | 0.36 |  |  | 100 | 402 | 510 | 0.76 | 1.52 | 2.28 | 3.8 | 5.7 | 7.6 | 94.7 | 96.8 | 97.1 | 97.1 | 97 | 96.7 | 96.9 | 94 | 96.5 | 96.9 | 97 | 96.9 | 96.6 | 96.8 | 91.4 | 95.3 | 96.1 | 96.4 | 96.4 | 96.3 | 96.1
KACO | blueplanet 10.0 TL3 [480V] | 10 kW, 480 Vac, Utility Interactive Inverter, 280-600 Vdc input, 2x MPPT channel | 9.99 | 480 | 97 | Y | N |  | 1.59 |  |  | 100 | 430 | 480 | 1 | 2 | 3 | 4.99 | 7.49 | 9.99 | 93.7 | 95.9 | 96.3 | 96.6 | 96.5 | 96.2 | 96.3 | 93.8 | 96.2 | 96.9 | 97.2 | 97.2 | 97.1 | 97 | 94.3 | 96.4 | 96.9 | 97.3 | 97.3 | 97.2 | 97.1
KACO | XP10U-H4 (-PSD) [480V] | 10 kW, 600 Vdc, 480 Vac, 3-phase Utility Interactive Inverter | 9.99 | 480 | 97 | Y | N |  | 1.59 |  |  | 100 | 430 | 480 | 1 | 2 | 3 | 4.99 | 7.49 | 9.99 | 93.7 | 95.9 | 96.3 | 96.6 | 96.5 | 96.2 | 96.3 | 93.8 | 96.2 | 96.9 | 97.2 | 97.2 | 97.1 | 97 | 94.3 | 96.4 | 96.9 | 97.3 | 97.3 | 97.2 | 97.1
KACO | blueplanet 32.0 TL3 M1 [480V] | 32 kW, 600 Vdc, 480 Vac, Utility Interactive Inverter | 32 | 480 | 97 | Y | N |  | 1.42 |  |  | 310 | 530 | 600 | 3.2 | 6.4 | 9.6 | 16 | 24 | 32 | 94.2 | 95.6 | 96.2 | 96.5 | 96.4 | 96.2 | 96.3 | 97.6 | 98 | 98 | 98 | 97.8 | 97.6 | 97.9 | 96 | 96.9 | 97.3 | 97.6 | 97.6 | 97.5 | 97.5
KACO | blueplanet 32.0 TL3 M3 [480V] | 32 kW, 600 Vdc, 480 Vac, 3-phase, Utility Interactive Inverte,r 3 MPPT | 32 | 480 | 97 | Y | N |  | 1.42 |  |  | 310 | 530 | 600 | 3.2 | 6.4 | 9.6 | 16 | 24 | 32 | 94.2 | 95.6 | 96.2 | 96.5 | 96.4 | 96.2 | 96.3 | 97.6 | 98 | 98 | 98 | 97.8 | 97.6 | 97.9 | 96 | 96.9 | 97.3 | 97.6 | 97.6 | 97.5 | 97.5
KACO | blueplanet 40.0 TL3 M1 [480V] | 40 kW, 1000 Vdc, 480 Vac 3-phase, Utility Interactive Inverter | 40 | 480 | 97.5 | Y | N |  | 1.42 |  |  | 390 | 760 | 850 | 4 | 8 | 12 | 20 | 30 | 40 | 95.2 | 96.4 | 96.8 | 97 | 96.8 | 96.5 | 96.8 | 97.1 | 97.5 | 97.7 | 97.7 | 97.8 | 97.6 | 97.7 | 96.6 | 97 | 97.4 | 97.7 | 97.8 | 97.7 | 97.6
KACO | blueplanet 40.0 TL3 M3 [480V] | 40 kW, 1000 Vdc, 480 Vac, 3-phase Utility Interactive Inverter, 3 MPPT | 40 | 480 | 97.5 | Y | N |  | 1.42 |  |  | 390 | 760 | 850 | 4 | 8 | 12 | 20 | 30 | 40 | 95.2 | 96.4 | 96.8 | 97 | 96.8 | 96.5 | 96.8 | 97.1 | 97.5 | 97.7 | 97.7 | 97.8 | 97.6 | 97.7 | 96.6 | 97 | 97.4 | 97.7 | 97.8 | 97.7 | 97.6
KACO | XP42U-H2 [208V] | 42 kW, 208 Vac, 3-phase Utility Interactive Inverter | 41.35 | 208 | 95.5 | Y | N |  | 48.27 |  |  | 250 | 307.5 | 480 | 4.14 | 8.27 | 12.41 | 20.68 | 31.01 | 41.35 | 92 | 95 | 95.9 | 96.2 | 96.2 | 95.8 | 95.9 | 91.1 | 94.7 | 95.6 | 96 | 96.1 | 95.8 | 95.7 | 88.9 | 93.3 | 94.6 | 95.3 | 95.3 | 95.3 | 94.9
KACO | blueplanet 50.0 TL3 M1 [480V] | 50 kW, 1000 Vdc, 480 Vac, 3-phase Utility Interactive Inverter | 51.28 | 480 | 97.5 | Y | N |  | 1.42 |  |  | 480 | 760 | 850 | 5.13 | 10.26 | 15.38 | 25.64 | 38.46 | 51.28 | 95.4 | 97.4 | 97.6 | 97.5 | 97.1 | 96.8 | 97.2 | 95.6 | 97.3 | 97.7 | 98 | 98.1 | 97.6 | 97.9 | 98.3 | 98.4 | 98.2 | 98.1 | 97.9 | 97.7 | 98
KACO | blueplanet 50.0 TL3 M3 [480V] | 50 kW, 1000 Vdc, 480 Vac, 3-phase Utility Interactive Inverter, 3 MPPT | 51.28 | 480 | 97.5 | Y | N |  | 1.42 |  |  | 480 | 760 | 850 | 5.13 | 10.26 | 15.38 | 25.64 | 38.46 | 51.28 | 95.4 | 97.4 | 97.6 | 97.5 | 97.1 | 96.8 | 97.2 | 95.6 | 97.3 | 97.7 | 98 | 98.1 | 97.6 | 97.9 | 98.3 | 98.4 | 98.2 | 98.1 | 97.9 | 97.7 | 98
KACO | XP50U-H4 [480V] | 50 kW, 480 Vac, 3-phase Utility Interactive Inverter | 51.3 | 480 | 96 | Y | N |  | 44.68 |  |  | 300 | 345 | 480 | 5.13 | 10.26 | 15.39 | 25.65 | 38.48 | 51.3 | 91.9 | 95.3 | 96.1 | 96.7 | 96.6 | 96.3 | 96.3 | 91.6 | 95 | 95.9 | 96.4 | 96.4 | 96.2 | 96.1 | 89.6 | 94 | 95.1 | 95.9 | 95.9 | 95.7 | 95.5
KACO | XP100U-H2 [480V] | 100 kW, 480 Vac, 3-phase Utility Interactive Inverter | 100 | 480 | 95.5 | Y | N |  | 60.43 |  |  | 300 | 345 | 480 | 10 | 20 | 30 | 50 | 75 | 100 | 93 | 95.3 | 95.9 | 96 | 95.8 | 95.4 | 95.7 | 91.5 | 94.8 | 95.7 | 96.2 | 96.1 | 95.8 | 95.8 | 88.5 | 93.6 | 94.8 | 95.5 | 95.7 | 95.5 | 95.2
KACO | XP100U-H4 [480V] | 100 kW, 480 Vac, 3-phase Utility Interactive Inverter | 100 | 480 | 96 | Y | N |  | 61.75 |  |  | 300 | 345 | 480 | 10 | 20 | 30 | 50 | 75 | 100 | 92.6 | 95.1 | 96 | 96.5 | 96.4 | 96.1 | 96.1 | 91.7 | 94.7 | 95.8 | 96.4 | 96.3 | 96.1 | 96 | 87.8 | 93.5 | 94.8 | 95.7 | 95.9 | 95.8 | 95.3
KACO | XP500U-TL | 500 kW Utility Interactive Inverter | 500 |  | 98 | Y | N |  | 108.4 |  |  | 550 | 613 | 800 | 50 | 100 | 150 | 250 | 375 | 500 | 97.4 | 98.3 | 98.4 | 98.4 | 98.3 | 98 | 98.3 | 96.9 | 98 | 98.2 | 98.2 | 98.1 | 97.9 | 98.1 | 95.5 | 97.3 | 97.7 | 97.8 | 97.7 | 97.6 | 97.6
KACO | XP550U-TL | 550 kW Utility Interactive Inverter | 550 |  | 98 | Y | N |  | 108.6 |  |  | 550 | 613 | 800 | 55 | 110 | 165 | 275 | 412.5 | 550 | 97.5 | 98.3 | 98.4 | 98.4 | 98.2 | 97.9 | 98.3 | 97.1 | 98.1 | 98.1 | 98.2 | 98 | 97.6 | 98 | 95.8 | 97.4 | 97.7 | 97.7 | 97.6 | 97.4 | 97.6
KACO | KACO blueplanet 750 TL3 750 TL3 M1 GM OD USX0 | 750 kW Utility Interactive Inverter | 749.4 |  | 98 | Y | N |  | 149 |  |  | 620 | 665 | 800 | 74.94 | 149.9 | 224.8 | 374.7 | 562.1 | 749.4 | 97.4 | 98.3 | 98.5 | 98.5 | 98.3 | 98.2 | 98.3 | 97.2 | 98.2 | 98.4 | 98.4 | 98.3 | 98.1 | 98.3 | 96.3 | 97.8 | 98 | 98.2 | 98.2 | 98 | 98.1
KACO | KACO blueplanet 875 TL3 875 TL3 M1 GM OD USX0 | 875 kW Utility Interactive Inverter | 874 |  | 98 | Y | N |  | 148.7 |  |  | 620 | 665 | 800 | 87.4 | 174.8 | 262.2 | 437 | 655.5 | 874 | 97.7 | 98.4 | 98.5 | 98.6 | 98.3 | 98 | 98.3 | 97.4 | 98.2 | 98.4 | 98.4 | 98.3 | 97.9 | 98.3 | 96.8 | 97.9 | 98.2 | 98.2 | 98.2 | 97.9 | 98.1
KACO | KACO blueplanet 1000 TL3 1000 TL3 M1 GM OD USX0 | 1000 kW Utility Interactive Inverter | 1000 |  | 98 | Y | N |  | 148.2 |  |  | 620 | 665 | 800 | 100 | 200 | 300 | 500 | 750 | 1000 | 97.8 | 98.3 | 98.4 | 98.4 | 98.1 | 97.7 | 98.2 | 97.5 | 98.2 | 98.3 | 98.3 | 98.1 | 97.7 | 98.1 | 97 | 97.9 | 98.1 | 98.1 | 98 | 97.6 | 98
KACO | KACO blueplanet 1500 TL3 M1 GM OD USX0 | 1500 kW Utility Interactive Inverter | 1500 |  | 98 | Y | N |  | 180.91 |  |  | 580 | 635 | 800 | 150 | 300 | 450 | 750 | 1125 | 1500 | 96.9 | 98.1 | 98.2 | 98.2 | 98.1 | 97.8 | 98 | 96.5 | 97.8 | 98.1 | 98.1 | 98 | 97.7 | 98 | 95.1 | 97.2 | 97.6 | 97.8 | 97.8 | 97.6 | 97.6
KACO | KACO blueplanet 2200 TL3 M1 GM OD USX0 | 2200 kW Utility Interactive Inverter | 2000 |  | 98 | Y | N |  | 176.74 |  |  | 580 | 635 | 800 | 200 | 400 | 600 | 1000 | 1500 | 2000 | 97.5 | 98.2 | 98.3 | 98.2 | 97.8 | 97.4 | 97.9 | 97.2 | 98.1 | 98.2 | 98.1 | 97.8 | 97.4 | 97.9 | 96.1 | 97.6 | 97.8 | 97.9 | 97.7 | 97.3 | 97.6
Kostal Solar Electric | Piko 5.3 US | 5.3 kW 3-phase Inverter | 5.3 |  | 94 | Y | N |  | 0.96 | 5.3 | 0.96 | 100 | 380 | 480 | 0.53 | 1.06 | 1.59 | 2.65 | 3.98 | 5.3 | 90.5 | 92.9 | 92.9 | 93.4 | 93.4 | 93.2 | 93.2 | 92.6 | 94.3 | 94.9 | 94.8 | 94.8 | 94.2 | 94.7 | 91.3 | 93.5 | 94.1 | 94.6 | 94.2 | 93.7 | 94.1
LeadSolar Energy Co., Ltd | LS560 [240V] | 500 W, 1-phase Utility Interactive Inverter | 0.5 | 240 | 95.5 | N | Y |  | 0.09 |  |  | 27 | 36 | 45 | 0.05 | 0.1 | 0.15 | 0.25 | 0.375 | 0.5 | 94.6 | 95.4 | 95.6 | 95.6 | 95.4 | 94.9 | 95.4 | 94.2 | 95.6 | 95.2 | 95.9 | 95.7 | 95.3 | 95.6 | 93.7 | 93.8 | 94.8 | 95.9 | 95.7 | 95.5 | 95.5 |  | 2018-09-04
LeadSolar Energy Co., Ltd | LS600 [240V] | 500 W, 1-phase Utility Interactive Inverter | 0.5 | 240 | 95.5 | N | Y |  | 0.09 |  |  | 27 | 36 | 45 | 0.05 | 0.1 | 0.15 | 0.25 | 0.375 | 0.5 | 94.6 | 95.4 | 95.6 | 95.6 | 95.4 | 94.9 | 95.4 | 94.2 | 95.6 | 95.2 | 95.9 | 95.7 | 95.3 | 95.6 | 93.7 | 93.8 | 94.8 | 95.9 | 95.7 | 95.5 | 95.5 | 2017-10-13 | 2018-10-15
LeadSolar Energy Co., Ltd | LS600T [208V] | 500 W, 1-phase Utility Interactive Inverter | 0.5 | 208 | 95 | N | Y |  | 1 |  |  | 27 | 36 | 45 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 93.6 | 95 | 95.1 | 95.3 | 94.7 | 93.8 | 94.8 | 93.7 | 94.2 | 95.1 | 95.7 | 95.5 | 95 | 95.3 | 93.2 | 93.2 | 94.9 | 95.7 | 95.8 | 95.4 | 95.4 |  | 2018-09-04
LeadSolar Energy Co., Ltd | LS600ES [277V] | 0.6 kW, 277 Vac, 1-phase Utility Interactive Inverter | 0.6 | 277 | 96 | N | Y |  | 0.04 |  |  | 52 | 54 | 56 | 0.06 | 0.12 | 0.18 | 0.3 | 0.45 | 0.6 | 92.6 | 95.4 | 96.1 | 95.8 | 96.1 | 96.1 | 95.9 | 92.4 | 95.4 | 96 | 95.8 | 96.1 | 96.1 | 95.9 | 92.3 | 95.3 | 96 | 96 | 96.1 | 96.1 | 95.9 |  | 2018-09-04
LeadSolar Energy Co., Ltd | LS700TS-208 [208V] | 0.6 kW, 208 Vac, 1-phase Utility Interactive Inverter | 0.6 | 208 | 95.5 | N | Y |  | 0.21 |  |  | 52 | 54 | 56 | 0.06 | 0.12 | 0.18 | 0.3 | 0.45 | 0.6 | 91.2 | 94.3 | 94.9 | 95.5 | 95.6 | 95.3 | 95.2 | 90.1 | 93.7 | 95 | 95.7 | 95.8 | 95.5 | 95.3 | 90.2 | 93.9 | 95 | 95.4 | 95.8 | 95.6 | 95.3 |  | 2018-09-04
LeadSolar Energy Co., Ltd | LS650S [277V] | 0.65 kW, 277 Vac, 1-phase Utility Interactive Inverter | 0.65 | 277 | 96 | N | Y |  | 0.04 |  |  | 52 | 54 | 56 | 0.065 | 0.13 | 0.195 | 0.325 | 0.488 | 0.65 | 93 | 95.6 | 96.1 | 95.7 | 96.1 | 96 | 95.9 | 92.9 | 95.5 | 96.1 | 95.8 | 96.1 | 96.1 | 95.9 | 92.7 | 95.5 | 96.1 | 95.9 | 96.1 | 96.1 | 95.9 |  | 2018-09-04
LeadSolar Energy Co., Ltd | LS700S [277V] | 0.7 kW, 277 Vac, 1-phase Utility Interactive Inverter | 0.7 | 277 | 96 | N | Y |  | 0.04 |  |  | 52 | 54 | 56 | 0.07 | 0.14 | 0.21 | 0.35 | 0.525 | 0.7 | 93.4 | 95.7 | 96.1 | 95.4 | 96 | 95.8 | 95.8 | 93.2 | 95.7 | 96.2 | 95.5 | 96.1 | 96 | 95.8 | 93.1 | 95.6 | 96.2 | 95.8 | 96.1 | 96 | 95.9 |  | 2018-09-04
LeadSolar Energy Co., Ltd | LS700TS-240 [240V] | 0.7 kW, 240 Vac, 1-phase Utility Interactive Inverter | 0.7 | 240 | 95.5 | N | Y |  | 0.21 |  |  | 52 | 54 | 56 | 0.07 | 0.14 | 0.21 | 0.35 | 0.53 | 0.7 | 91.5 | 94.3 | 94.9 | 95.9 | 96 | 95.6 | 95.6 | 90.8 | 93.8 | 95.2 | 96 | 95.9 | 95.6 | 95.5 | 90.4 | 94.1 | 95.1 | 95.5 | 96 | 95.7 | 95.4 |  | 2018-09-04
LeadSolar Energy Co., Ltd | LS1400-240V [240V] | 1400 W, 240 Vac Utility Interactive Micro Inverter | 1.4 | 240 | 95 | N | Y |  | 0.13 |  |  | 37.5 | 40 | 44 | 0.14 | 0.28 | 0.42 | 0.7 | 1.05 | 1.4 | 91.8572 | 94.1762 | 94.9474 | 95.3395 | 95.2958 | 94.6945 | 95.0396 | 91.7584 | 94.1999 | 94.9268 | 95.3636 | 95.3473 | 94.8208 | 95.073 | 91.5513 | 94.2107 | 94.883 | 95.3302 | 95.3488 | 94.956 | 95.0606 | 2018-09-04
Leatec Fine Ceramics | CM21-0113 [240V] | 300 W, 240 Vac, Utility Interactive Inverter | 0.286 | 240 | 96 | N | Y |  | 0.1 |  |  | 26 | 31 | 43 | 0.03 | 0.06 | 0.09 | 0.14 | 0.22 | 0.29 | 92.1 | 94.4 | 95 | 95.7 | 96.3 | 95.9 | 95.7 | 91.6 | 95.1 | 94.8 | 96.5 | 96.5 | 96.5 | 96.1 | 89.9 | 94.3 | 95.3 | 96.3 | 96.2 | 96.2 | 95.8
LG Electronics Inc. | LG315E1K-A5 [208V] | 315 W DC, ACPV module with Enphase IQ6PLUS72-ACM-US Microinverter | 0.28 | 208 | 97 | N | Y | This model is specifically for the ACPV module. The microinverter is also sold as an individual unit. | 0.02 |  |  | 27 | 36 | 45 | 28 | 56 | 84 | 140 | 210 | 280 | 94.6361 | 96.3401 | 96.9302 | 97.3761 | 97.1425 | 96.5786 | 96.9975 | 94.5629 | 95.6844 | 96.451 | 97.1497 | 97.092 | 96.6838 | 96.8353 | 93.9289 | 95.0271 | 95.9707 | 96.9185 | 96.9131 | 96.595 | 96.5716 | 2017-08-01 | 2018-10-15
LG Electronics Inc. | LG315E1K-A5 [240V] | 315 W DC, ACPV module with Enphase IQ6PLUS72-ACM-US Microinverter | 0.28 | 240 | 97 | N | Y | This model is specifically for the ACPV module. The microinverter is also sold as an individual unit. | 0.02 |  |  | 27 | 36 | 45 | 28 | 56 | 84 | 140 | 210 | 280 | 94.2531 | 96.1631 | 96.8171 | 97.3026 | 97.1456 | 96.7165 | 96.9529 | 94.5548 | 95.7444 | 96.2814 | 97.2549 | 97.3334 | 97.1701 | 96.9919 | 93.9059 | 95.0901 | 95.7449 | 96.972 | 97.1487 | 97.0384 | 96.705 | 2017-08-01 | 2018-10-15
LG Electronics Inc. | LG320E1K-A5 [208V] | 320 W DC, ACPV module with Enphase IQ6PLUS72-ACM-US Microinverter | 0.28 | 208 | 97 | N | Y | This model is specifically for the ACPV module. The microinverter is also sold as an individual unit. | 0.02 |  |  | 27 | 36 | 45 | 28 | 56 | 84 | 140 | 210 | 280 | 94.6361 | 96.3401 | 96.9302 | 97.3761 | 97.1425 | 96.5786 | 96.9975 | 94.5629 | 95.6844 | 96.451 | 97.1497 | 97.092 | 96.6838 | 96.8353 | 93.9289 | 95.0271 | 95.9707 | 96.9185 | 96.9131 | 96.595 | 96.5716 | 2017-08-01 | 2018-10-15
LG Electronics Inc. | LG320E1K-A5 [240V] | 320 W DC, ACPV module with Enphase IQ6PLUS72-ACM-US Microinverter | 0.28 | 240 | 97 | N | Y | This model is specifically for the ACPV module. The microinverter is also sold as an individual unit. | 0.02 |  |  | 27 | 36 | 45 | 28 | 56 | 84 | 140 | 210 | 280 | 94.2531 | 96.1631 | 96.8171 | 97.3026 | 97.1456 | 96.7165 | 96.9529 | 94.5548 | 95.7444 | 96.2814 | 97.2549 | 97.3334 | 97.1701 | 96.9919 | 93.9059 | 95.0901 | 95.7449 | 96.972 | 97.1487 | 97.0384 | 96.705 | 2017-08-01 | 2018-10-15
LG Electronics Inc. | LG325E1C-A5 [208V] | 325 W DC, ACPV module with Enphase IQ6PLUS72-ACM-US Microinverter | 0.28 | 208 | 97 | N | Y | This model is specifically for the ACPV module. The microinverter is also sold as an individual unit. | 0.02 |  |  | 27 | 36 | 45 | 28 | 56 | 84 | 140 | 210 | 280 | 94.6361 | 96.3401 | 96.9302 | 97.3761 | 97.1425 | 96.5786 | 96.9975 | 94.5629 | 95.6844 | 96.451 | 97.1497 | 97.092 | 96.6838 | 96.8353 | 93.9289 | 95.0271 | 95.9707 | 96.9185 | 96.9131 | 96.595 | 96.5716 | 2017-08-01 | 2018-10-15
LG Electronics Inc. | LG325E1C-A5 [240V] | 325 W DC, ACPV module with Enphase IQ6PLUS72-ACM-US Microinverter | 0.28 | 240 | 97 | N | Y | This model is specifically for the ACPV module. The microinverter is also sold as an individual unit. | 0.02 |  |  | 27 | 36 | 45 | 28 | 56 | 84 | 140 | 210 | 280 | 94.2531 | 96.1631 | 96.8171 | 97.3026 | 97.1456 | 96.7165 | 96.9529 | 94.5548 | 95.7444 | 96.2814 | 97.2549 | 97.3334 | 97.1701 | 96.9919 | 93.9059 | 95.0901 | 95.7449 | 96.972 | 97.1487 | 97.0384 | 96.705 | 2017-08-01 | 2018-10-15
LG Electronics Inc. | LG325E1K-A5 [208V] | 325 W DC, ACPV module with Enphase IQ6PLUS72-ACM-US Microinverter | 0.28 | 208 | 97 | N | Y | This model is specifically for the ACPV module. The microinverter is also sold as an individual unit. | 0.02 |  |  | 27 | 36 | 45 | 28 | 56 | 84 | 140 | 210 | 280 | 94.6361 | 96.3401 | 96.9302 | 97.3761 | 97.1425 | 96.5786 | 96.9975 | 94.5629 | 95.6844 | 96.451 | 97.1497 | 97.092 | 96.6838 | 96.8353 | 93.9289 | 95.0271 | 95.9707 | 96.9185 | 96.9131 | 96.595 | 96.5716 | 2017-08-01 | 2018-10-15
LG Electronics Inc. | LG325E1K-A5 [240V] | 325 W DC, ACPV module with Enphase IQ6PLUS72-ACM-US Microinverter | 0.28 | 240 | 97 | N | Y | This model is specifically for the ACPV module. The microinverter is also sold as an individual unit. | 0.02 |  |  | 27 | 36 | 45 | 28 | 56 | 84 | 140 | 210 | 280 | 94.2531 | 96.1631 | 96.8171 | 97.3026 | 97.1456 | 96.7165 | 96.9529 | 94.5548 | 95.7444 | 96.2814 | 97.2549 | 97.3334 | 97.1701 | 96.9919 | 93.9059 | 95.0901 | 95.7449 | 96.972 | 97.1487 | 97.0384 | 96.705 | 2017-08-01 | 2018-10-15
LG Electronics Inc. | LG330E1C-A5 [208V] | 330 W DC, ACPV module with Enphase IQ6PLUS72-ACM-US Microinverter | 0.28 | 208 | 97 | N | Y | This model is specifically for the ACPV module. The microinverter is also sold as an individual unit. | 0.02 |  |  | 27 | 36 | 45 | 28 | 56 | 84 | 140 | 210 | 280 | 94.6361 | 96.3401 | 96.9302 | 97.3761 | 97.1425 | 96.5786 | 96.9975 | 94.5629 | 95.6844 | 96.451 | 97.1497 | 97.092 | 96.6838 | 96.8353 | 93.9289 | 95.0271 | 95.9707 | 96.9185 | 96.9131 | 96.595 | 96.5716 | 2017-08-01 | 2018-10-15
LG Electronics Inc. | LG330E1C-A5 [240V] | 330 W DC, ACPV module with Enphase IQ6PLUS72-ACM-US Microinverter | 0.28 | 240 | 97 | N | Y | This model is specifically for the ACPV module. The microinverter is also sold as an individual unit. | 0.02 |  |  | 27 | 36 | 45 | 28 | 56 | 84 | 140 | 210 | 280 | 94.3 | 96.2 | 96.8 | 97.3 | 97.1 | 96.7 | 97 | 94.6 | 95.7 | 96.3 | 97.3 | 97.3 | 97.2 | 97 | 93.9 | 95.1 | 95.7 | 97 | 97.1 | 97 | 96.7 | 2017-08-01 | 2018-10-15
LG Electronics Inc. | LG335E1C-A5 [208V] | 335 W DC, ACPV module with Enphase IQ6PLUS72-ACM-US Microinverter | 0.28 | 208 | 97 | N | Y | This model is specifically for the ACPV module. The microinverter is also sold as an individual unit. | 0.02 |  |  | 27 | 36 | 45 | 28 | 56 | 84 | 140 | 210 | 280 | 94.6 | 96.3 | 96.9 | 97.4 | 97.1 | 96.6 | 97 | 94.6 | 95.7 | 96.5 | 97.1 | 97.1 | 96.7 | 96.8 | 93.9 | 95 | 96 | 96.9 | 96.9 | 96.6 | 96.6 | 2017-08-01 | 2018-10-15
LG Electronics Inc. | LG335E1C-A5 [240V] | 335 W DC, ACPV module with Enphase IQ6PLUS72-ACM-US Microinverter | 0.28 | 240 | 97 | N | Y | This model is specifically for the ACPV module. The microinverter is also sold as an individual unit. | 0.02 |  |  | 27 | 36 | 45 | 28 | 56 | 84 | 140 | 210 | 280 | 94.3 | 96.2 | 96.8 | 97.3 | 97.1 | 96.7 | 97 | 94.6 | 95.7 | 96.3 | 97.3 | 97.3 | 97.2 | 97 | 93.9 | 95.1 | 95.7 | 97 | 97.1 | 97 | 96.7 | 2017-08-01 | 2018-10-15
LG Electronics Inc. | LG295A1C-B3 [208V] | 295W 208Vac Utility Interactive Microinverter | 0.29969 | 208 | 96 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.07 |  |  | 27 | 32 | 38 | 0.03 | 0.06 | 0.09 | 0.15 | 0.225 | 0.29969 | 93.8 | 95.7 | 96.2 | 96.3 | 96.1 | 95.6 | 96 | 93.7 | 95.6 | 96.2 | 96.4 | 96.3 | 95.9 | 96.2 | 93.4 | 95.4 | 96.2 | 96.5 | 96.5 | 96.2 | 96.3 |  | 2017-11-15
LG Electronics Inc. | LG295A1W-B3 [208V] | 295W 208Vac Utility Interactive Microinverter | 0.29969 | 208 | 96 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.07 |  |  | 27 | 32 | 38 | 0.03 | 0.06 | 0.09 | 0.15 | 0.225 | 0.29969 | 93.8 | 95.7 | 96.2 | 96.3 | 96.1 | 95.6 | 96 | 93.7 | 95.6 | 96.2 | 96.4 | 96.3 | 95.9 | 96.2 | 93.4 | 95.4 | 96.2 | 96.5 | 96.5 | 96.2 | 96.3 |  | 2017-11-15
LG Electronics Inc. | LG300A1C-B3 [208V] | 300W 208Vac Utility Interactive Microinverter | 0.29969 | 208 | 96 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.07 |  |  | 27 | 32 | 38 | 0.03 | 0.06 | 0.09 | 0.15 | 0.225 | 0.29969 | 93.8 | 95.7 | 96.2 | 96.3 | 96.1 | 95.6 | 96 | 93.7 | 95.6 | 96.2 | 96.4 | 96.3 | 95.9 | 96.2 | 93.4 | 95.4 | 96.2 | 96.5 | 96.5 | 96.2 | 96.3 |  | 2017-11-15
LG Electronics Inc. | LG300A1W-B3 [208V] | 300W 208Vac Utility Interactive Microinverter | 0.29969 | 208 | 96 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.07 |  |  | 27 | 32 | 38 | 0.03 | 0.06 | 0.09 | 0.15 | 0.225 | 0.29969 | 93.8 | 95.7 | 96.2 | 96.3 | 96.1 | 95.6 | 96 | 93.7 | 95.6 | 96.2 | 96.4 | 96.3 | 95.9 | 96.2 | 93.4 | 95.4 | 96.2 | 96.5 | 96.5 | 96.2 | 96.3 |  | 2017-11-15
LG Electronics Inc. | LG305A1C-B3 [208V] | 305W 208Vac Utility Interactive Microinverter | 0.29969 | 208 | 96 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.07 |  |  | 27 | 32 | 38 | 0.03 | 0.06 | 0.09 | 0.15 | 0.225 | 0.29969 | 93.8 | 95.7 | 96.2 | 96.3 | 96.1 | 95.6 | 96 | 93.7 | 95.6 | 96.2 | 96.4 | 96.3 | 95.9 | 96.2 | 93.4 | 95.4 | 96.2 | 96.5 | 96.5 | 96.2 | 96.3 |  | 2017-11-15
LG Electronics Inc. | LG305A1W-B3 [208V] | 305W 208Vac Utility Interactive Microinverter | 0.29969 | 208 | 96 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.07 |  |  | 27 | 32 | 38 | 0.03 | 0.06 | 0.09 | 0.15 | 0.225 | 0.29969 | 93.8 | 95.7 | 96.2 | 96.3 | 96.1 | 95.6 | 96 | 93.7 | 95.6 | 96.2 | 96.4 | 96.3 | 95.9 | 96.2 | 93.4 | 95.4 | 96.2 | 96.5 | 96.5 | 96.2 | 96.3 |  | 2017-11-15
LG Electronics Inc. | LM305UE-G1 [208V] | 300W, 208 Vac Utility Interactive Microinverter | 0.29969 | 208 | 96 | N | Y |  | 0.07 |  |  | 27 | 32 | 38 | 0.03 | 0.06 | 0.09 | 0.15 | 0.225 | 0.29969 | 93.8 | 95.7 | 96.2 | 96.3 | 96.1 | 95.6 | 96 | 93.7 | 95.6 | 96.2 | 96.4 | 96.3 | 95.9 | 96.2 | 93.4 | 95.4 | 96.2 | 96.5 | 96.5 | 96.2 | 96.3 |  | 2017-11-15
LG Electronics Inc. | LG295A1C-B3 [240V] | 295W 240Vac Utility Interactive Microinverter | 0.30497 | 240 | 96.5 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.09 |  |  | 27 | 32 | 38 | 0.0305 | 0.061 | 0.0915 | 0.1525 | 0.22875 | 0.30497 | 93.7 | 95.6 | 96.2 | 96.5 | 96.3 | 95.9 | 96.2 | 93.5 | 95.5 | 96.3 | 96.5 | 96.5 | 96.3 | 96.3 | 93.2 | 95.3 | 96.3 | 96.6 | 96.7 | 96.5 | 96.4 |  | 2017-11-15
LG Electronics Inc. | LG295A1W-B3 [240V] | 295W 240Vac Utility Interactive Microinverter | 0.30497 | 240 | 96.5 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.09 |  |  | 27 | 32 | 38 | 0.0305 | 0.061 | 0.0915 | 0.1525 | 0.22875 | 0.30497 | 93.7 | 95.6 | 96.2 | 96.5 | 96.3 | 95.9 | 96.2 | 93.5 | 95.5 | 96.3 | 96.5 | 96.5 | 96.3 | 96.3 | 93.2 | 95.3 | 96.3 | 96.6 | 96.7 | 96.5 | 96.4 |  | 2017-11-15
LG Electronics Inc. | LG300A1C-B3 [240V] | 300W 240Vac Utility Interactive Microinverter | 0.30497 | 240 | 96.5 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.09 |  |  | 27 | 32 | 38 | 0.0305 | 0.061 | 0.0915 | 0.1525 | 0.22875 | 0.30497 | 93.7 | 95.6 | 96.2 | 96.5 | 96.3 | 95.9 | 96.2 | 93.5 | 95.5 | 96.3 | 96.5 | 96.5 | 96.3 | 96.3 | 93.2 | 95.3 | 96.3 | 96.6 | 96.7 | 96.5 | 96.4 |  | 2017-11-15
LG Electronics Inc. | LG300A1W-B3 [240V] | 300W 240Vac Utility Interactive Microinverter | 0.30497 | 240 | 96.5 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.09 |  |  | 27 | 32 | 38 | 0.0305 | 0.061 | 0.0915 | 0.1525 | 0.22875 | 0.30497 | 93.7 | 95.6 | 96.2 | 96.5 | 96.3 | 95.9 | 96.2 | 93.5 | 95.5 | 96.3 | 96.5 | 96.5 | 96.3 | 96.3 | 93.2 | 95.3 | 96.3 | 96.6 | 96.7 | 96.5 | 96.4 |  | 2017-11-15
LG Electronics Inc. | LG305A1C-B3 [240V] | 305W 240Vac Utility Interactive Microinve | 0.30497 | 240 | 96.5 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.09 |  |  | 27 | 32 | 38 | 0.0305 | 0.061 | 0.0915 | 0.1525 | 0.22875 | 0.30497 | 93.7 | 95.6 | 96.2 | 96.5 | 96.3 | 95.9 | 96.2 | 93.5 | 95.5 | 96.3 | 96.5 | 96.5 | 96.3 | 96.3 | 93.2 | 95.3 | 96.3 | 96.6 | 96.7 | 96.5 | 96.4 |  | 2017-11-15
LG Electronics Inc. | LG305A1W-B3 [240V] | 305W 240Vac Utility Interactive Microinve | 0.30497 | 240 | 96.5 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.09 |  |  | 27 | 32 | 38 | 0.0305 | 0.061 | 0.0915 | 0.1525 | 0.22875 | 0.30497 | 93.7 | 95.6 | 96.2 | 96.5 | 96.3 | 95.9 | 96.2 | 93.5 | 95.5 | 96.3 | 96.5 | 96.5 | 96.3 | 96.3 | 93.2 | 95.3 | 96.3 | 96.6 | 96.7 | 96.5 | 96.4 |  | 2017-11-15
LG Electronics Inc. | LM305UE-G1 [240V] | 305W, 240 Vac Utility Interactive Microinverter | 0.30497 | 240 | 96.5 | N | Y |  | 0.09 |  |  | 27 | 32 | 38 | 0.0305 | 0.061 | 0.0915 | 0.1525 | 0.22875 | 0.30497 | 93.7 | 95.6 | 96.2 | 96.5 | 96.3 | 95.9 | 96.2 | 93.5 | 95.5 | 96.3 | 96.5 | 96.5 | 96.3 | 96.3 | 93.2 | 95.3 | 96.3 | 96.6 | 96.7 | 96.5 | 96.4 |  | 2017-11-15
Lixma Tech | LSI4000 [240V] | 4000 W, 240 Vac Utility Interactive Inverter | 4.03 | 240 | 95 | Y | N |  | 0.19 |  |  | 250 | 310 | 440 | 0.4 | 0.81 | 1.21 | 2.02 | 3.02 | 4.03 | 91.6 | 94.5 | 95.2 | 95.3 | 95 | 93.9 | 94.9 | 90.2 | 94.5 | 95.5 | 95.8 | 95.6 | 95 | 95.3 | 87.4 | 92.8 | 94 | 95 | 95.2 | 94.6 | 94.5
Mage Solar | POWERTEC Plus 240 / 6 PL-US AC [240V] | 240 W, 240 Vac Inverter | 0.24 | 240 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.0238 | 0.0476 | 0.0714 | 0.119 | 0.1785 | 0.238 | 88.74 | 93.68 | 94.03 | 94.87 | 94.98 | 94.74 | 94.52 | 87.73 | 93.5 | 94.82 | 95.13 | 95.52 | 95.46 | 94.94 | 86.91 | 93.18 | 94.64 | 95.08 | 95.65 | 95.69 | 94.94
Mage Solar | POWERTEC Plus 245 / 6 PL US AC [240V] | 245W, 240 Vac Inverter | 0.24 | 240 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.22 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 88.7 | 93.7 | 94 | 94.9 | 95 | 94.7 | 94.5 | 87.7 | 93.5 | 94.8 | 95.1 | 95.5 | 95.5 | 94.9 | 86.9 | 93.2 | 94.6 | 95.1 | 95.7 | 95.7 | 94.9
Mage Solar USA | POWERTEC Plus 250 / 6 PL US AC [208V] | 240 W, 208 Vac Inverter | 0.24 | 208 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.22 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 88.7 | 93.7 | 94 | 94.9 | 95 | 94.7 | 94.5 | 87.7 | 93.5 | 94.8 | 95.1 | 95.5 | 95.5 | 94.9 | 86.9 | 93.2 | 94.6 | 95.1 | 95.7 | 95.7 | 94.9
Mage Solar USA | POWERTEC Plus 250 / 6 PL US AC [240V] | 240 W, 240 Vac Inverter | 0.24 | 240 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.22 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 88.7 | 93.7 | 94 | 94.9 | 95 | 94.7 | 94.5 | 87.7 | 93.5 | 94.8 | 95.1 | 95.5 | 95.5 | 94.9 | 86.9 | 93.2 | 94.6 | 95.1 | 95.7 | 95.7 | 94.9
Ming Shen Energy Technology | EnerBridge Emi_301RD [240V] | 300 W 240 Vac Utility Interactive Inverter | 0.29 | 240 | 96 | N | Y |  | 0.1 |  |  | 26 | 31 | 43 | 0.03 | 0.06 | 0.09 | 0.14 | 0.22 | 0.29 | 92.1 | 94.4 | 95 | 95.7 | 96.3 | 95.9 | 95.7 | 91.6 | 95.1 | 94.8 | 96.5 | 96.5 | 96.5 | 96.1 | 89.9 | 94.3 | 95.3 | 96.3 | 96.2 | 96.2 | 95.8
Mohr Power | MPS1100EVR [120V] | 1100 W, 120 Vac Utility Interactive Inverter | 1.1 | 120 | 90.5 | Y | N |  | 3.6 |  |  | 100 | 182 | 380 | 0.11 | 0.22 | 0.33 | 0.55 | 0.83 | 1.1 | 81.8 | 89 | 90.9 | 92.1 | 92.4 | 92.5 | 91.6 | 79.9 | 88 | 90.1 | 91.7 | 92.2 | 92.3 | 91.1 | 74.8 | 84.7 | 87.8 | 90 | 90.8 | 91.1 | 89.3
Mohr Power | MPS2000EVR [240V] | 2000 W, 240 Vac Utility Interactive Inverter | 2 | 240 | 92 | Y | N |  | 3.6 |  |  | 100 | 199 | 380 | 0.2 | 0.4 | 0.6 | 1 | 1.5 | 2 | 87.3 | 91.7 | 92.6 | 93.5 | 93.2 | 93 | 92.9 | 85.7 | 90.8 | 92.1 | 92.9 | 92.9 | 92.6 | 92.4 | 82.4 | 88.8 | 90.5 | 91.6 | 91.8 | 91.6 | 91.1
Mohr Power | MPS2500 [240V] | 2500 W, 240 Vac Utility Interactive Inverter | 2.5 | 240 | 94.5 | Y | N |  | 3.9 |  |  | 100 | 218 | 400 | 0.25 | 0.5 | 0.75 | 1.25 | 1.88 | 2.5 | 87.1 | 93.3 | 94.9 | 95.8 | 95.8 | 95.6 | 95.2 | 85.2 | 92.4 | 93.8 | 95.2 | 95.4 | 95.1 | 94.6 | 80.4 | 90 | 91.7 | 93.7 | 94.5 | 93.8 | 93.2
Mohr Power | MPS3000 [240V] | 3000 W, 240 Vac Utility Interactive Inverter | 3 | 240 | 93.5 | Y | N |  | 3.63 |  |  | 100 | 222.5 | 380 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 88.9 | 92.9 | 93.8 | 94.3 | 94.2 | 93.9 | 93.9 | 87.9 | 92.5 | 93.5 | 94.1 | 94 | 93.8 | 93.7 | 84.9 | 90.9 | 92.4 | 93.3 | 93.2 | 93 | 92.7
Mohr Power | MPS3500 [240V] | 3500 W, 240 Vac Utility Interactive Inverter | 3.5 | 240 | 95.5 | Y | N |  | 3.86 |  |  | 100 | 263 | 400 | 0.35 | 0.7 | 1.05 | 1.75 | 2.625 | 3.5 | 87.2 | 93.1 | 95.4 | 96.5 | 96.7 | 96.6 | 95.9 | 85.7 | 92.2 | 94.9 | 96.2 | 96.4 | 96.3 | 95.5 | 82.1 | 90.2 | 93.6 | 95.4 | 95.7 | 95.6 | 94.5
Mohr Power | MPS4600 [208V] | 4600 W, 208 Vac Utility Interactive Inverter | 4.6 | 208 | 95.5 | Y | N |  | 4 |  |  | 100 | 254 | 400 | 0.46 | 0.92 | 1.38 | 2.3 | 3.45 | 4.6 | 90.3 | 94.8 | 95.9 | 96.5 | 96.5 | 96.2 | 96.1 | 89.2 | 94.3 | 95.6 | 96.3 | 96.4 | 96.1 | 95.9 | 86.5 | 92.9 | 94.7 | 95.6 | 95.7 | 95.4 | 95
Mohr Power | MPS4800 [240V] | 4800 W, 240 Vac Utility Interactive Inverter | 4.8 | 240 | 96 | Y | N |  | 4.1 |  |  | 100 | 263 | 400 | 0.48 | 0.96 | 1.44 | 2.4 | 3.6 | 4.8 | 86.8 | 93.5 | 95.5 | 97 | 97.2 | 97.1 | 96.4 | 85.5 | 92.9 | 95 | 96.7 | 96.9 | 96.8 | 96 | 84.5 | 91.5 | 93.9 | 95.9 | 96.2 | 96.1 | 95.1
Mohr Power | MPS5200 [240V] | 5200 W, 240 Vac Utility Interactive Inverter | 5.2 | 240 | 96 | Y | N |  | 4 |  |  | 100 | 280 | 400 | 0.52 | 1.04 | 1.56 | 2.6 | 3.9 | 5.2 | 89.4 | 94.8 | 96 | 96.8 | 97 | 96.8 | 96.4 | 88.6 | 94.4 | 95.7 | 96.7 | 96.8 | 96.6 | 96.2 | 87.7 | 93.1 | 94.8 | 96.1 | 96.3 | 96.1 | 95.5
Motech Industries | PVMate 2900U [208V] | 2.7 kW, 208 Vac Utility Interactive Inverter | 2.7 | 208 | 95.5 | Y | N |  | 0.5 |  |  | 100 | 250 | 400 | 0.27 | 0.54 | 0.81 | 1.35 | 2.03 | 2.7 | 90.7 | 94.5 | 95.8 | 96.4 | 96.3 | 95.9 | 95.9 | 89.8 | 94.1 | 95.5 | 96.2 | 96.2 | 95.8 | 95.7 | 88.2 | 92.5 | 94.3 | 95.5 | 95.6 | 95.3 | 94.9
Motech Industries | PVMate 2900U-POS [208V] | 2.7 kW, 208 Vac Utility Interactive Inverter | 2.7 | 208 | 95.5 | Y | N |  | 0.5 |  |  | 100 | 250 | 400 | 0.27 | 0.54 | 0.81 | 1.35 | 2.03 | 2.7 | 90.7 | 94.5 | 95.8 | 96.4 | 96.3 | 95.9 | 95.9 | 89.8 | 94.1 | 95.5 | 96.2 | 96.2 | 95.8 | 95.7 | 88.2 | 92.5 | 94.3 | 95.5 | 95.6 | 95.3 | 94.9
Motech Industries | PVMate 3000U [208V] | 2.7 kW, 208 Vac Utility Interactive Inverter | 2.81 | 208 | 95.5 | Y | N |  | 0.35 |  |  | 100 | 275 | 400 | 0.28 | 0.56 | 0.84 | 1.41 | 2.11 | 2.81 | 89.4 | 94.4 | 95.5 | 96.2 | 96.2 | 95.9 | 95.8 | 88.7 | 93.8 | 95.2 | 95.9 | 96 | 95.7 | 95.5 | 86.5 | 92.1 | 94 | 95.1 | 95.3 | 95.2 | 94.6
Motech Industries | PVMate 3000U-PG [208V] | 2.7 kW, 208 Vac Utility Interactive Inverter | 2.81 | 208 | 95.5 | Y | N |  | 0.35 |  |  | 100 | 275 | 400 | 0.28 | 0.56 | 0.84 | 1.41 | 2.11 | 2.81 | 89.4 | 94.4 | 95.5 | 96.2 | 96.2 | 95.9 | 95.8 | 88.7 | 93.8 | 95.2 | 95.9 | 96 | 95.7 | 95.5 | 86.5 | 92.1 | 94 | 95.1 | 95.3 | 95.2 | 94.6
Motech Industries | PVMate 2900U [240V] | 2.9 kW, 240 Vac Utility Interactive Inverter | 2.9 | 240 | 96 | Y | N |  | 0.5 |  |  | 100 | 250 | 400 | 0.29 | 0.58 | 0.87 | 1.45 | 2.18 | 2.9 | 91.9 | 95.1 | 96.2 | 96.7 | 96.5 | 96.1 | 96.3 | 91.3 | 94.7 | 95.9 | 96.5 | 96.4 | 96 | 96.1 | 89.3 | 93.3 | 94.8 | 95.8 | 95.8 | 95.4 | 95.3
Motech Industries | PVMate 2900U-POS [240V] | 2.9 kW, 240 Vac Utility Interactive Inverter | 2.9 | 240 | 96 | Y | N |  | 0.5 |  |  | 100 | 250 | 400 | 0.29 | 0.58 | 0.87 | 1.45 | 2.18 | 2.9 | 91.9 | 95.1 | 96.2 | 96.7 | 96.5 | 96.1 | 96.3 | 91.3 | 94.7 | 95.9 | 96.5 | 96.4 | 96 | 96.1 | 89.3 | 93.3 | 94.8 | 95.8 | 95.8 | 95.4 | 95.3
Motech Industries | PVMate 3000U [240V] | 2.9 kW, 240 Vac Utility Interactive Inverter | 3.01 | 240 | 96 | Y | N |  | 0.47 |  |  | 100 | 275 | 400 | 0.3 | 0.6 | 0.9 | 1.51 | 2.26 | 3.01 | 90.6 | 95 | 96 | 96.6 | 96.6 | 96.2 | 96.2 | 89.8 | 94.4 | 95.6 | 96.4 | 96.4 | 96 | 95.9 | 87.7 | 92.9 | 94.5 | 95.6 | 95.8 | 95.5 | 95.1
Motech Industries | PVMate 3000U-PG [240V] | 2.9 kW, 240 Vac Utility Interactive Inverter | 3.01 | 240 | 96 | Y | N |  | 0.47 |  |  | 100 | 275 | 400 | 0.3 | 0.6 | 0.9 | 1.51 | 2.26 | 3.01 | 90.6 | 95 | 96 | 96.6 | 96.6 | 96.2 | 96.2 | 89.8 | 94.4 | 95.6 | 96.4 | 96.4 | 96 | 95.9 | 87.7 | 92.9 | 94.5 | 95.6 | 95.8 | 95.5 | 95.1
Motech Industries | PVMate 3840U [208V] | Same unit as PVMate 3900U with max power for use with 20-A breaker | 3.32 | 208 | 95.5 | Y | N |  | 0.5 |  |  | 100 | 250 | 400 | 0.34 | 0.68 | 1.02 | 1.7 | 2.55 | 3.4 | 92.4 | 95.4 | 96.3 | 96.5 | 96.1 | 95.3 | 96 | 91.8 | 95.1 | 96 | 96.3 | 96 | 95.2 | 95.8 | 90.1 | 93.8 | 95.1 | 95.7 | 95.5 | 94.9 | 95.2
Motech Industries | PVMate 3840U-POS [208V] | Same unit as PVMate 3900U with max power for use with 20-A breaker | 3.32 | 208 | 95.5 | Y | N |  | 0.5 |  |  | 100 | 250 | 400 | 0.34 | 0.68 | 1.02 | 1.7 | 2.55 | 3.4 | 92.4 | 95.4 | 96.3 | 96.5 | 96.1 | 95.3 | 96 | 91.8 | 95.1 | 96 | 96.3 | 96 | 95.2 | 95.8 | 90.1 | 93.8 | 95.1 | 95.7 | 95.5 | 94.9 | 95.2
Motech Industries | PVMate 3900U [208V] | 3.4 kW 208 Vac Utility Interactive Inverter | 3.4 | 208 | 95.5 | Y | N |  | 0.5 |  |  | 100 | 250 | 400 | 0.34 | 0.68 | 1.02 | 1.7 | 2.55 | 3.4 | 92.4 | 95.4 | 96.3 | 96.5 | 96.1 | 95.3 | 96 | 91.8 | 95.1 | 96 | 96.3 | 96 | 95.2 | 95.8 | 90.1 | 93.8 | 95.1 | 95.7 | 95.5 | 94.9 | 95.2
Motech Industries | PVMate 3900U-POS [208V] | 3.4 kW 208 Vac Utility Interactive Inverter | 3.4 | 208 | 95.5 | Y | N |  | 0.5 |  |  | 100 | 250 | 400 | 0.34 | 0.68 | 1.02 | 1.7 | 2.55 | 3.4 | 92.4 | 95.4 | 96.3 | 96.5 | 96.1 | 95.3 | 96 | 91.8 | 95.1 | 96 | 96.3 | 96 | 95.2 | 95.8 | 90.1 | 93.8 | 95.1 | 95.7 | 95.5 | 94.9 | 95.2
Motech Industries | PVMate 4000U [208V] | 3.4 kW 208 Vac Utility Interactive Inverter | 3.51 | 208 | 95.5 | Y | N |  | 0.35 |  |  | 100 | 275 | 400 | 0.35 | 0.7 | 1.05 | 1.76 | 2.63 | 3.51 | 91.3 | 95.1 | 96 | 96.3 | 96.1 | 95.4 | 95.9 | 90.4 | 94.7 | 95.7 | 96 | 95.9 | 95.3 | 95.6 | 88.4 | 93.3 | 94.7 | 95.3 | 95.3 | 94.7 | 94.8
Motech Industries | PVMate 4000U-PG [208V] | 3.4 kW 208 Vac Utility Interactive Inverter | 3.51 | 208 | 95.5 | Y | N |  | 0.35 |  |  | 100 | 275 | 400 | 0.35 | 0.7 | 1.05 | 1.76 | 2.63 | 3.51 | 91.3 | 95.1 | 96 | 96.3 | 96.1 | 95.4 | 95.9 | 90.4 | 94.7 | 95.7 | 96 | 95.9 | 95.3 | 95.6 | 88.4 | 93.3 | 94.7 | 95.3 | 95.3 | 94.7 | 94.8
Motech Industries | PVMate 3840U [240V] | Same unit as PVMate 3900U with max power for use with 20-A breaker | 3.84 | 240 | 96 | Y | N |  | 0.5 |  |  | 100 | 250 | 400 | 0.39 | 0.78 | 1.17 | 1.95 | 2.93 | 3.9 | 93 | 95.7 | 96.5 | 96.7 | 96.1 | 95.5 | 96.1 | 92.9 | 95.6 | 96.4 | 96.5 | 96 | 95.4 | 96 | 90 | 93.7 | 95.2 | 95.7 | 95.5 | 95 | 95.2
Motech Industries | PVMate 3840U-POS [240V] | Same unit as PVMate 3900U with max power for use with 20-A breaker | 3.84 | 240 | 96 | Y | N |  | 0.5 |  |  | 100 | 250 | 400 | 0.39 | 0.78 | 1.17 | 1.95 | 2.93 | 3.9 | 93 | 95.7 | 96.5 | 96.7 | 96.1 | 95.5 | 96.1 | 92.9 | 95.6 | 96.4 | 96.5 | 96 | 95.4 | 96 | 90 | 93.7 | 95.2 | 95.7 | 95.5 | 95 | 95.2
Motech Industries | PVMate 3900U [240V] | 3.9 kW, 240 Vac Utility Interactive Inverter | 3.9 | 240 | 96 | Y | N |  | 0.5 |  |  | 100 | 250 | 400 | 0.39 | 0.78 | 1.17 | 1.95 | 2.93 | 3.9 | 93 | 95.7 | 96.5 | 96.7 | 96.1 | 95.5 | 96.1 | 92.9 | 95.6 | 96.4 | 96.5 | 96 | 95.4 | 96 | 90 | 93.7 | 95.2 | 95.7 | 95.5 | 95 | 95.2
Motech Industries | PVMate 3900U-POS [240V] | 3.9 kW, 240 Vac Utility Interactive Inverter | 3.9 | 240 | 96 | Y | N |  | 0.5 |  |  | 100 | 250 | 400 | 0.39 | 0.78 | 1.17 | 1.95 | 2.93 | 3.9 | 93 | 95.7 | 96.5 | 96.7 | 96.1 | 95.5 | 96.1 | 92.9 | 95.6 | 96.4 | 96.5 | 96 | 95.4 | 96 | 90 | 93.7 | 95.2 | 95.7 | 95.5 | 95 | 95.2
Motech Industries | PVMate 4000U [240V] | 3.9 kW, 240 Vac Utility Interactive Inverter | 4.02 | 240 | 96 | Y | N |  | 0.47 |  |  | 100 | 275 | 400 | 0.4 | 0.8 | 1.21 | 2.01 | 3.02 | 4.02 | 92.6 | 95.7 | 96.4 | 96.5 | 96.3 | 95.5 | 96.1 | 91.8 | 95.3 | 96.1 | 96.3 | 96.1 | 95.4 | 95.9 | 90 | 94.1 | 95.2 | 95.7 | 95.5 | 94.9 | 95.2
Motech Industries | PVMate 4000U-PG [240V] | 3.9 kW, 240 Vac Utility Interactive Inverter | 4.02 | 240 | 96 | Y | N |  | 0.47 |  |  | 100 | 275 | 400 | 0.4 | 0.8 | 1.21 | 2.01 | 3.02 | 4.02 | 92.6 | 95.7 | 96.4 | 96.5 | 96.3 | 95.5 | 96.1 | 91.8 | 95.3 | 96.1 | 96.3 | 96.1 | 95.4 | 95.9 | 90 | 94.1 | 95.2 | 95.7 | 95.5 | 94.9 | 95.2
Motech Industries | PVMate 4900U [208V] | 4.3 kW, 208 Vac Utility Interactive Inverter | 4.3 | 208 | 96 | Y | N |  | 0.5 |  |  | 100 | 275 | 400 | 0.43 | 0.86 | 1.29 | 2.15 | 3.23 | 4.3 | 93.3 | 95.5 | 96.2 | 96.4 | 96.1 | 95.6 | 96 | 92.7 | 95.2 | 95.9 | 96.2 | 96 | 95.5 | 95.8 | 91.4 | 94.2 | 95.2 | 95.8 | 95.7 | 95.2 | 95.4
Motech Industries | PVMate 4900U-POS [208V] | 4.3 kW, 208 Vac Utility Interactive Inverter | 4.3 | 208 | 96 | Y | N |  | 0.5 |  |  | 100 | 275 | 400 | 0.43 | 0.86 | 1.29 | 2.15 | 3.23 | 4.3 | 93.3 | 95.5 | 96.2 | 96.4 | 96.1 | 95.6 | 96 | 92.7 | 95.2 | 95.9 | 96.2 | 96 | 95.5 | 95.8 | 91.4 | 94.2 | 95.2 | 95.8 | 95.7 | 95.2 | 95.4
Motech Industries | PVMate 5000U [208V] | 4.3 kW, 208 Vac Utility Interactive Inverter | 4.4 | 208 | 96 | Y | N |  | 0.47 |  |  | 100 | 275 | 400 | 0.44 | 0.88 | 1.32 | 2.2 | 3.3 | 4.4 | 92.9 | 95.8 | 96.5 | 96.8 | 96.6 | 95.9 | 96.4 | 92.2 | 95.3 | 96.2 | 96.4 | 96.2 | 95.5 | 96 | 90.1 | 93.9 | 95 | 95.7 | 95.6 | 95.2 | 95.2
Motech Industries | PVMate 5000U-PG [208V] | 4.3 kW, 208 Vac Utility Interactive Inverter | 4.4 | 208 | 96 | Y | N |  | 0.47 |  |  | 100 | 275 | 400 | 0.44 | 0.88 | 1.32 | 2.2 | 3.3 | 4.4 | 92.9 | 95.8 | 96.5 | 96.8 | 96.6 | 95.9 | 96.4 | 92.2 | 95.3 | 96.2 | 96.4 | 96.2 | 95.5 | 96 | 90.1 | 93.9 | 95 | 95.7 | 95.6 | 95.2 | 95.2
Motech Industries | PVMate 5300U [208V] | 4.6 kW, 208 Vac Utility Interactive Inverter | 4.6 | 208 | 95.5 | Y | N |  | 0.5 |  |  | 100 | 275 | 400 | 0.46 | 0.92 | 1.38 | 2.3 | 3.45 | 4.6 | 93.5 | 95.6 | 96.2 | 96.1 | 95.9 | 95.3 | 95.9 | 93 | 95.3 | 96 | 95.9 | 95.9 | 95.2 | 95.7 | 91.7 | 94.4 | 95.2 | 95.7 | 95.5 | 95 | 95.3
Motech Industries | PVMate 5300U-POS [208V] | 4.6 kW, 208 Vac Utility Interactive Inverter | 4.6 | 208 | 95.5 | Y | N |  | 0.5 |  |  | 100 | 275 | 400 | 0.46 | 0.92 | 1.38 | 2.3 | 3.45 | 4.6 | 93.5 | 95.6 | 96.2 | 96.1 | 95.9 | 95.3 | 95.9 | 93 | 95.3 | 96 | 95.9 | 95.9 | 95.2 | 95.7 | 91.7 | 94.4 | 95.2 | 95.7 | 95.5 | 95 | 95.3
Motech Industries | PVMate 4900U [240V] | 4.9 kW, 240 Vac Utility Interactive Inverter | 4.9 | 240 | 96 | Y | N |  | 0.5 |  |  | 100 | 275 | 400 | 0.49 | 0.98 | 1.47 | 2.45 | 3.68 | 4.9 | 93.9 | 96 | 96.5 | 96.6 | 96.2 | 95.6 | 96.2 | 93.4 | 95.7 | 96.3 | 96.5 | 96 | 95.4 | 96 | 92.1 | 94.8 | 95.7 | 96 | 95.8 | 95.2 | 95.6
Motech Industries | PVMate 4900U-POS [240V] | 4.9 kW, 240 Vac Utility Interactive Inverter | 4.9 | 240 | 96 | Y | N |  | 0.5 |  |  | 100 | 275 | 400 | 0.49 | 0.98 | 1.47 | 2.45 | 3.68 | 4.9 | 93.9 | 96 | 96.5 | 96.6 | 96.2 | 95.6 | 96.2 | 93.4 | 95.7 | 96.3 | 96.5 | 96 | 95.4 | 96 | 92.1 | 94.8 | 95.7 | 96 | 95.8 | 95.2 | 95.6
Motech Industries | PVMate 5000U [240V] | 4.9 kW, 240 Vac Utility Interactive Inverter | 5.01 | 240 | 96 | Y | N |  | 0.47 |  |  | 100 | 275 | 400 | 0.5 | 1 | 1.5 | 2.51 | 3.76 | 5.01 | 93.9 | 96.1 | 96.6 | 96.7 | 96.4 | 95.7 | 96.3 | 92.7 | 95.8 | 96.4 | 96.5 | 96.2 | 95.6 | 96.1 | 91.2 | 94.7 | 95.7 | 96.1 | 95.9 | 95.4 | 95.7
Motech Industries | PVMate 5000U-PG [240V] | 4.9 kW, 240 Vac Utility Interactive Inverter | 5.01 | 240 | 96 | Y | N |  | 0.47 |  |  | 100 | 275 | 400 | 0.5 | 1 | 1.5 | 2.51 | 3.76 | 5.01 | 93.9 | 96.1 | 96.6 | 96.7 | 96.4 | 95.7 | 96.3 | 92.7 | 95.8 | 96.4 | 96.5 | 96.2 | 95.6 | 96.1 | 91.2 | 94.7 | 95.7 | 96.1 | 95.9 | 95.4 | 95.7
Motech Industries | PVMate 5300U [240V] | 5.3 kW, 240 Vac Utility Interactive Inverter | 5.3 | 240 | 96 | Y | N |  | 0.5 |  |  | 100 | 275 | 400 | 0.53 | 1.06 | 1.59 | 2.65 | 3.98 | 5.3 | 94.3 | 96.1 | 96.3 | 96.4 | 96 | 95.2 | 96 | 93.8 | 95.9 | 96.1 | 96.3 | 95.8 | 95.2 | 95.8 | 92.5 | 95 | 95.7 | 96 | 95.5 | 94.9 | 95.4
Motech Industries | PVMate 5300U-POS [240V] | 5.3 kW, 240 Vac Utility Interactive Inverter | 5.3 | 240 | 96 | Y | N |  | 0.5 |  |  | 100 | 275 | 400 | 0.53 | 1.06 | 1.59 | 2.65 | 3.98 | 5.3 | 94.3 | 96.1 | 96.3 | 96.4 | 96 | 95.2 | 96 | 93.8 | 95.9 | 96.1 | 96.3 | 95.8 | 95.2 | 95.8 | 92.5 | 95 | 95.7 | 96 | 95.5 | 94.9 | 95.4
Motech Industries | PVMate 6500U [208V] | 6.43 kW, 208 Vac Utility Interactive Inverter | 6.43 | 208 | 95.5 | Y | N |  | 0.5 |  |  | 100 | 275 | 400 | 0.643 | 1.286 | 1.929 | 3.215 | 4.823 | 6.43 | 93.3 | 95.6 | 96 | 96 | 95.6 | 94.8 | 95.6 | 92.9 | 95.4 | 95.9 | 95.9 | 95.5 | 94.8 | 95.5 | 91.6 | 94.8 | 95.4 | 95.6 | 95.2 | 94.6 | 95.1
Motech Industries | PVMate 6500U [240V] | 6.45 kW, 240 Vac Utility Interactive Inverter | 6.45 | 240 | 96 | Y | N |  | 0.65 |  |  | 100 | 275 | 400 | 0.645 | 1.29 | 1.935 | 3.225 | 4.838 | 6.45 | 93.5 | 95.9 | 96.3 | 96.3 | 96 | 95.4 | 96 | 93.1 | 95.7 | 96.2 | 96.3 | 96 | 95.3 | 95.9 | 91.8 | 95 | 95.6 | 95.9 | 95.7 | 95.2 | 95.5
Motech Industries | PVMate 6500U [277V] | 6.45 kW, 277 Vac Utility Interactive Inverter | 6.45 | 277 | 96 | Y | N |  | 0.9 |  |  | 100 | 275 | 400 | 0.645 | 1.29 | 1.935 | 3.225 | 4.838 | 6.45 | 93.8 | 96.1 | 96.5 | 96.7 | 96.4 | 95.8 | 96.3 | 93.4 | 95.9 | 96.4 | 96.5 | 96.3 | 95.8 | 96.2 | 92 | 95.3 | 95.9 | 96.2 | 96 | 95.6 | 95.8
Motech Industries | PVMate 7500U [208V] | 7.43 kW, 208 Vac Utility Interactive Inverter | 7.43 | 208 | 95.5 | Y | N |  | 0.52 |  |  | 100 | 275 | 400 | 0.743 | 1.486 | 2.229 | 3.715 | 5.573 | 7.43 | 94.1 | 96 | 96.2 | 96.1 | 95.4 | 94.6 | 95.6 | 93.7 | 95.7 | 96 | 96 | 95.3 | 94.5 | 95.5 | 92.5 | 95.1 | 95.6 | 95.6 | 95.1 | 94.3 | 95.1
Motech Industries | PVMate 7500U [240V] | 7.45 kW, 240 Vac Utility Interactive Inverter | 7.45 | 240 | 96 | Y | N |  | 0.68 |  |  | 100 | 275 | 400 | 0.745 | 1.49 | 2.235 | 3.725 | 5.588 | 7.45 | 94.3 | 96.2 | 96.5 | 96.5 | 95.9 | 95.2 | 96 | 93.9 | 96 | 96.3 | 96.3 | 95.8 | 95.1 | 95.9 | 92.7 | 95.4 | 95.9 | 96 | 95.5 | 94.9 | 95.5
Motech Industries | PVMate 7500U [277V] | 7.46 kW, 277 Vac Utility Interactive Inverter | 7.46 | 277 | 96 | Y | N |  | 0.9 |  |  | 100 | 275 | 400 | 0.746 | 1.492 | 2.238 | 3.73 | 5.595 | 7.46 | 94.4 | 96.4 | 96.7 | 96.6 | 96.2 | 95.5 | 96.3 | 94 | 96.1 | 96.5 | 96.6 | 96.2 | 95.5 | 96.2 | 92.9 | 95.5 | 96.1 | 96.2 | 95.9 | 95.3 | 95.8
NeoVolta Inc. | NV7600 [208V] | 7680W, 208 Vac, 1-phase hybrid Utility Interactive Inverter that works with PV and energy storage. | 7.4473 | 208 | 96.5 | N | N |  |  |  |  | 240 | 370 | 425 | 0.74473 | 1.4895 | 2.2342 | 3.7237 | 5.5855 | 7.4473 | 91.4863 | 94.7602 | 95.3527 | 97.2963 | 97.1851 | 96.8599 | 96.6231 | 91.7 | 94.9639 | 95.4957 | 97.4288 | 97.2316 | 96.9297 | 96.715 | 91.9073 | 94.929 | 95.3698 | 97.3187 | 96.9256 | 97.0631 | 96.5278 | 2019-03-01
NeoVolta Inc. | NV7600 [240V] | 7680W, 240 Vac, 1-phase hybrid Utility Interactive Inverter that works with PV and energy storage. | 7.657 | 240 | 96.5 | N | N |  |  |  |  | 240 | 370 | 425 | 0.76571 | 1.5314 | 2.2971 | 3.8286 | 5.7428 | 7.6571 | 91.8196 | 94.911 | 95.5205 | 97.0796 | 96.988 | 97.1305 | 96.5277 | 91.6709 | 95.0008 | 95.7077 | 97.5465 | 97.4459 | 97.0835 | 96.8871 | 91.5513 | 95.0717 | 95.8584 | 97.6006 | 97.274 | 97.0868 | 96.8243 | 2019-03-01
Nextronex Energy Systems | Ray-Max 150 | 150 kW, Utility Interactive Inverter with medium voltage transformer | 150 |  | 96 | N | N |  | 507.8 |  |  | 600 | 620 | 730 | 15 | 30 | 45 | 75 | 112.5 | 150 | 93.1 | 94.2 | 95.6 | 96.7 | 96.7 | 96.7 | 96.3 | 93.9 | 94.4 | 94.8 | 96.5 | 96.6 | 96.7 | 96.1 | 87.5 | 92 | 93.8 | 95.5 | 96.2 | 96.1 | 95.2
Nidec ASI | PV800A60UNO04LNU0NN [600V] | 800 kW, 600 Vac, 1500 Vdc Utility Interactive Inverter | 802.9 | 600 | 98 | N | N |  | 258.4 |  |  | 900 | 1100 | 1400 | 80.29 | 160.58 | 240.87 | 401.45 | 602.175 | 802.9 | 97.343 | 98.2387 | 98.4327 | 98.4922 | 98.3802 | 98.2527 | 98.3551 | 96.8819 | 98.1219 | 98.3102 | 98.4329 | 98.3239 | 98.2114 | 98.2717 | 95.8048 | 97.6221 | 98.171 | 98.217 | 98.238 | 98.0092 | 98.086 | 2018-12-17
Ningbo Ginlong Technologies Co.,Ltd. | GCI-1K-2G-H-US [208V] | 1 kW, 208 Vac Utility Interactive Inverter | 0.99 | 208 | 96 | Y | N |  | 0.25 |  |  | 100 | 280 | 400 | 0.1 | 0.2 | 0.3 | 0.5 | 0.74 | 0.99 | 91.8 | 94.1 | 95.2 | 96 | 95.8 | 95.5 | 95.5 | 92.2 | 94.4 | 95.4 | 96.1 | 96 | 95.8 | 95.7 | 93.3 | 94.9 | 95.6 | 96.4 | 96.3 | 96.1 | 96.1 |  | 2018-02-15
Ningbo Ginlong Technologies Co.,Ltd. | GCI-1K-2G-H-US [240V] | 1 kW, 240 Vac Utility Interactive Inverter | 0.99 | 240 | 96 | Y | N |  | 0.25 |  |  | 100 | 280 | 400 | 0.1 | 0.2 | 0.3 | 0.5 | 0.74 | 0.99 | 91.8 | 94 | 95 | 96 | 95.6 | 95.4 | 95.4 | 93.3 | 94.8 | 95.5 | 96.3 | 96 | 95.4 | 95.8 | 93.5 | 95 | 95.8 | 96.8 | 96.7 | 96 | 96.3 |  | 2018-02-15
Ningbo Ginlong Technologies Co.,Ltd. | GCI-1K-2G-W-US [208V] | 1 kW, 208 Vac Utility Interactive Inverter | 0.99 | 208 | 96 | Y | N |  | 0.25 |  |  | 100 | 280 | 400 | 0.1 | 0.2 | 0.3 | 0.5 | 0.74 | 0.99 | 91.8 | 94.1 | 95.2 | 96 | 95.8 | 95.5 | 95.5 | 92.2 | 94.4 | 95.4 | 96.1 | 96 | 95.8 | 95.7 | 93.3 | 94.9 | 95.6 | 96.4 | 96.3 | 96.1 | 96.1 |  | 2018-02-15
Ningbo Ginlong Technologies Co.,Ltd. | GCI-1K-2G-W-US [240V] | 1 kW, 240 Vac Utility Interactive Inverter | 0.99 | 240 | 96 | Y | N |  | 0.25 |  |  | 100 | 280 | 400 | 0.1 | 0.2 | 0.3 | 0.5 | 0.74 | 0.99 | 91.8 | 94 | 95 | 96 | 95.6 | 95.4 | 95.4 | 93.3 | 94.8 | 95.5 | 96.3 | 96 | 95.4 | 95.8 | 93.5 | 95 | 95.8 | 96.8 | 96.7 | 96 | 96.3 |  | 2018-02-15
Ningbo Ginlong Technologies Co.,Ltd. | Solis-1K-2G-US [208V] | 1 kW, 208 Vac Utility Interactive Inverter | 0.99 | 208 | 96 | Y | N |  | 0.25 |  |  | 100 | 280 | 400 | 0.1 | 0.2 | 0.3 | 0.5 | 0.74 | 0.99 | 91.8 | 94.1 | 95.2 | 96 | 95.8 | 95.5 | 95.5 | 92.2 | 94.4 | 95.4 | 96.1 | 96 | 95.8 | 95.7 | 93.3 | 94.9 | 95.6 | 96.4 | 96.3 | 96.1 | 96.1 |  | 2018-02-15
Ningbo Ginlong Technologies Co.,Ltd. | Solis-1K-2G-US [240V] | 1 kW, 240 Vac Utility Interactive Inverter | 0.99 | 240 | 96 | Y | N |  | 0.25 |  |  | 100 | 280 | 400 | 0.1 | 0.2 | 0.3 | 0.5 | 0.74 | 0.99 | 91.8 | 94 | 95 | 96 | 95.6 | 95.4 | 95.4 | 93.3 | 94.8 | 95.5 | 96.3 | 96 | 95.4 | 95.8 | 93.5 | 95 | 95.8 | 96.8 | 96.7 | 96 | 96.3 |  | 2018-02-15
Ningbo Ginlong Technologies Co.,Ltd. | GCI-1.5K-2G-H-US [208V] | 1.5 kW, 208 Vac Utility Interactive Inverter | 1.49 | 208 | 96 | Y | N |  | 0.25 |  |  | 100 | 280 | 400 | 0.15 | 0.3 | 0.45 | 0.75 | 1.12 | 1.49 | 92 | 94.1 | 95.4 | 96.3 | 96.1 | 95.7 | 95.7 | 93.2 | 94.8 | 95.8 | 96.6 | 96.2 | 96 | 96.1 | 93.3 | 95.1 | 95.9 | 96.8 | 96.4 | 96.1 | 96.2 |  | 2018-02-15
Ningbo Ginlong Technologies Co.,Ltd. | GCI-1.5K-2G-H-US [240V] | 1.5 kW, 240 Vac Utility Interactive Inverter | 1.49 | 240 | 96 | Y | N |  | 0.25 |  |  | 100 | 280 | 400 | 0.15 | 0.3 | 0.45 | 0.75 | 1.12 | 1.49 | 91.8 | 93.9 | 95.2 | 96.1 | 96 | 95.2 | 95.6 | 93.3 | 95 | 95.9 | 96.6 | 96.3 | 96.1 | 96.1 | 93.6 | 95.3 | 96.1 | 96.8 | 96.4 | 96 | 96.3 |  | 2018-02-15
Ningbo Ginlong Technologies Co.,Ltd. | GCI-1.5K-2G-W-US [208V] | 1.5 kW, 208 Vac Utility Interactive Inverter | 1.49 | 208 | 96 | Y | N |  | 0.25 |  |  | 100 | 280 | 400 | 0.15 | 0.3 | 0.45 | 0.75 | 1.12 | 1.49 | 92 | 94.1 | 95.4 | 96.3 | 96.1 | 95.7 | 95.7 | 93.2 | 94.8 | 95.8 | 96.6 | 96.2 | 96 | 96.1 | 93.3 | 95.1 | 95.9 | 96.8 | 96.4 | 96.1 | 96.2 |  | 2018-02-15
Ningbo Ginlong Technologies Co.,Ltd. | GCI-1.5K-2G-W-US [240V] | 1.5 kW, 240 Vac Utility Interactive Inverter | 1.49 | 240 | 96 | Y | N |  | 0.25 |  |  | 100 | 280 | 400 | 0.15 | 0.3 | 0.45 | 0.75 | 1.12 | 1.49 | 91.8 | 93.9 | 95.2 | 96.1 | 96 | 95.2 | 95.6 | 93.3 | 95 | 95.9 | 96.6 | 96.3 | 96.1 | 96.1 | 93.6 | 95.3 | 96.1 | 96.8 | 96.4 | 96 | 96.3 |  | 2018-02-15
Ningbo Ginlong Technologies Co.,Ltd. | Solis-1.5K-2G-US [208V] | 1.5 kW, 208 Vac Utility Interactive Inverter | 1.49 | 208 | 96 | Y | N |  | 0.25 |  |  | 100 | 280 | 400 | 0.15 | 0.3 | 0.45 | 0.75 | 1.12 | 1.49 | 92 | 94.1 | 95.4 | 96.3 | 96.1 | 95.7 | 95.7 | 93.2 | 94.8 | 95.8 | 96.6 | 96.2 | 96 | 96.1 | 93.3 | 95.1 | 95.9 | 96.8 | 96.4 | 96.1 | 96.2 |  | 2018-02-15
Ningbo Ginlong Technologies Co.,Ltd. | Solis-1.5K-2G-US [240V] | 1.5 kW, 240 Vac Utility Interactive Inverter | 1.49 | 240 | 96 | Y | N |  | 0.25 |  |  | 100 | 280 | 400 | 0.15 | 0.3 | 0.45 | 0.75 | 1.12 | 1.49 | 91.8 | 93.9 | 95.2 | 96.1 | 96 | 95.2 | 95.6 | 93.3 | 95 | 95.9 | 96.6 | 96.3 | 96.1 | 96.1 | 93.6 | 95.3 | 96.1 | 96.8 | 96.4 | 96 | 96.3 |  | 2018-02-15
Ningbo Ginlong Technologies Co.,Ltd. | GCI-2K-2G-H-US [208V] | 2 kW, 208 Vac Utility Interactive Inverter | 1.99 | 208 | 96.5 | Y | N |  | 0.25 |  |  | 100 | 280 | 400 | 0.2 | 0.4 | 0.6 | 1 | 1.49 | 1.99 | 92.1 | 94.1 | 95.2 | 96.5 | 96.6 | 96 | 96.1 | 93.2 | 94.8 | 95.8 | 96.9 | 96.7 | 96.4 | 96.4 | 93.4 | 95.1 | 96.3 | 97.1 | 96.8 | 96.6 | 96.6 |  | 2018-02-15
Ningbo Ginlong Technologies Co.,Ltd. | GCI-2K-2G-H-US [240V] | 2 kW, 240 Vac Utility Interactive Inverter | 1.99 | 240 | 96.5 | Y | N |  | 0.25 |  |  | 100 | 280 | 400 | 0.2 | 0.4 | 0.6 | 1 | 1.49 | 1.99 | 92.3 | 94 | 95.1 | 96.5 | 96.2 | 96 | 95.8 | 93.1 | 94.6 | 95.7 | 97.1 | 96.8 | 96.5 | 96.5 | 93.4 | 94.8 | 95.8 | 97.2 | 97.2 | 96.9 | 96.8 |  | 2018-02-15
Ningbo Ginlong Technologies Co.,Ltd. | GCI-2K-2G-W-US [208V] | 2 kW, 208 Vac Utility Interactive Inverter | 1.99 | 208 | 96.5 | Y | N |  | 0.25 |  |  | 100 | 280 | 400 | 0.2 | 0.4 | 0.6 | 1 | 1.49 | 1.99 | 92.1 | 94.1 | 95.2 | 96.5 | 96.6 | 96 | 96.1 | 93.2 | 94.8 | 95.8 | 96.9 | 96.7 | 96.4 | 96.4 | 93.4 | 95.1 | 96.3 | 97.1 | 96.8 | 96.6 | 96.6 |  | 2018-02-15
Ningbo Ginlong Technologies Co.,Ltd. | GCI-2K-2G-W-US [240V] | 2 kW, 240 Vac Utility Interactive Inverter | 1.99 | 240 | 96.5 | Y | N |  | 0.25 |  |  | 100 | 280 | 400 | 0.2 | 0.4 | 0.6 | 1 | 1.49 | 1.99 | 92.3 | 94 | 95.1 | 96.5 | 96.2 | 96 | 95.8 | 93.1 | 94.6 | 95.7 | 97.1 | 96.8 | 96.5 | 96.5 | 93.4 | 94.8 | 95.8 | 97.2 | 97.2 | 96.9 | 96.8 |  | 2018-02-15
Ningbo Ginlong Technologies Co.,Ltd. | Solis-2K-2G-US [208V] | 2 kW, 208 Vac Utility Interactive Inverter | 1.99 | 208 | 96.5 | Y | N |  | 0.25 |  |  | 100 | 280 | 400 | 0.2 | 0.4 | 0.6 | 1 | 1.49 | 1.99 | 92.1 | 94.1 | 95.2 | 96.5 | 96.6 | 96 | 96.1 | 93.2 | 94.8 | 95.8 | 96.9 | 96.7 | 96.4 | 96.4 | 93.4 | 95.1 | 96.3 | 97.1 | 96.8 | 96.6 | 96.6 |  | 2018-02-15
Ningbo Ginlong Technologies Co.,Ltd. | Solis-2K-2G-US [240V] | 2 kW, 240 Vac Utility Interactive Inverter | 1.99 | 240 | 96.5 | Y | N |  | 0.25 |  |  | 100 | 280 | 400 | 0.2 | 0.4 | 0.6 | 1 | 1.49 | 1.99 | 92.3 | 94 | 95.1 | 96.5 | 96.2 | 96 | 95.8 | 93.1 | 94.6 | 95.7 | 97.1 | 96.8 | 96.5 | 96.5 | 93.4 | 94.8 | 95.8 | 97.2 | 97.2 | 96.9 | 96.8 |  | 2018-02-15
Ningbo Ginlong Technologies Co.,Ltd. | GCI-2K [240V] | 2 kW, 240 Vac Utility Interactive Inverter | 2 | 240 | 94 | Y | N |  | 6.53 |  |  | 100 | 520 | 650 | 0.2 | 0.4 | 0.6 | 1 | 1.5 | 2 | 88.38 | 92.36 | 93.22 | 94.04 | 94.22 | 93.94 | 93.72 | 89.12 | 92.88 | 93.65 | 94.43 | 94.45 | 94.41 | 94.06 | 89.37 | 93.29 | 94.09 | 94.88 | 94.99 | 94.76 | 94.53 |  | 2018-02-15
Ningbo Ginlong Technologies Co.,Ltd. | GCI-2.5K-2G-H-US [208V] | 2.5 kW, 208 Vac Utility Interactive Inverter | 2.49 | 208 | 96.5 | Y | N |  | 0.25 |  |  | 100 | 360 | 480 | 0.25 | 0.5 | 0.75 | 1.25 | 1.87 | 2.49 | 92.2 | 94.4 | 95.6 | 97 | 96.5 | 96.2 | 96.2 | 93.1 | 95.2 | 96.4 | 97.5 | 97.3 | 96.9 | 96.9 | 93 | 95.1 | 96.3 | 97.3 | 96.9 | 96.6 | 96.6 |  | 2018-02-15
Ningbo Ginlong Technologies Co.,Ltd. | GCI-2.5K-2G-H-US [240V] | 2.5 kW, 240 Vac Utility Interactive Inverter | 2.49 | 240 | 96.5 | Y | N |  | 0.25 |  |  | 100 | 360 | 480 | 0.25 | 0.5 | 0.75 | 1.25 | 1.87 | 2.49 | 92.3 | 94.6 | 95.7 | 96.9 | 96.7 | 96.4 | 96.3 | 93.4 | 95.5 | 96.6 | 97.6 | 97.4 | 97 | 97 | 93.1 | 95.1 | 96.3 | 97.4 | 96.9 | 96.7 | 96.7 |  | 2018-02-15
Ningbo Ginlong Technologies Co.,Ltd. | GCI-2.5K-2G-W-US [208V] | 2.5 kW, 208 Vac Utility Interactive Inverter | 2.49 | 208 | 96.5 | Y | N |  | 0.25 |  |  | 100 | 360 | 480 | 0.25 | 0.5 | 0.75 | 1.25 | 1.87 | 2.49 | 92.2 | 94.4 | 95.6 | 97 | 96.5 | 96.2 | 96.2 | 93.1 | 95.2 | 96.4 | 97.5 | 97.3 | 96.9 | 96.9 | 93 | 95.1 | 96.3 | 97.3 | 96.9 | 96.6 | 96.6 |  | 2018-02-15
Ningbo Ginlong Technologies Co.,Ltd. | GCI-2.5K-2G-W-US [240V] | 2.5 kW, 240 Vac Utility Interactive Inverter | 2.49 | 240 | 96.5 | Y | N |  | 0.25 |  |  | 100 | 360 | 480 | 0.25 | 0.5 | 0.75 | 1.25 | 1.87 | 2.49 | 92.3 | 94.6 | 95.7 | 96.9 | 96.7 | 96.4 | 96.3 | 93.4 | 95.5 | 96.6 | 97.6 | 97.4 | 97 | 97 | 93.1 | 95.1 | 96.3 | 97.4 | 96.9 | 96.7 | 96.7 |  | 2018-02-15
Ningbo Ginlong Technologies Co.,Ltd. | Solis-2.5K-2G-US [208V] | 2.5 kW, 208 Vac Utility Interactive Inverter | 2.49 | 208 | 96.5 | Y | N |  | 0.25 |  |  | 100 | 360 | 480 | 0.25 | 0.5 | 0.75 | 1.25 | 1.87 | 2.49 | 92.2 | 94.4 | 95.6 | 97 | 96.5 | 96.2 | 96.2 | 93.1 | 95.2 | 96.4 | 97.5 | 97.3 | 96.9 | 96.9 | 93 | 95.1 | 96.3 | 97.3 | 96.9 | 96.6 | 96.6 |  | 2018-02-15
Ningbo Ginlong Technologies Co.,Ltd. | Solis-2.5K-2G-US [240V] | 2.5 kW, 240 Vac Utility Interactive Inverter | 2.49 | 240 | 96.5 | Y | N |  | 0.25 |  |  | 100 | 360 | 480 | 0.25 | 0.5 | 0.75 | 1.25 | 1.87 | 2.49 | 92.3 | 94.6 | 95.7 | 96.9 | 96.7 | 96.4 | 96.3 | 93.4 | 95.5 | 96.6 | 97.6 | 97.4 | 97 | 97 | 93.1 | 95.1 | 96.3 | 97.4 | 96.9 | 96.7 | 96.7 |  | 2018-02-15
Ningbo Ginlong Technologies Co.,Ltd. | Solis-1P2.5K-4G-US [240V] | 2.5 kW, 240 Vac, 1-phase Utility Interactive Inverter | 2.5 | 240 | 97 | N | N |  | 3.2 |  |  | 120 | 330 | 500 | 0.25 | 0.5 | 0.75 | 1.25 | 1.875 | 2.5 | 93.6401 | 94.6457 | 95.692 | 96.8363 | 96.713 | 96.4833 | 96.3786 | 93.9159 | 95.5043 | 96.5921 | 97.6896 | 97.4379 | 97.114 | 97.1355 | 93.7984 | 95.1685 | 96.3297 | 97.4269 | 96.9989 | 96.8047 | 96.7792 | 2017-10-16 | 2018-10-15
Ningbo Ginlong Technologies Co.,Ltd. | GCI-3K-2G-H-US [208V] | 3 kW, 208 Vac Utility Interactive Inverter | 2.99 | 208 | 96.5 | Y | N |  | 0.25 |  |  | 100 | 360 | 480 | 0.3 | 0.6 | 0.9 | 1.5 | 2.24 | 2.99 | 93 | 94.9 | 95.8 | 97.1 | 96.8 | 96.5 | 96.5 | 93.6 | 95.3 | 96.2 | 97.6 | 97.4 | 96.8 | 97 | 93.3 | 95.1 | 96.1 | 97.3 | 97.1 | 96.6 | 96.7 |  | 2018-02-15
Ningbo Ginlong Technologies Co.,Ltd. | GCI-3K-2G-H-US [240V] | 3 kW, 240 Vac Utility Interactive Inverter | 2.99 | 240 | 97 | Y | N |  | 0.25 |  |  | 100 | 360 | 480 | 0.3 | 0.6 | 0.9 | 1.5 | 2.24 | 2.99 | 93.1 | 94.7 | 95.6 | 97.1 | 96.8 | 96.4 | 96.4 | 93.7 | 95.5 | 96.4 | 97.6 | 97.4 | 96.9 | 97 | 93.6 | 95.3 | 96.2 | 97.4 | 97.2 | 96.7 | 96.8 |  | 2018-02-15
Ningbo Ginlong Technologies Co.,Ltd. | GCI-3K-2G-W-US [208V] | 3 kW, 208 Vac Utility Interactive Inverter | 2.99 | 208 | 96.5 | Y | N |  | 0.25 |  |  | 100 | 360 | 480 | 0.3 | 0.6 | 0.9 | 1.5 | 2.24 | 2.99 | 93 | 94.9 | 95.8 | 97.1 | 96.8 | 96.5 | 96.5 | 93.6 | 95.3 | 96.2 | 97.6 | 97.4 | 96.8 | 97 | 93.3 | 95.1 | 96.1 | 97.3 | 97.1 | 96.6 | 96.7 |  | 2018-02-15
Ningbo Ginlong Technologies Co.,Ltd. | GCI-3K-2G-W-US [240V] | 3 kW, 240 Vac Utility Interactive Inverter | 2.99 | 240 | 97 | Y | N |  | 0.25 |  |  | 100 | 360 | 480 | 0.3 | 0.6 | 0.9 | 1.5 | 2.24 | 2.99 | 93.1 | 94.7 | 95.6 | 97.1 | 96.8 | 96.4 | 96.4 | 93.7 | 95.5 | 96.4 | 97.6 | 97.4 | 96.9 | 97 | 93.6 | 95.3 | 96.2 | 97.4 | 97.2 | 96.7 | 96.8 |  | 2018-02-15
Ningbo Ginlong Technologies Co.,Ltd. | Solis-3K-2G-US [208V] | 3 kW, 208 Vac Utility Interactive Inverter | 2.99 | 208 | 96.5 | Y | N |  | 0.25 |  |  | 100 | 360 | 480 | 0.3 | 0.6 | 0.9 | 1.5 | 2.24 | 2.99 | 93 | 94.9 | 95.8 | 97.1 | 96.8 | 96.5 | 96.5 | 93.6 | 95.3 | 96.2 | 97.6 | 97.4 | 96.8 | 97 | 93.3 | 95.1 | 96.1 | 97.3 | 97.1 | 96.6 | 96.7 |  | 2018-02-15
Ningbo Ginlong Technologies Co.,Ltd. | Solis-3K-2G-US [240V] | 3 kW, 240 Vac Utility Interactive Inverter | 2.99 | 240 | 97 | Y | N |  | 0.25 |  |  | 100 | 360 | 480 | 0.3 | 0.6 | 0.9 | 1.5 | 2.24 | 2.99 | 93.1 | 94.7 | 95.6 | 97.1 | 96.8 | 96.4 | 96.4 | 93.7 | 95.5 | 96.4 | 97.6 | 97.4 | 96.9 | 97 | 93.6 | 95.3 | 96.2 | 97.4 | 97.2 | 96.7 | 96.8 |  | 2018-02-15
Ningbo Ginlong Technologies Co.,Ltd. | Solis-1P3K-4G-US [240V] | 3 kW, 240 Vac, 1-phase Utility Interactive Inverter | 3 | 240 | 97 | N | N |  | 3.3 |  |  | 140 | 330 | 500 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 93.8664 | 94.7136 | 95.6114 | 97.0574 | 96.8122 | 96.477 | 96.4801 | 94.0667 | 95.6697 | 96.5539 | 97.7675 | 97.4264 | 97.0012 | 97.1499 | 93.845 | 95.2969 | 96.1758 | 97.4408 | 97.1733 | 96.697 | 96.859 | 2017-10-16 | 2018-10-15
Ningbo Ginlong Technologies Co.,Ltd. | GCI-3.6K-2G-H-US [208V] | 3.6 kW, 208 Vac Utility Interactive Inverter | 3.59 | 208 | 96.5 | Y | N |  | 0.25 |  |  | 100 | 360 | 480 | 0.36 | 0.72 | 1.08 | 1.8 | 2.69 | 3.59 | 92 | 94.5 | 95.7 | 96.7 | 96.7 | 96.2 | 96.2 | 92.9 | 95.4 | 96.4 | 97.2 | 97.4 | 96.6 | 96.9 | 92.5 | 95 | 96 | 97.2 | 97.1 | 96.3 | 96.6 |  | 2018-02-15
Ningbo Ginlong Technologies Co.,Ltd. | GCI-3.6K-2G-H-US [240V] | 3.6 kW, 240 Vac Utility Interactive Inverter | 3.59 | 240 | 96.5 | Y | N |  | 0.25 |  |  | 100 | 360 | 480 | 0.36 | 0.72 | 1.08 | 1.8 | 2.69 | 3.59 | 92.8 | 94.7 | 95.9 | 97 | 96.6 | 96.4 | 96.3 | 93.8 | 95.6 | 96.8 | 97.7 | 97.3 | 97.1 | 97.1 | 93.6 | 95.4 | 96.6 | 97.5 | 96.9 | 96.7 | 96.8 |  | 2018-02-15
Ningbo Ginlong Technologies Co.,Ltd. | GCI-3.6K-2G-W-US [208V] | 3.6 kW, 208 Vac Utility Interactive Inverter | 3.59 | 208 | 96.5 | Y | N |  | 0.25 |  |  | 100 | 360 | 480 | 0.36 | 0.72 | 1.08 | 1.8 | 2.69 | 3.59 | 92 | 94.5 | 95.7 | 96.7 | 96.7 | 96.2 | 96.2 | 92.9 | 95.4 | 96.4 | 97.2 | 97.4 | 96.6 | 96.9 | 92.5 | 95 | 96 | 97.2 | 97.1 | 96.3 | 96.6 |  | 2018-02-15
Ningbo Ginlong Technologies Co.,Ltd. | GCI-3.6K-2G-W-US [240V] | 3.6 kW, 240 Vac Utility Interactive Inverter | 3.59 | 240 | 96.5 | Y | N |  | 0.25 |  |  | 100 | 360 | 480 | 0.36 | 0.72 | 1.08 | 1.8 | 2.69 | 3.59 | 92.8 | 94.7 | 95.9 | 97 | 96.6 | 96.4 | 96.3 | 93.8 | 95.6 | 96.8 | 97.7 | 97.3 | 97.1 | 97.1 | 93.6 | 95.4 | 96.6 | 97.5 | 96.9 | 96.7 | 96.8 |  | 2018-02-15
Ningbo Ginlong Technologies Co.,Ltd. | Solis-3.6K-2G-US [208V] | 3.6 kW, 208 Vac Utility Interactive Inverter | 3.59 | 208 | 96.5 | Y | N |  | 0.25 |  |  | 100 | 360 | 480 | 0.36 | 0.72 | 1.08 | 1.8 | 2.69 | 3.59 | 92 | 94.5 | 95.7 | 96.7 | 96.7 | 96.2 | 96.2 | 92.9 | 95.4 | 96.4 | 97.2 | 97.4 | 96.6 | 96.9 | 92.5 | 95 | 96 | 97.2 | 97.1 | 96.3 | 96.6 |  | 2018-02-15
Ningbo Ginlong Technologies Co.,Ltd. | Solis-3.6K-2G-US [240V] | 3.6 kW, 240 Vac Utility Interactive Inverter | 3.59 | 240 | 96.5 | Y | N |  | 0.25 |  |  | 100 | 360 | 480 | 0.36 | 0.72 | 1.08 | 1.8 | 2.69 | 3.59 | 92.8 | 94.7 | 95.9 | 97 | 96.6 | 96.4 | 96.3 | 93.8 | 95.6 | 96.8 | 97.7 | 97.3 | 97.1 | 97.1 | 93.6 | 95.4 | 96.6 | 97.5 | 96.9 | 96.7 | 96.8 |  | 2018-02-15
Ningbo Ginlong Technologies Co.,Ltd. | Solis-1P3.6K-4G-US [240V] | 3.6 kW, 240 Vac, 1-phase Utility Interactive Inverter | 3.6 | 240 | 97 | N | N |  | 3.5 |  |  | 180 | 330 | 500 | 0.36 | 0.72 | 1.08 | 1.8 | 2.7 | 3.6 | 93.8804 | 94.7446 | 95.6302 | 97.0904 | 96.8386 | 96.4907 | 96.506 | 93.9017 | 95.6722 | 96.8973 | 97.7959 | 97.4214 | 97.0622 | 97.1909 | 93.8792 | 95.4947 | 96.5522 | 97.4831 | 97.1511 | 96.7645 | 96.9159 | 2017-10-16 | 2018-10-15
Ningbo Ginlong Technologies Co.,Ltd. | GCI-4K-2G-H-US [208V] | 4 kW, 208 Vac Utility Interactive Inverter | 3.99 | 208 | 97 | Y | N |  | 0.25 |  |  | 100 | 360 | 480 | 0.4 | 0.8 | 1.2 | 2 | 2.99 | 3.99 | 92.8 | 94.8 | 96 | 97.2 | 96.8 | 96.4 | 96.5 | 93.6 | 95.4 | 96.5 | 97.8 | 97.3 | 96.8 | 97 | 93.6 | 95.2 | 96.3 | 97.5 | 97.1 | 96.6 | 96.8 |  | 2018-02-15
Ningbo Ginlong Technologies Co.,Ltd. | GCI-4K-2G-H-US [240V] | 4 kW, 240 Vac Utility Interactive Inverter | 3.99 | 240 | 97 | Y | N |  | 0.25 |  |  | 100 | 360 | 480 | 0.4 | 0.8 | 1.2 | 2 | 2.99 | 3.99 | 93.1 | 94.8 | 96 | 97.1 | 96.7 | 96.3 | 96.4 | 93.7 | 95.5 | 96.6 | 97.8 | 97.4 | 96.9 | 97.1 | 93.5 | 95.3 | 96.4 | 97.6 | 97.2 | 96.7 | 96.9 |  | 2018-02-15
Ningbo Ginlong Technologies Co.,Ltd. | GCI-4K-2G-W-US [208V] | 4 kW, 208 Vac Utility Interactive Inverter | 3.99 | 208 | 97 | Y | N |  | 0.25 |  |  | 100 | 360 | 480 | 0.4 | 0.8 | 1.2 | 2 | 2.99 | 3.99 | 92.8 | 94.8 | 96 | 97.2 | 96.8 | 96.4 | 96.5 | 93.6 | 95.4 | 96.5 | 97.8 | 97.3 | 96.8 | 97 | 93.6 | 95.2 | 96.3 | 97.5 | 97.1 | 96.6 | 96.8 |  | 2018-02-15
Ningbo Ginlong Technologies Co.,Ltd. | GCI-4K-2G-W-US [240V] | 4 kW, 240 Vac Utility Interactive Inverter | 3.99 | 240 | 97 | Y | N |  | 0.25 |  |  | 100 | 360 | 480 | 0.4 | 0.8 | 1.2 | 2 | 2.99 | 3.99 | 93.1 | 94.8 | 96 | 97.1 | 96.7 | 96.3 | 96.4 | 93.7 | 95.5 | 96.6 | 97.8 | 97.4 | 96.9 | 97.1 | 93.5 | 95.3 | 96.4 | 97.6 | 97.2 | 96.7 | 96.9 |  | 2018-02-15
Ningbo Ginlong Technologies Co.,Ltd. | Solis-4K-2G-US [208V] | 4 kW, 208 Vac Utility Interactive Inverter | 3.99 | 208 | 97 | Y | N |  | 0.25 |  |  | 100 | 360 | 480 | 0.4 | 0.8 | 1.2 | 2 | 2.99 | 3.99 | 92.8 | 94.8 | 96 | 97.2 | 96.8 | 96.4 | 96.5 | 93.6 | 95.4 | 96.5 | 97.8 | 97.3 | 96.8 | 97 | 93.6 | 95.2 | 96.3 | 97.5 | 97.1 | 96.6 | 96.8 |  | 2018-02-15
Ningbo Ginlong Technologies Co.,Ltd. | Solis-4K-2G-US [240V] | 4 kW, 240 Vac Utility Interactive Inverter | 3.99 | 240 | 97 | Y | N |  | 0.25 |  |  | 100 | 360 | 480 | 0.4 | 0.8 | 1.2 | 2 | 2.99 | 3.99 | 93.1 | 94.8 | 96 | 97.1 | 96.7 | 96.3 | 96.4 | 93.7 | 95.5 | 96.6 | 97.8 | 97.4 | 96.9 | 97.1 | 93.5 | 95.3 | 96.4 | 97.6 | 97.2 | 96.7 | 96.9 |  | 2018-02-15
Ningbo Ginlong Technologies Co.,Ltd. | Solis-1P4K-4G-US [240V] | 4 kW, 240 Vac, 1-phase Utility Interactive Inverter | 4 | 240 | 97 | N | N |  | 3.5 |  |  | 190 | 330 | 500 | 0.4 | 0.8 | 1.2 | 2 | 3 | 4 | 93.8715 | 94.7255 | 96.0908 | 97.0869 | 96.8217 | 96.404 | 96.546 | 94.0293 | 95.7206 | 96.9837 | 97.9192 | 97.4909 | 97.3216 | 97.2845 | 93.8761 | 95.4725 | 96.5568 | 97.5311 | 97.1444 | 96.7796 | 96.9225 | 2017-10-16 | 2018-10-15
Ningbo Ginlong Technologies Co.,Ltd. | GCI-4.6K-2G-H-US [208V] | 4.6 kW, 208 Vac Utility Interactive Inverter | 4.59 | 208 | 97 | Y | N |  | 0.25 |  |  | 100 | 360 | 480 | 0.46 | 0.92 | 1.38 | 2.3 | 3.44 | 4.59 | 92.8 | 94.4 | 95.9 | 97 | 96.9 | 96.6 | 96.5 | 93.4 | 95.1 | 96.6 | 97.7 | 97.5 | 96.9 | 97.1 | 93.3 | 94.8 | 96.3 | 97.4 | 97.2 | 96.8 | 96.8 |  | 2018-02-15
Ningbo Ginlong Technologies Co.,Ltd. | GCI-4.6K-2G-H-US [240V] | 4.6 kW, 240 Vac Utility Interactive Inverter | 4.59 | 240 | 97 | Y | N |  | 0.25 |  |  | 100 | 360 | 480 | 0.46 | 0.92 | 1.38 | 2.3 | 3.44 | 4.59 | 93.1 | 94.4 | 95.7 | 96.9 | 96.8 | 96.5 | 96.4 | 93.8 | 95.3 | 96.7 | 97.8 | 97.5 | 97 | 97.2 | 93.7 | 95.1 | 96.5 | 97.4 | 97.2 | 96.9 | 96.9 |  | 2018-02-15
Ningbo Ginlong Technologies Co.,Ltd. | GCI-4.6K-2G-W-US [208V] | 4.6 kW, 208 Vac Utility Interactive Inverter | 4.59 | 208 | 97 | Y | N |  | 0.25 |  |  | 100 | 360 | 480 | 0.46 | 0.92 | 1.38 | 2.3 | 3.44 | 4.59 | 92.8 | 94.4 | 95.9 | 97 | 96.9 | 96.6 | 96.5 | 93.4 | 95.1 | 96.6 | 97.7 | 97.5 | 96.9 | 97.1 | 93.3 | 94.8 | 96.3 | 97.4 | 97.2 | 96.8 | 96.8 |  | 2018-02-15
Ningbo Ginlong Technologies Co.,Ltd. | GCI-4.6K-2G-W-US [240V] | 4.6 kW, 240 Vac Utility Interactive Inverter | 4.59 | 240 | 97 | Y | N |  | 0.25 |  |  | 100 | 360 | 480 | 0.46 | 0.92 | 1.38 | 2.3 | 3.44 | 4.59 | 93.1 | 94.4 | 95.7 | 96.9 | 96.8 | 96.5 | 96.4 | 93.8 | 95.3 | 96.7 | 97.8 | 97.5 | 97 | 97.2 | 93.7 | 95.1 | 96.5 | 97.4 | 97.2 | 96.9 | 96.9 |  | 2018-02-15
Ningbo Ginlong Technologies Co.,Ltd. | Solis-4.6K-2G-US [208V] | 4.6 kW, 208 Vac Utility Interactive Inverter | 4.59 | 208 | 97 | Y | N |  | 0.25 |  |  | 100 | 360 | 480 | 0.46 | 0.92 | 1.38 | 2.3 | 3.44 | 4.59 | 92.8 | 94.4 | 95.9 | 97 | 96.9 | 96.6 | 96.5 | 93.4 | 95.1 | 96.6 | 97.7 | 97.5 | 96.9 | 97.1 | 93.3 | 94.8 | 96.3 | 97.4 | 97.2 | 96.8 | 96.8 |  | 2018-02-15
Ningbo Ginlong Technologies Co.,Ltd. | Solis-4.6K-2G-US [240V] | 4.6 kW, 240 Vac Utility Interactive Inverter | 4.59 | 240 | 97 | Y | N |  | 0.25 |  |  | 100 | 360 | 480 | 0.46 | 0.92 | 1.38 | 2.3 | 3.44 | 4.59 | 93.1 | 94.4 | 95.7 | 96.9 | 96.8 | 96.5 | 96.4 | 93.8 | 95.3 | 96.7 | 97.8 | 97.5 | 97 | 97.2 | 93.7 | 95.1 | 96.5 | 97.4 | 97.2 | 96.9 | 96.9 |  | 2018-02-15
Ningbo Ginlong Technologies Co.,Ltd. | Solis-1P4.6K-4G-US [240V] | 4.6 kW, 240 Vac, 1-phase Utility Interactive Inverter | 4.6 | 240 | 97 | N | N |  | 3.6 |  |  | 200 | 360 | 500 | 0.46 | 0.92 | 1.38 | 2.3 | 3.45 | 4.6 | 93.0282 | 94.3391 | 95.7359 | 96.9043 | 96.8001 | 96.5325 | 96.407 | 94.0655 | 95.5741 | 96.9074 | 97.9375 | 97.5427 | 97.3118 | 97.3003 | 93.7876 | 95.1009 | 96.5461 | 97.4374 | 97.2666 | 96.964 | 96.9534 | 2017-10-16 | 2018-10-15
Ningbo Ginlong Technologies Co.,Ltd. | GCI-5K-2G-H-US [208V] | 5 kW, 208 Vac Utility Interactive Inverter | 4.99 | 208 | 97 | Y | N |  | 0.25 |  |  | 100 | 360 | 480 | 0.5 | 1 | 1.5 | 2.5 | 3.74 | 4.99 | 93.4 | 94.6 | 95.5 | 97 | 96.9 | 96.3 | 96.5 | 94.4 | 95.5 | 96.4 | 97.7 | 97.6 | 96.7 | 97.2 | 94 | 94.9 | 96.1 | 97.5 | 97.3 | 96.5 | 96.9 |  | 2018-02-15
Ningbo Ginlong Technologies Co.,Ltd. | GCI-5K-2G-H-US [240V] | 5 kW, 240 Vac Utility Interactive Inverter | 4.99 | 240 | 97 | Y | N |  | 0.25 |  |  | 100 | 360 | 480 | 0.5 | 1 | 1.5 | 2.5 | 3.74 | 4.99 | 93.5 | 94.6 | 95.6 | 97 | 96.9 | 96.5 | 96.5 | 94.3 | 95.5 | 96.4 | 97.7 | 97.6 | 97.1 | 97.2 | 94.1 | 95 | 96.1 | 97.5 | 97.3 | 97 | 97 |  | 2018-02-15
Ningbo Ginlong Technologies Co.,Ltd. | GCI-5K-2G-W-US [208V] | 5 kW, 208 Vac Utility Interactive Inverter | 4.99 | 208 | 97 | Y | N |  | 0.25 |  |  | 100 | 360 | 480 | 0.5 | 1 | 1.5 | 2.5 | 3.74 | 4.99 | 93.4 | 94.6 | 95.5 | 97 | 96.9 | 96.3 | 96.5 | 94.4 | 95.5 | 96.4 | 97.7 | 97.6 | 96.7 | 97.2 | 94 | 94.9 | 96.1 | 97.5 | 97.3 | 96.5 | 96.9 |  | 2018-02-15
Ningbo Ginlong Technologies Co.,Ltd. | GCI-5K-2G-W-US [240V] | 5 kW, 240 Vac Utility Interactive Inverter | 4.99 | 240 | 97 | Y | N |  | 0.25 |  |  | 100 | 360 | 480 | 0.5 | 1 | 1.5 | 2.5 | 3.74 | 4.99 | 93.5 | 94.6 | 95.6 | 97 | 96.9 | 96.5 | 96.5 | 94.3 | 95.5 | 96.4 | 97.7 | 97.6 | 97.1 | 97.2 | 94.1 | 95 | 96.1 | 97.5 | 97.3 | 97 | 97 |  | 2018-02-15
Ningbo Ginlong Technologies Co.,Ltd. | Solis-5K-2G-US [208V] | 5 kW, 208 Vac Utility Interactive Inverter | 4.99 | 208 | 97 | Y | N |  | 0.25 |  |  | 100 | 360 | 480 | 0.5 | 1 | 1.5 | 2.5 | 3.74 | 4.99 | 93.4 | 94.6 | 95.5 | 97 | 96.9 | 96.3 | 96.5 | 94.4 | 95.5 | 96.4 | 97.7 | 97.6 | 96.7 | 97.2 | 94 | 94.9 | 96.1 | 97.5 | 97.3 | 96.5 | 96.9 |  | 2018-02-15
Ningbo Ginlong Technologies Co.,Ltd. | Solis-5K-2G-US [240V] | 5 kW, 240 Vac Utility Interactive Inverter | 4.99 | 240 | 97 | Y | N |  | 0.25 |  |  | 100 | 360 | 480 | 0.5 | 1 | 1.5 | 2.5 | 3.74 | 4.99 | 93.5 | 94.6 | 95.6 | 97 | 96.9 | 96.5 | 96.5 | 94.3 | 95.5 | 96.4 | 97.7 | 97.6 | 97.1 | 97.2 | 94.1 | 95 | 96.1 | 97.5 | 97.3 | 97 | 97 |  | 2018-02-15
Ningbo Ginlong Technologies Co.,Ltd. | GCI-5K-DB [240V] | 5 kW, 240 Vac Utility Interactive Inverter | 5 | 240 | 95.5 | Y | N |  | 0.45 |  |  | 100 | 410 | 500 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 92.1 | 94.9 | 95.5 | 95.5 | 94.8 | 94.1 | 94.9 | 93.8 | 96.1 | 96.8 | 96.7 | 96.1 | 95.5 | 96.2 | 92.2 | 95.4 | 96.4 | 96.3 | 95.9 | 95.3 | 95.8 |  | 2018-02-15
Ningbo Ginlong Technologies Co.,Ltd. | GCI-5K-W [240V] | 5 kW, 240 Vac Utility Interactive Inverter | 5 | 240 | 95.5 | Y | N |  | 0.45 |  |  | 100 | 410 | 500 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 92.1 | 94.9 | 95.5 | 95.5 | 94.8 | 94.1 | 94.9 | 93.8 | 96.1 | 96.8 | 96.7 | 96.1 | 95.5 | 96.2 | 92.2 | 95.4 | 96.4 | 96.3 | 95.9 | 95.3 | 95.8 |  | 2018-02-15
Ningbo Ginlong Technologies Co.,Ltd. | Solis 5000-DB [240V] | 5 kW, 240 Vac Utility Interactive Inverter | 5 | 240 | 95.5 | Y | N |  | 0.45 |  |  | 100 | 410 | 500 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 92.1 | 94.9 | 95.5 | 95.5 | 94.8 | 94.1 | 94.9 | 93.8 | 96.1 | 96.8 | 96.7 | 96.1 | 95.5 | 96.2 | 92.2 | 95.4 | 96.4 | 96.3 | 95.9 | 95.3 | 95.8 |  | 2018-02-15
Ningbo Ginlong Technologies Co.,Ltd. | Solis-1P5K-4G-US [240V] | 5 kW, 240 Vac, 1-phase Utility Interactive Inverter | 5 | 240 | 97 | N | N |  | 3.6 |  |  | 240 | 360 | 500 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 93.9967 | 94.5979 | 95.7172 | 97.3161 | 97.0155 | 96.5167 | 96.6563 | 94.5418 | 95.7374 | 96.5953 | 97.9319 | 97.6168 | 97.433 | 97.3342 | 94.0094 | 94.9752 | 96.145 | 97.4705 | 97.3308 | 96.8481 | 96.9431 | 2017-10-16 | 2018-10-15
Ningbo Ginlong Technologies Co.,Ltd. | Solis-1P6K2-4G-US [240V] | 6 kW, 240 Vac, 1-phase Utility Interactive Inverter, 2 channel | 6 | 240 | 97 | N | N |  | 3.5 |  |  | 300 | 360 | 500 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 94.1975 | 94.8034 | 95.9161 | 97.4325 | 97.2123 | 96.7122 | 96.837 | 94.4335 | 95.6416 | 96.5269 | 97.8303 | 97.7139 | 97.3363 | 97.3422 | 94.2126 | 95.1763 | 96.3489 | 97.6663 | 97.5266 | 97.0427 | 97.1403 | 2017-10-16 | 2018-10-15
Ningbo Ginlong Technologies Co.,Ltd. | Solis-1P6K-4G-US | 6.0 kW, transformerless Utility Interactive Inverter | 6 |  | 97.5 | Y | N |  | 6 |  |  | 200 | 380 | 500 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 94.8998 | 96.1208 | 96.7645 | 97.3045 | 97.3234 | 96.4761 | 97.0529 | 95.5487 | 96.9813 | 97.3964 | 97.4228 | 97.3717 | 97.9525 | 97.322 | 95.3083 | 96.9146 | 97.4794 | 97.5873 | 97.5795 | 97.5828 | 97.4452 |  | 2018-02-15
Ningbo Ginlong Technologies Co.,Ltd. | Solis-6K-US 480 Vac [480V] | 6.0 kW, 480 Vac Utility Interactive Inverter | 6 | 480 | 97 | Y | N |  | 7 |  |  | 100 | 650 | 780 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 93.9 | 94.8 | 95.6 | 96.5 | 97 | 96.5 | 96.5 | 95 | 96.1 | 96.7 | 97.3 | 97.6 | 97.3 | 97.2 | 94.5 | 95.8 | 96.5 | 97.2 | 97.4 | 96.7 | 97 |  | 2018-02-15
Ningbo Ginlong Technologies Co.,Ltd. | Solis-1P7K-4G-US [240V] | 7 kW, 240 Vac, 1-phase Utility Interactive Inverter | 7 | 240 | 97.5 | Y | N | Multiple Listing of Flextronics Industrial Ltd, FLV-IA-7.0S1UA | 7 |  |  | 250 | 380 | 500 | 0.7 | 1.4 | 2.1 | 3.5 | 5.25 | 7 | 94.9607 | 96.155 | 96.8314 | 97.3565 | 97.3538 | 96.5398 | 97.0953 | 95.5846 | 97.0123 | 97.429 | 97.5 | 97.509 | 97.0437 | 97.3725 | 95.3208 | 96.9551 | 97.5201 | 97.6639 | 97.5988 | 97.5959 | 97.4796 | 2017-10-16 | 2018-10-15
Ningbo Ginlong Technologies Co.,Ltd. | Solis-1P7.6K-4G-US | 7.6 kW, transformerless Utility Interactive Inverter | 7.6 |  | 97.5 | Y | N |  | 7 |  |  | 200 | 380 | 500 | 0.76 | 1.52 | 2.28 | 3.8 | 5.7 | 7.6 | 95.0545 | 96.1601 | 96.8885 | 97.3433 | 97.1468 | 96.576 | 96.9955 | 95.631 | 97.1836 | 97.4753 | 97.7794 | 97.347 | 97.8962 | 97.4038 | 95.3586 | 96.7534 | 97.606 | 97.8242 | 97.8541 | 97.7094 | 97.6559 |  | 2018-02-15
Ningbo Ginlong Technologies Co.,Ltd. | Solis-1P8K-4G-US | 8.0 kW, transformerless Utility Interactive Inverter | 8 |  | 97.5 | Y | N |  | 6 |  |  | 250 | 380 | 500 | 0.8 | 1.6 | 2.4 | 4 | 6 | 8 | 95.1153 | 96.1755 | 96.939 | 97.3693 | 97.1827 | 96.6319 | 97.0321 | 95.6565 | 97.2399 | 97.4217 | 97.5479 | 97.7024 | 96.9559 | 97.494 | 95.3757 | 96.7466 | 97.6107 | 97.8173 | 97.8528 | 97.7053 | 97.6545 |  | 2018-02-15
Ningbo Ginlong Technologies Co.,Ltd. | Solis-1P9K-4G-US | 9.0 kW, transformerless Utility Interactive Inverter | 9 |  | 97.5 | Y | N |  | 7 |  |  | 250 | 380 | 500 | 0.9 | 1.8 | 2.7 | 4.5 | 6.75 | 9 | 95.142 | 96.7533 | 96.9992 | 97.4866 | 97.373 | 96.9957 | 97.2129 | 95.718 | 97.2744 | 97.4478 | 97.6088 | 97.7501 | 97.1064 | 97.5469 | 95.5774 | 96.7392 | 97.6611 | 97.8213 | 97.8215 | 97.7076 | 97.6526 |  | 2018-02-15
Ningbo Ginlong Technologies Co.,Ltd. | Solis-10K-US [480V] | 10.0 kW, 480 Vac Utility Interactive Inverter | 10 | 480 | 97.5 | Y | N |  | 12 |  |  | 450 | 650 | 780 | 1 | 2 | 3 | 5 | 7.5 | 10 | 94.2 | 95.2 | 96.3 | 97.1 | 97.5 | 96.8 | 97 | 95.2 | 96.3 | 96.9 | 97.6 | 98.1 | 97.5 | 97.6 | 94.7 | 96.1 | 96.7 | 97.5 | 97.8 | 97.4 | 97.4 |  | 2018-02-15
Ningbo Ginlong Technologies Co.,Ltd. | Solis-1P10K-4G-US | 10.0 kW, transformerless Utility Interactive Inverter | 10 |  | 97.5 | Y | N |  | 7 |  |  | 250 | 380 | 500 | 1 | 2 | 3 | 5 | 7.5 | 10 | 95.1813 | 96.7793 | 97.0795 | 97.5465 | 97.6095 | 97.0578 | 97.3665 | 95.3043 | 96.3202 | 97.584 | 97.6578 | 97.7307 | 97.2052 | 97.5039 | 95.5999 | 96.7961 | 97.6824 | 97.7928 | 97.8088 | 97.7069 | 97.6462 |  | 2018-02-15
Ningbo Ginlong Technologies Co.,Ltd. | Solis-15K-US [480V] | 15.0 kW, 480 Vac Utility Interactive Inverter | 15 | 480 | 97.5 | Y | N |  | 15 |  |  | 450 | 650 | 780 | 1.5 | 3 | 4.5 | 7.5 | 11.25 | 15 | 94.2 | 95.3 | 96.4 | 97.2 | 97.6 | 96.9 | 97.1 | 95.2 | 96.3 | 96.9 | 97.6 | 98.1 | 97.5 | 97.6 | 94.7 | 96.1 | 96.7 | 97.5 | 97.8 | 97.4 | 97.4 |  | 2018-02-15
Ningbo Ginlong Technologies Co.,Ltd. | Solis-20K-US [480V] | 20.0 kW, 480 Vac Utility Interactive Inverter | 20 | 480 | 97.5 | Y | N |  | 15 |  |  | 580 | 650 | 780 | 2 | 4 | 6 | 10 | 15 | 20 | 94.2 | 95.3 | 96.4 | 97.2 | 97.6 | 96.9 | 97.1 | 95.3 | 96.4 | 97 | 97.8 | 98.2 | 97.6 | 97.7 | 94.9 | 96.3 | 96.9 | 97.7 | 98 | 97.6 | 97.5 |  | 2018-02-15
Ningbo Ginlong Technologies Co.,Ltd. | Solis-25K-US [480V] | 25 kW, 480 Vac, 3-phase Utility Interactive Inverter, | 25.05 | 480 | 98 | N | N |  | 14 |  |  | 580 | 650 | 780 | 2.5 | 5 | 7.5 | 12.5 | 18.75 | 25 | 97.1 | 97.4 | 97.6 | 97.9 | 98 | 97.8 | 97.9 | 97.1 | 97.3 | 97.6 | 97.8 | 98.3 | 97.6 | 98 | 97.2 | 97.4 | 97.7 | 97.8 | 98 | 97.5 | 97.9 | 2018-02-15 | 2018-10-15
Ningbo Ginlong Technologies Co.,Ltd. | Solis-30K-US [480V] | 30 kW, 480 Vac, 3-phase Utility Interactive Inverter, | 30.05 | 480 | 98 | N | N |  | 15 |  |  | 580 | 650 | 780 | 3 | 6 | 9 | 15 | 22.5 | 30 | 97.1 | 97.9 | 97.9 | 98.3 | 97.5 | 97.9 | 97.8 | 97.4 | 98.1 | 98.1 | 98.4 | 98.1 | 97.9 | 98.1 | 97.1 | 97.9 | 98 | 98.3 | 98 | 97.8 | 98 | 2018-02-15 | 2018-10-15
Ningbo Ginlong Technologies Co.,Ltd. | Solis-36K-US [480V] | 36 kW, 480 Vac, 3-phase Utility Interactive Inverter, | 36.05 | 480 | 98 | N | N |  | 15 |  |  | 580 | 650 | 780 | 3.6 | 7.2 | 10.8 | 18 | 27 | 36 | 97.3 | 98.2 | 98.1 | 98.4 | 97.6 | 98.1 | 97.9 | 97.7 | 98.3 | 98.3 | 98.4 | 98.3 | 98.1 | 98.3 | 97.4 | 98.1 | 98.2 | 98.3 | 98.2 | 98.1 | 98.2 | 2018-02-15 | 2018-10-15
Ningbo Ginlong Technologies Co.,Ltd. | Solis-40K-US-F [480V] | It's a series of 3 phase inverter , with rated output from 40--66kW for roof top commerical and ground commerical PV site. | 40 | 480 | 98.5 | N | N |  | 1 |  |  | 580 | 650 | 780 | 4 | 8 | 12 | 20 | 30 | 40 | 97.5 | 98 | 98.1 | 98.2 | 98.1 | 97.7 | 98.1 | 97.8 | 98.3 | 98.4 | 98.6 | 98.5 | 98.3 | 98.5 | 97.6 | 98.1 | 98.2 | 98.4 | 98.3 | 98 | 98.3 | 2017-10-16 | 2018-02-15
Ningbo Ginlong Technologies Co.,Ltd. | Solis-40K-US [480V] | 40 kW, 480 Vac, 3-phase Utility Interactive Inverter, | 40.05 | 480 | 98.5 | N | N |  | 1 |  |  | 580 | 650 | 780 | 4 | 8 | 12 | 20 | 30 | 40 | 97.5 | 98 | 98.1 | 98.2 | 98.1 | 98 | 98.1 | 97.9 | 98.3 | 98.4 | 98.7 | 98.6 | 98.3 | 98.5 | 97.6 | 98.2 | 98.2 | 98.4 | 98.3 | 98.2 | 98.3 | 2018-02-15 | 2018-10-15
Ningbo Ginlong Technologies Co.,Ltd. | Solis-50K-US [480V] | It's a series of 3 phase inverter , with rated output from 40--66kW for roof top commerical and ground commerical PV site. | 50 | 480 | 98.5 | N | N |  | 1 |  |  | 580 | 650 | 720 | 5 | 10 | 15 | 25 | 37.5 | 50 | 97.52 | 98.53 | 98.44 | 98.56 | 98.32 | 98.45 | 98.37 | 97.75 | 98.55 | 98.52 | 98.65 | 98.43 | 98.49 | 98.47 | 97.98 | 98.7 | 98.8 | 98.79 | 98.57 | 98.5 | 98.62 | 2017-10-16 | 2018-02-15
Ningbo Ginlong Technologies Co.,Ltd. | Solis-50K-US-F [480V] | 50 kW, 480 Vac, 3-phase Utility Interactive Inverter, | 50.083 | 480 | 98.5 | N | N | Multiple Listing of Canadian Solar Incorporated. CSI-50KTL-GS | 1 |  |  | 580 | 650 | 720 | 5 | 10 | 15 | 25 | 37.5 | 50 | 97.74 | 98.44 | 98.46 | 98.58 | 98.45 | 98.35 | 98.44 | 97.8 | 98.53 | 98.55 | 98.7 | 98.51 | 98.4 | 98.52 | 97.88 | 98.58 | 98.65 | 98.76 | 98.57 | 98.46 | 98.59 | 2018-02-01 | 2018-10-15
Ningbo Ginlong Technologies Co.,Ltd. | Solis-60K-US-F [480V] | 60 kW, 480 Vac, 3-phase Utility Interactive Inverter, | 60.086 | 480 | 98.5 | N | N | Multiple Listing of Canadian Solar Incorporated. CSI-60KTL-GS | 1 |  |  | 580 | 650 | 720 | 6 | 12 | 18 | 30 | 45 | 60 | 97.73 | 98.31 | 98.42 | 98.55 | 98.37 | 98.22 | 98.38 | 97.82 | 98.45 | 98.54 | 98.63 | 98.5 | 98.33 | 98.49 | 97.86 | 98.53 | 98.59 | 98.7 | 98.55 | 98.45 | 98.55 | 2018-02-01 | 2018-10-15
Ningbo Ginlong Technologies Co.,Ltd. | Solis-66K-US-F [480V] | 66 kW, 480 Vac, 3-phase Utility Interactive Inverter. | 66.07 | 480 | 98.5 | N | N | Multiple Listing of Canadian Solar Incorporated. CSI-66KTL-GS | 1 |  |  | 580 | 650 | 720 | 6.6 | 13.2 | 19.8 | 33 | 49.5 | 66 | 97.57 | 98.38 | 98.48 | 98.56 | 98.42 | 98.31 | 98.42 | 97.74 | 98.5 | 98.55 | 98.7 | 98.5 | 98.39 | 98.51 | 97.77 | 98.67 | 98.65 | 98.77 | 98.56 | 98.49 | 98.58 | 2018-02-01 | 2018-10-15
Northern Electric | BDM-300X2-208A [208V] | 500 W, 208 Vac Utility Interactive Inverter | 0.508 | 208 | 95.5 | N | Y |  | 0.11 |  |  | 22 | 33 | 48 | 0.05 | 0.1 | 0.15 | 0.25 | 0.38 | 0.51 | 92.8 | 94.1 | 94.8 | 95.4 | 95.4 | 94.6 | 95.1 | 94.1 | 95.6 | 95.5 | 95.8 | 96.3 | 95.4 | 95.9 | 94.6 | 95.4 | 95.3 | 95.9 | 95.7 | 95.6 | 95.6
Northern Electric | BDM-300X2-240A [240V] | 500 W, 240 Vac Utility Interactive Inverter | 0.51 | 240 | 95.5 | N | Y |  | 0.11 |  |  | 22 | 33 | 48 | 0.05 | 0.1 | 0.15 | 0.26 | 0.38 | 0.51 | 92.7 | 93.5 | 94.7 | 95.4 | 95.4 | 95.1 | 95.1 | 94.5 | 93.9 | 94.9 | 95.8 | 96.1 | 95.5 | 95.7 | 94.5 | 94.2 | 94.4 | 95.4 | 95.9 | 95.6 | 95.4
Northern Electric & Power | BDM-250-208A [208V] | 217 W, 208 Vac Utility Interactive Inverter | 0.217 | 208 | 95 | N | Y |  | 0.17 |  |  | 22 | 28.5 | 44 | 0.22 | 0.43 | 0.65 | 1.08 | 1.63 | 2.17 | 89.6 | 95.5 | 95.3 | 95.7 | 95 | 94.1 | 94.9 | 90.8 | 95.2 | 94.8 | 95.5 | 95.4 | 95 | 95.2 | 85.8 | 91.5 | 93.5 | 94.4 | 95.1 | 95.5 | 94.2
Northern Electric & Power | BDM-250-240A [240V] | 225 W, 240 Vac Utility Interactive Inverter | 0.225 | 240 | 95 | N | Y |  | 0.17 |  |  | 22 | 28.5 | 44 | 0.23 | 0.45 | 0.68 | 1.13 | 1.69 | 2.25 | 90.1 | 94.5 | 94.9 | 95.1 | 95.9 | 95.4 | 95.3 | 89.7 | 93.9 | 95.2 | 95.1 | 96.2 | 96.2 | 95.5 | 85.2 | 91.4 | 93.7 | 92.5 | 95.2 | 96.3 | 93.9
Northern Electric & Power Co., Ltd | BDM-300-208A [208V] | 250 W, 208 Vac Utility Interactive Inverter | 0.25 | 208 | 95.5 | N | Y |  | 0.06 |  |  | 22 | 29 | 38 | 0.0251 | 0.05019 | 0.07529 | 0.12548 | 0.18821 | 0.25095 | 93.3 | 94.8 | 96.1 | 95.2 | 95.5 | 95.3 | 95.4 | 94.1 | 95.7 | 96.2 | 95.6 | 95.7 | 95.6 | 95.7 | 94.2 | 96.1 | 95.9 | 95.8 | 95.5 | 96 | 95.6 |  | 2018-03-01
Northern Electric & Power Co., Ltd | BDM-300-240A [240V] | 250 W, 240 Vac Utility Interactive Inverter | 0.25 | 240 | 95.5 | N | Y |  | 0.08 |  |  | 22 | 29 | 38 | 0.0251 | 0.05019 | 0.07529 | 0.12548 | 0.18821 | 0.25095 | 92.2 | 94.1 | 94.9 | 95.2 | 96.1 | 95.7 | 95.5 | 92.9 | 94.7 | 94.5 | 95.7 | 96.1 | 96.3 | 95.7 | 92.7 | 94.6 | 93.2 | 95.7 | 95.4 | 96.4 | 95.1 |  | 2018-03-01
Open Energy | Solar Save 1100 [240V] | 1100 W, 240 Vac Utility Interactive Inverter | 1.1 | 240 | 90.5 | Y | N |  | 3.6 |  |  | 100 | 182 | 380 | 0.11 | 0.22 | 0.33 | 0.55 | 0.83 | 1.1 | 81.8 | 89 | 90.9 | 92.1 | 92.4 | 92.5 | 91.6 | 79.9 | 88 | 90.1 | 91.7 | 92.2 | 92.3 | 91.1 | 74.8 | 84.7 | 87.8 | 90 | 90.8 | 91.1 | 89.3
Open Energy | Solar Save 2000 [240V] | 2000 W, 240 Vac Utility Interactive Inverter | 2 | 240 | 92 | Y | N |  | 3.6 |  |  | 100 | 199 | 380 | 0.2 | 0.4 | 0.6 | 1 | 1.5 | 2 | 87.3 | 91.7 | 92.6 | 93.5 | 93.2 | 93 | 92.9 | 85.7 | 90.8 | 92.1 | 92.9 | 92.9 | 92.6 | 92.4 | 82.4 | 88.8 | 90.5 | 91.6 | 91.8 | 91.6 | 91.1
Open Energy | Solar Save 2500 [240V] | 2500 W, 240 Vac Utility Interactive Inverter | 2.5 | 240 | 94.5 | Y | N |  | 3.9 |  |  | 100 | 218 | 400 | 0.25 | 0.5 | 0.75 | 1.25 | 1.88 | 2.5 | 87.1 | 93.3 | 94.9 | 95.8 | 95.8 | 95.6 | 95.2 | 85.2 | 92.4 | 93.8 | 95.2 | 95.4 | 95.1 | 94.6 | 80.4 | 90 | 91.7 | 93.7 | 94.5 | 93.8 | 93.2
Open Energy | Solar Save 3500 [240V] | 3500 W, 240 Vac Utility Interactive Inverter | 3.5 | 240 | 95.5 | Y | N |  | 3.86 |  |  | 100 | 263 | 400 | 0.35 | 0.7 | 1.05 | 1.75 | 2.625 | 3.5 | 87.2 | 93.1 | 95.4 | 96.5 | 96.7 | 96.6 | 95.9 | 85.7 | 92.2 | 94.9 | 96.2 | 96.4 | 96.3 | 95.5 | 82.1 | 90.2 | 93.6 | 95.4 | 95.7 | 95.6 | 94.5
Open Energy | Solar Save 4600 [208V] | 4600 W, 208 Vac Utility Interactive Inverter | 4.6 | 208 | 95.5 | Y | N |  | 4 |  |  | 100 | 254 | 400 | 0.46 | 0.92 | 1.38 | 2.3 | 3.45 | 4.6 | 90.3 | 94.8 | 95.9 | 96.5 | 96.5 | 96.2 | 96.1 | 89.2 | 94.3 | 95.6 | 96.3 | 96.4 | 96.1 | 95.9 | 86.5 | 92.9 | 94.7 | 95.6 | 95.7 | 95.4 | 95
Open Energy | Solar Save 4800 [240V] | 4800 W, 240 Vac Utility Interactive Inverter | 4.8 | 240 | 96 | Y | N |  | 4.1 |  |  | 100 | 263 | 400 | 0.48 | 0.96 | 1.44 | 2.4 | 3.6 | 4.8 | 86.8 | 93.5 | 95.5 | 97 | 97.2 | 97.1 | 96.4 | 85.5 | 92.9 | 95 | 96.7 | 96.9 | 96.8 | 96 | 84.5 | 91.5 | 93.9 | 95.9 | 96.2 | 96.1 | 95.1
Open Energy | Solar Save 5200 [240V] | 5200 W, 240 Vac Utility Interactive Inverter | 5.2 | 240 | 96 | Y | N |  | 4 |  |  | 100 | 280 | 400 | 0.52 | 1.04 | 1.56 | 2.6 | 3.9 | 5.2 | 89.4 | 94.8 | 96 | 96.8 | 97 | 96.8 | 96.4 | 88.6 | 94.4 | 95.7 | 96.7 | 96.8 | 96.6 | 96.2 | 87.7 | 93.1 | 94.8 | 96.1 | 96.3 | 96.1 | 95.5
OPTI International | GT 1500 [208V] | 1.5 kW, 208 Vac Utility Interactive Inverter | 1.55 | 208 | 94.5 | Y | N |  | 0.21 |  |  | 100 | 325 | 360 | 0.155 | 0.31 | 0.465 | 0.775 | 1.163 | 1.55 | 84.46 | 90.49 | 92.52 | 94.25 | 94.92 | 95.02 | 93.86 | 85.04 | 91.04 | 93.19 | 94.79 | 95.41 | 95.53 | 94.38 | 85.31 | 91.19 | 93.54 | 95.02 | 95.55 | 95.76 | 94.58
OPTI International | GT 1500 [240V] | 2 kW, 240 Vac Utility Interactive Inverter | 1.55 | 240 | 94.5 | Y | N |  | 0.32 |  |  | 100 | 325 | 360 | 0.155 | 0.31 | 0.465 | 0.775 | 1.163 | 1.55 | 84.62 | 90.46 | 92.57 | 94.42 | 95.07 | 95.25 | 93.99 | 84.89 | 90.97 | 93.04 | 94.81 | 95.51 | 95.73 | 94.42 | 85.22 | 91.38 | 93.44 | 95.12 | 95.65 | 95.93 | 94.66
OPTI International | GT 2000 [208V] | 2 kW, 208 Vac Utility Interactive Inverter | 2.06 | 208 | 95.5 | Y | N |  | 0.29 |  |  | 100 | 325 | 360 | 0.206 | 0.412 | 0.618 | 1.03 | 1.545 | 2.06 | 88.28 | 93.12 | 94.41 | 95.27 | 95.43 | 95.37 | 94.87 | 89.63 | 93.68 | 94.91 | 95.73 | 95.84 | 95.8 | 95.34 | 89.74 | 94.01 | 95.11 | 96.13 | 96.38 | 96.07 | 95.77
OPTI International | GT 2000 [240V] | 2 kW, 240 Vac Utility Interactive Inverter | 2.06 | 240 | 95 | Y | N |  | 0.36 |  |  | 100 | 325 | 360 | 0.206 | 0.412 | 0.618 | 1.03 | 1.545 | 2.06 | 86.91 | 92.14 | 93.78 | 94.94 | 95.3 | 95.37 | 94.55 | 87.84 | 92.87 | 94.26 | 95.56 | 95.79 | 95.73 | 95.09 | 88.1 | 93.05 | 94.37 | 95.71 | 96 | 95.94 | 95.28
OPTI International | GT 3000 [208V] | 3 kW, 208 Vac Utility Interactive Inverter | 3 | 208 | 95.5 | Y | N |  | 0.18 |  |  | 100 | 325 | 360 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 91.57 | 94.41 | 95.16 | 95.47 | 95.31 | 94.62 | 95.1 | 92.05 | 94.92 | 95.58 | 95.89 | 95.76 | 95.37 | 95.56 | 92.22 | 95.17 | 95.79 | 96.25 | 95.93 | 95.8 | 95.78
OPTI International | GT 3000 [240V] | 3 kW, 240 Vac Utility Interactive Inverter | 3.01 | 240 | 95.5 | Y | N |  | 0.25 |  |  | 100 | 325 | 360 | 0.301 | 0.602 | 0.903 | 1.505 | 2.258 | 3.01 | 90 | 93.9 | 94.85 | 95.4 | 95.31 | 94.83 | 94.97 | 90.64 | 94.34 | 95.34 | 95.79 | 95.87 | 95.6 | 95.49 | 91 | 94.59 | 95.44 | 95.97 | 96.01 | 95.77 | 95.65
OPTI-Solar | GT-4000 [208V] | 4 kW, 208 Vac Utility Interactive Inverter | 3.98 | 208 | 95.5 | Y | N |  | 0.18 |  |  | 100 | 325 | 360 | 0.4 | 0.8 | 1.19 | 1.99 | 2.99 | 3.98 | 90.5 | 94.3 | 95.2 | 95.4 | 95.4 | 95.2 | 95.1 | 91.6 | 94.9 | 95.6 | 96 | 96 | 95.5 | 95.7 | 91.8 | 95 | 95.8 | 96.5 | 96.3 | 95.8 | 96
OPTI-Solar | GT-4000 [240V] | 4 kW, 240 Vac Utility Interactive Inverter | 3.99 | 240 | 96 | Y | N |  | 0.25 |  |  | 100 | 325 | 360 | 0.4 | 0.8 | 1.2 | 2 | 2.99 | 3.99 | 90.6 | 94.3 | 95.2 | 95.7 | 95.7 | 95.6 | 95.4 | 91.5 | 95 | 95.8 | 96.3 | 96.3 | 96 | 96 | 91.9 | 95.2 | 96 | 96.4 | 96.5 | 96.3 | 96.1
OutBack Power Technologies, Inc. | FXR3048A | 2.5 kW, 48 Vdc Utility Interactive Inverter with battery backup | 2.56 |  | 91 | Y | N |  | 0 |  |  | 40 | 52 | 60 | 0.26 | 0.51 | 0.77 | 1.28 | 1.92 | 2.56 | 83.7 | 90.2 | 92.2 | 93.3 | 92.6 | 91.6 | 92.2 | 79.8 | 87.1 | 90 | 92 | 92 | 91.2 | 91 | 77.3 | 85.1 | 88.1 | 90.6 | 91 | 90.7 | 89.7 |  | 2018-09-17
OutBack Power Technologies, Inc. | GTFX3048 | 2.5 kW, 48 Vdc Utility Interactive Inverter with battery backup | 2.56 |  | 91 | N | N |  |  |  |  | 40 | 52 | 60 | 0.2562 | 0.5124 | 0.7686 | 1.281 | 1.922 | 2.562 | 83.8 | 90 | 92.2 | 93.4 | 92.7 | 91.5 | 92.2 | 80 | 87.2 | 90 | 92 | 92 | 91.5 | 91 | 77.2 | 84.9 | 88.2 | 90.7 | 91.1 | 90.6 | 89.8 |  | 2018-09-17
OutBack Power Technologies, Inc. | GVFX3524 | Utility Interactive Inverter | 2.96 |  | 90.5 | Y | N |  | 0 |  |  | 22 | 24 | 28 | 0.3 | 0.59 | 0.89 | 1.48 | 2.22 | 2.96 | 88.3 | 91.9 | 92.9 | 93 | 91.3 | 88.7 | 91.6 | 87.2 | 90.8 | 92.1 | 92.1 | 91 | 88.6 | 91.1 | 83.7 | 87.1 | 89.1 | 90.6 | 90 | 87.8 | 89.5 |  | 2018-09-17
OutBack Power Technologies, Inc. | VFXR3524A | 3 kW Utility Interactive Inverter | 2.96 |  | 90.5 | Y | N |  | 0 |  |  | 22 | 24 | 28 | 0.3 | 0.59 | 0.89 | 1.48 | 2.22 | 2.96 | 88.3 | 91.9 | 92.9 | 93 | 91.3 | 88.7 | 91.6 | 87.2 | 90.8 | 92.1 | 92.1 | 91 | 88.6 | 91.1 | 83.7 | 87.1 | 89.1 | 90.6 | 90 | 87.8 | 89.5 |  | 2018-09-17
OutBack Power Technologies, Inc. | GVFX3648 | 3 kW, 48 Vdc Utility Interactive Inverter (with battery backup | 3.037 |  | 91 | N | N |  | 0 |  |  | 40 | 51.2 | 60 | 0.3037 | 0.6075 | 0.9112 | 1.519 | 2.278 | 3.037 | 88 | 92.2 | 93.2 | 94 | 93 | 91.3 | 92.9 | 82.1 | 88.5 | 90.7 | 91.8 | 91.6 | 89.7 | 90.9 | 80.4 | 86.1 | 87.9 | 90.3 | 90.5 | 88.4 | 89.4 |  | 2018-09-17
OutBack Power Technologies, Inc. | VFXR3648A | 4 kW, 48 Vdc Utility Interactive Inverter (with battery backup | 3.037 |  | 91 | Y | N |  | 0 |  |  | 40 | 51.2 | 60 | 0.3 | 0.61 | 0.91 | 1.52 | 2.28 | 3.04 | 88 | 92.2 | 93.5 | 94 | 93 | 91.2 | 92.9 | 82.2 | 88.5 | 90.7 | 91.8 | 91.6 | 89.7 | 90.9 | 80.3 | 86.1 | 87.9 | 90.3 | 90.4 | 88.3 | 89.4 |  | 2018-09-17
OutBack Power Technologies, Inc. | GS4048A | Utility Interactive Inverter with battery backup | 3.6 |  | 92.5 | Y | N |  | 0.1 |  |  | 44 | 48 | 56 | 0.36 | 0.72 | 1.08 | 1.8 | 2.7 | 3.6 | 88.3 | 92.6 | 94.1 | 94.4 | 93.2 | 91.2 | 93.3 | 87.1 | 91.5 | 92.9 | 93.3 | 93 | 90.8 | 92.6 | 84 | 89 | 90.9 | 92.1 | 91.9 | 90.2 | 91.3 |  | 2018-09-17
OutBack Power Technologies, Inc. | SBX5048-120/240 [240V] | 5.0kW, 240Vac Utility Interactive Multimode Inverter | 4.985 | 240 | 94 | Y | N |  | 24.85 |  |  | 250 | 420 | 550 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 85.9112 | 91.8786 | 93.404 | 94.206 | 94.0833 | 93.7751 | 93.575 | 87.0418 | 92.4308 | 94.1918 | 94.8976 | 95.0953 | 94.8942 | 94.4799 | 85.3624 | 91.926 | 93.5091 | 94.4779 | 94.7418 | 94.6173 | 94.0163 | 2018-09-17
OutBack Power Technologies, Inc. | GS8048A | Utility Interactive Inverter with battery backup | 7.2 |  | 92.5 | Y | N |  | 0.1 |  |  | 44 | 48 | 56 | 0.72 | 1.44 | 2.16 | 3.6 | 5.4 | 7.2 | 92.6 | 94.4 | 93.7 | 94.4 | 93 | 90.4 | 93.3 | 91.5 | 93.4 | 93 | 93.3 | 92.7 | 90.8 | 92.7 | 89 | 91.6 | 92.2 | 92.1 | 91.5 | 89.9 | 91.5 |  | 2018-09-17
OutBack Power Technologies, Inc. | GS8048 | Utility Interactive Inverter with battery backup | 7.65 |  | 90 | N | N |  | 0 |  |  | 40 | 52 | 64 | 0.76 | 1.53 | 2.29 | 3.82 | 5.74 | 7.65 | 87.4 | 91.8 | 92 | 93.3 | 92 | 90.5 | 92 | 83.4 | 88.4 | 89.2 | 90.4 | 89.7 | 88.3 | 89.4 | 79.9 | 87 | 88.5 | 89.7 | 89.2 | 88.3 | 88.7 |  | 2018-09-17
OutBack Power Technologies, Inc. | PHXL480-10k [480V] | 10 kW, 480 Vac, 3 phase Utility Interactive Inverter | 9.975 | 480 | 97.5 | N | N | Multiple Listing of HiQ Solar, Inc., TSXL480-10k. |  |  |  | 450 | 750 | 850 | 0.9975 | 1.995 | 2.9925 | 4.9875 | 7.4812 | 9.975 | 94.1157 | 96.7771 | 97.3429 | 97.7271 | 97.6957 | 97.5171 | 97.4619 | 94.11 | 96.8457 | 97.6443 | 98.1614 | 98.22 | 98.14 | 97.9015 | 93.1871 | 96.46 | 97.4557 | 98.1029 | 98.2386 | 98.2 | 97.8232 | 2019-02-15
Perfect Galaxy | AE-30-60-PV-A [480V] | 30 kW, 480 Vac, 3-phase Utility Interactive Inverter | 30 | 480 | 93 | Y | N |  | 59 |  |  | 330 | 410 | 480 | 3 | 6 | 9 | 15 | 22.5 | 30 | 82.9 | 89.8 | 92 | 93.5 | 94.2 | 94.3 | 93.1 | 83.5 | 89.7 | 91.9 | 93.5 | 93.9 | 93.8 | 93 | 81 | 88.6 | 91 | 93 | 93.5 | 93.6 | 92.3
Perfect Galaxy | AE-30-60-PV-D [208V] | 30 kW, 208 Vac, 3-phase Utility Interactive Inverter | 30 | 208 | 92.5 | Y | N |  | 54 |  |  | 330 | 410 | 480 | 3 | 6 | 9 | 15 | 22.5 | 30 | 82.1 | 89.2 | 91.4 | 93.1 | 93.4 | 93.2 | 92.5 | 81.5 | 88.7 | 91.2 | 92.8 | 93.2 | 93 | 92.1 | 85.2 | 90.5 | 92.5 | 93.5 | 93.8 | 93.5 | 93.1
Perfect Galaxy | AE-30-60-PV-E [240V] | 30 kW, 240 Vac, 1-phase Utility Interactive Inverter | 30 | 240 | 93 | Y | N |  | 68 |  |  | 330 | 410 | 480 | 3 | 6 | 9 | 15 | 22.5 | 30 | 85.1 | 90.7 | 92.6 | 93.7 | 93.8 | 93.5 | 93.1 | 84.7 | 90.3 | 92.2 | 93.4 | 93.4 | 92.9 | 92.8 | 83.6 | 89.8 | 91.7 | 93 | 93.1 | 92.8 | 92.4
Perfect Galaxy | AE-30-60-PV-F [240V] | 30 kW, 240 Vac, 3-phase Utility Interactive Inverter | 30 | 240 | 94.5 | Y | N |  | 59 |  |  | 340 | 375 | 480 | 3 | 6 | 9 | 15 | 22.5 | 30 | 91.6 | 92.5 | 93.9 | 95.2 | 95.5 | 95.6 | 94.9 | 91.8 | 91.9 | 93.6 | 95 | 95.3 | 95.4 | 94.7 | 89.9 | 91.2 | 92.9 | 94.5 | 94.9 | 95 | 94.2
Perfect Galaxy | PVS-30 [208V] | 30 kW, 208 Vac, 3-phase Utility Interactive Inverter | 30 | 208 | 95 | Y | N |  | 75.62 |  |  | 305 | 350 | 480 | 3 | 6 | 9 | 15 | 22.5 | 30 | 88.8 | 93.5 | 94.8 | 95.7 | 95.6 | 95.4 | 95.1 | 88 | 93.1 | 94.7 | 95.4 | 95.5 | 95.3 | 95 | 87 | 92.4 | 94.2 | 95 | 95.1 | 95.1 | 94.5
Perfect Galaxy | PVS-30 [240V] | 30 kW, 240 Vac, 3-phase Utility Interactive Inverter | 30 | 240 | 95 | Y | N |  | 64.58 |  |  | 305 | 355 | 480 | 3 | 6 | 9 | 15 | 22.5 | 30 | 88.2 | 93.8 | 95 | 96 | 95.8 | 95.6 | 95.3 | 88.2 | 93.3 | 94.8 | 95.7 | 95.7 | 95.6 | 95.1 | 86.1 | 92.5 | 94.4 | 95.3 | 95.5 | 95.2 | 94.8
Perfect Galaxy | PVS-30 [480V] | 30 kW, 480 Vac, 3-phase Utility Interactive Inverter | 30 | 480 | 95 | Y | N |  | 72.3 |  |  | 305 | 350 | 480 | 3 | 6 | 9 | 15 | 22.5 | 30 | 88.4 | 93.5 | 94.6 | 95.6 | 95.6 | 95.3 | 95.1 | 87.7 | 93.1 | 94.6 | 95.4 | 95.5 | 95.3 | 95 | 86.3 | 92.1 | 93.9 | 94.9 | 95 | 94.8 | 94.3
Perfect Galaxy | AE-50-60-PV-D [208V] | 50 kW, 208 Vac, 3-phase Utility Interactive Inverter | 50 | 208 | 94.5 | Y | N |  | 90 |  |  | 327.2 | 410.9 | 474.9 | 5 | 10 | 15 | 25 | 37.5 | 50 | 88.2 | 93 | 94.4 | 95.4 | 95.2 | 95.2 | 94.7 | 86.7 | 92 | 93.8 | 94.9 | 94.8 | 94.8 | 94.2 | 85.8 | 91.2 | 93.2 | 94.6 | 94.5 | 94.6 | 93.8
Perfect Galaxy | AE-50-60-PV-F [240V] | 50 kW, 240 Vac, 3-phase Utility Interactive Inverter | 50 | 240 | 93 | Y | N |  | 68 |  |  | 340 | 430 | 480 | 5 | 10 | 15 | 25 | 37.5 | 50 | 84.3 | 90.6 | 92.7 | 94.4 | 94.4 | 94.5 | 93.6 | 81.8 | 89.1 | 91.8 | 93.6 | 93.8 | 94 | 92.8 | 80.2 | 88.2 | 91 | 93.2 | 93.5 | 93.8 | 92.3
Perfect Galaxy | PVS-50 [208V] | 50 kW, 208 Vac, 3-phase Utility Interactive Inverter | 50 | 208 | 95.5 | Y | N |  | 76.5 |  |  | 305 | 350 | 480 | 5 | 10 | 15 | 25 | 37.5 | 50 | 90.4 | 93.8 | 95.4 | 95.9 | 95.9 | 95.7 | 95.5 | 89.7 | 94.1 | 95.2 | 95.8 | 95.8 | 95.6 | 95.4 | 88.7 | 93 | 94.5 | 95.3 | 95.4 | 95.3 | 94.9
Perfect Galaxy | PVS-50 [240V] | 50 kW, 240 Vac, 3-phase Utility Interactive Inverter | 50 | 240 | 95.5 | Y | N |  | 93.97 |  |  | 310 | 365 | 480 | 5 | 10 | 15 | 25 | 37.5 | 50 | 90.8 | 95 | 95.9 | 96.2 | 96 | 95.5 | 95.7 | 90.4 | 94.8 | 95.3 | 96 | 95.7 | 95.5 | 95.5 | 89.6 | 93.3 | 95.2 | 95.5 | 95.4 | 95 | 95.1
Perfect Galaxy | PVS-50 [480V] | 50 kW, 480 Vac, 3-phase Utility Interactive Inverter | 50 | 480 | 95.5 | Y | N |  | 76.5 |  |  | 305 | 350 | 480 | 5 | 10 | 15 | 25 | 37.5 | 50 | 90.5 | 95 | 95.9 | 96.3 | 96.4 | 96 | 96 | 89.4 | 94.7 | 95.6 | 96.1 | 96.1 | 95.9 | 95.7 | 89.5 | 94.2 | 95.1 | 95.8 | 95.6 | 95.4 | 95.3
Perfect Galaxy | PVS-50-S-MT [208V] | 50 kW, 208 Vac, 3-phase Utility Interactive Inverter | 50 | 208 | 95.5 | Y | N |  | 81 | 50 | 81 | 265 | 320 | 480 | 5 | 10 | 15 | 25 | 37.5 | 50 | 91.6 | 95.4 | 96.1 | 96.3 | 96.1 | 95.7 | 95.9 | 91.3 | 95.3 | 96 | 96.2 | 96 | 95.6 | 95.8 | 89 | 94.8 | 95.4 | 95.5 | 95.5 | 95.1 | 95.2
Perfect Galaxy | PVS-50-S-MT [240V] | 50 kW, 240 Vac, 3-phase Utility Interactive Inverter | 50 | 240 | 95.5 | Y | N |  | 78 | 50 | 78 | 265 | 320 | 480 | 5 | 10 | 15 | 25 | 37.5 | 50 | 91.6 | 95.3 | 96.1 | 96.2 | 95.9 | 95.6 | 95.8 | 91 | 95.1 | 95.8 | 96.2 | 95.8 | 95.5 | 95.7 | 87.8 | 94.7 | 95.3 | 95.7 | 95.4 | 95.2 | 95.1
Perfect Galaxy | PVS-50-S-MT [480V] | 50 kW, 480 Vac, 3-phase Utility Interactive Inverter | 50 | 480 | 95.5 | Y | N |  | 78 | 50 | 78 | 265 | 320 | 480 | 5 | 10 | 15 | 25 | 37.5 | 50 | 92.1 | 95.3 | 96 | 96.2 | 96 | 95.7 | 95.9 | 91.5 | 95 | 95.7 | 96.1 | 95.9 | 95.6 | 95.7 | 88.7 | 94.3 | 95.3 | 95.6 | 95.4 | 95.2 | 95.1
Perfect Galaxy | AE-50-60-PV-A [480V] | 50 kW, 480 Vac, 3-phase Utility Interactive Inverter | 50.25 | 480 | 93 | Y | N |  | 100.8 |  |  | 330 | 420 | 480 | 5.03 | 10.05 | 15.08 | 25.13 | 37.69 | 50.25 | 81.1 | 88.9 | 91.7 | 93.7 | 94.6 | 94.7 | 93.2 | 79.9 | 88.2 | 91.1 | 93.3 | 94.3 | 94.7 | 92.8 | 79.3 | 87.7 | 90.6 | 93 | 93.9 | 94.2 | 92.5
Perfect Galaxy | AE-75-60-PV-A [480V] | 75 kW, 480 Vac, 3-phase Utility Interactive Inverter | 75 | 480 | 95.5 | Y | N |  | 99 |  |  | 318.9 | 405.6 | 479.5 | 7.5 | 15 | 22.5 | 37.5 | 56.25 | 75 | 91.1 | 94.4 | 95.5 | 96.1 | 96 | 95.9 | 95.7 | 90.3 | 93.9 | 95.1 | 95.8 | 95.6 | 95.5 | 95.3 | 89.5 | 93.4 | 94.6 | 95.5 | 95.4 | 95.3 | 95
Perfect Galaxy | AE-75-60-PV-D [208V] | 75 kW, 208 Vac, 3-phase Utility Interactive Inverter | 75 | 208 | 95.5 | Y | N |  | 99 |  |  | 330 | 415 | 480 | 7.5 | 15 | 22.5 | 37.5 | 56.25 | 75 | 90.9 | 94.4 | 95.5 | 96.1 | 96 | 95.9 | 95.7 | 90.5 | 94 | 95.1 | 95.9 | 95.7 | 95.6 | 95.4 | 89.6 | 93.6 | 94.9 | 95.6 | 95.5 | 95.4 | 95.1
Perfect Galaxy | PVS-75 [208V] | 73 kW, 208 Vac, 3-phase Utility Interactive Inverter | 75 | 208 | 96 | Y | N |  | 65.36 |  |  | 315 | 365 | 480 | 7.5 | 15 | 22.5 | 37.5 | 56.25 | 75 | 91 | 95.5 | 96.1 | 96.6 | 96.4 | 96.1 | 96.1 | 90.9 | 95.3 | 95.9 | 96.4 | 96.3 | 96 | 96 | 89.7 | 94.6 | 95.4 | 96.1 | 95.9 | 95.7 | 95.5
Perfect Galaxy | PVS-75 [240V] | 74 kW, 240 Vac, 3-phase Utility Interactive Inverter | 75 | 240 | 96 | Y | N |  | 71.84 |  |  | 315 | 365 | 480 | 7.5 | 15 | 22.5 | 37.5 | 56.25 | 75 | 92.3 | 95.5 | 96.3 | 96.6 | 96.6 | 96.3 | 96.3 | 91.2 | 95.5 | 96 | 96.5 | 96.5 | 96.2 | 96.1 | 90.6 | 94.8 | 95.4 | 96.1 | 96 | 96 | 95.7
Perfect Galaxy | PVS-75 [480V] | 75 kW, 480 Vac, 3-phase Utility Interactive Inverter | 75 | 480 | 96 | Y | N |  | 69.5 |  |  | 315 | 365 | 480 | 7.5 | 15 | 22.5 | 37.5 | 56.25 | 75 | 92.6 | 95.6 | 96.3 | 96.7 | 96.6 | 96.3 | 96.3 | 92.1 | 95.3 | 96 | 96.5 | 96.4 | 96.2 | 96.2 | 91.3 | 94.9 | 95.7 | 96.1 | 96.1 | 96 | 95.8
Perfect Galaxy | AE-100-60-PV-A [480V] | 100 kW, 480 Vac, 3-phase Utility Interactive Inverter | 100 | 480 | 94.5 | Y | N |  | 97.7 |  |  | 330 | 410 | 470 | 10 | 20 | 30 | 50 | 75 | 100 | 88.7 | 93.1 | 94.6 | 95.6 | 95.8 | 95.7 | 95.2 | 87.3 | 92.3 | 93.9 | 95 | 95.3 | 95.2 | 94.6 | 86.6 | 91.8 | 93.6 | 94.8 | 95.1 | 95.1 | 94.4
Perfect Galaxy | AE-100-60-PV-A-HE [480V] | 100 kW, 480 Vac, 3-phase Utility Interactive Inverter | 100 | 480 | 95.5 | Y | N |  | 97.7 |  |  | 330 | 400 | 480 | 10 | 20 | 30 | 50 | 75 | 100 | 93.2 | 95.5 | 96 | 96.1 | 95.6 | 95.3 | 95.7 | 93.3 | 95.3 | 95.8 | 95.9 | 95.9 | 95.2 | 95.7 | 92.9 | 94.7 | 95.5 | 95.4 | 95.2 | 94.8 | 95.2
Perfect Galaxy | AE-100-60-PV-D [208V] | 100 kW, 208 Vac, 3-phase Utility Interactive Inverter | 100 | 208 | 94.5 | Y | N |  | 91.5 |  |  | 330 | 402 | 470 | 10 | 20 | 30 | 50 | 75 | 100 | 89.3 | 94.1 | 94.5 | 95.6 | 95.3 | 95.1 | 95 | 88.6 | 92.9 | 94.2 | 95 | 95.1 | 94.9 | 94.6 | 89.7 | 92.8 | 94.2 | 94.7 | 94.7 | 94.5 | 94.4
Perfect Galaxy | AE-100-60-PV-F [240V] | 100 kW, 240 Vac, 3-phase Utility Interactive Inverter | 100 | 240 | 95 | Y | N |  | 97.7 |  |  | 330 | 408 | 480 | 10 | 20 | 30 | 50 | 75 | 100 | 90.2 | 93.9 | 94.9 | 95.8 | 95.7 | 95.5 | 95.3 | 89.3 | 93.2 | 94.7 | 95.3 | 95.4 | 95.2 | 94.9 | 88.8 | 93.2 | 94.2 | 95 | 95.3 | 94.9 | 94.7
Perfect Galaxy | PVS-100 [208V] | 98 kW, 208 Vac, 3-phase Utility Interactive Inverter | 100 | 208 | 96 | Y | N |  | 62.34 |  |  | 315 | 365 | 480 | 10 | 20 | 30 | 50 | 75 | 100 | 92.6 | 95.7 | 96.4 | 96.6 | 96.5 | 96.2 | 96.3 | 92.4 | 95.5 | 96.2 | 96.5 | 96.4 | 96.1 | 96.2 | 91.3 | 94.9 | 95.7 | 96.1 | 96.1 | 95.8 | 95.8
Perfect Galaxy | PVS-100 [240V] | 99 kW, 240 Vac, 3-phase Utility Interactive Inverter | 100 | 240 | 96 | Y | N |  | 61.57 |  |  | 315 | 365 | 480 | 10 | 20 | 30 | 50 | 75 | 100 | 91.1 | 95.3 | 96.1 | 96.5 | 96.5 | 96.2 | 96.1 | 90.6 | 94.9 | 95.9 | 96.4 | 96.3 | 96.1 | 96 | 89.4 | 94.3 | 95.4 | 96 | 96 | 95.8 | 95.6
Perfect Galaxy | PVS-100 [480V] | 100 kW, 480 Vac, 3-phase Utility Interactive Inverter | 100 | 480 | 96 | Y | N |  | 66.13 |  |  | 315 | 365 | 480 | 10 | 20 | 30 | 50 | 75 | 100 | 93.2 | 96.1 | 96.5 | 96.7 | 96.5 | 96.1 | 96.4 | 93.6 | 95.9 | 96.4 | 96.5 | 96.4 | 96 | 96.3 | 93 | 95.6 | 96.2 | 96.3 | 96.1 | 95.8 | 96
Perfect Galaxy | SDMS0100208LNIU [208V] | 100 kW, 208 Vac, 3-phase Inverter with combiner | 100 | 208 | 95 | Y | N |  | 60.38 |  |  | 300 | 430 | 480 | 10 | 20 | 30 | 50 | 75 | 100 | 91.5 | 94.2 | 95.2 | 95.5 | 95.2 | 94.8 | 95 | 89.5 | 92.3 | 95 | 95.8 | 95.6 | 95.3 | 95.1 | 90.1 | 93.5 | 94.7 | 95.9 | 95.8 | 95.5 | 95.3
Perfect Galaxy | SDMS0100240LNIU [240V] | 100 kW, 240 Vac, 3-phase Inverter with combiner | 100 | 240 | 95 | Y | N |  | 61.79 |  |  | 300 | 430 | 480 | 10 | 20 | 30 | 50 | 75 | 100 | 90.1 | 93.5 | 94.6 | 95.1 | 95.1 | 94.7 | 94.7 | 88.1 | 91.6 | 94.4 | 95.4 | 95.5 | 95.2 | 94.8 | 88.7 | 92.8 | 94.2 | 95.5 | 95.7 | 95.3 | 95
Perfect Galaxy | SDMS0100480LNIU [480V] | 100 kW, 480 Vac, 3-phase Inverter with combiner | 100 | 480 | 95 | Y | N |  | 63.88 |  |  | 300 | 430 | 480 | 10 | 20 | 30 | 50 | 75 | 100 | 89.5 | 93.4 | 94.4 | 95.1 | 95 | 94.7 | 94.6 | 87.6 | 91.5 | 94.3 | 95.3 | 95.4 | 95.2 | 94.7 | 88.1 | 92.7 | 94 | 95.4 | 95.6 | 95.4 | 94.9
Perfect Galaxy | PVS-110-S-MT [208V] | 110 kW, 208 Vac, 3-phase Utility Interactive Inverter | 110 | 208 | 95 | Y | N |  | 72.5 |  |  | 265 | 320 | 480 | 11 | 22 | 33 | 55 | 82.5 | 110 | 92.6 | 95.4 | 95.8 | 95.9 | 95.6 | 94.8 | 95.5 | 91.9 | 95 | 95.5 | 95.7 | 95.4 | 94.7 | 95.3 | 89.8 | 93.7 | 94.6 | 95 | 94.8 | 94.1 | 94.5
Perfect Galaxy | PVS-110-S-MT [240V] | 110 kW, 240 Vac, 3-phase Utility Interactive Inverter | 110 | 240 | 95.5 | Y | N |  | 70.6 |  |  | 265 | 320 | 480 | 11 | 22 | 33 | 55 | 82.5 | 110 | 93 | 95.6 | 96.1 | 96.1 | 95.8 | 95.2 | 95.8 | 92.3 | 95.2 | 95.8 | 95.8 | 95.6 | 95 | 95.5 | 90.4 | 94.1 | 94.9 | 95.2 | 95 | 94.5 | 94.8
Perfect Galaxy | PVS-110-S-MT [480V] | 110 kW, 480 Vac, 3-phase Utility Interactive Inverter | 110 | 480 | 95.5 | Y | N |  | 74.3 |  |  | 265 | 320 | 480 | 11 | 22 | 33 | 55 | 82.5 | 110 | 93.2 | 95.8 | 96.1 | 96.3 | 96 | 95.5 | 95.9 | 92.6 | 95.4 | 95.8 | 96 | 95.8 | 95.3 | 95.7 | 90.9 | 94.3 | 95 | 95.3 | 95.3 | 94.8 | 95
Perfect Galaxy | AE-135-60-PV-A [480V] | 135 kW, 480 Vac, 3-phase Utility Interactive Inverter | 135 | 480 | 95.5 | Y | N |  | 98 |  |  | 330 | 415 | 470 | 13.5 | 27 | 40.5 | 67.5 | 101.3 | 135 | 90.7 | 94.2 | 95.4 | 96.1 | 96.1 | 95.9 | 95.7 | 90 | 93.8 | 95 | 95.6 | 95.7 | 95.5 | 95.3 | 89.4 | 93.4 | 94.7 | 95.4 | 95.5 | 95.4 | 95
Perfect Galaxy | AE-135-60-PV-D [208V] | 135 kW, 208 Vac, 3-phase Utility Interactive Inverter | 135 | 208 | 95 | Y | N |  | 96 |  |  | 330 | 415 | 470 | 13.5 | 27 | 40.5 | 67.5 | 101.3 | 135 | 91.6 | 94.9 | 95.6 | 96 | 95.9 | 95.5 | 95.7 | 91.1 | 94.5 | 95.4 | 95.9 | 95.7 | 95.3 | 95.4 | 88.7 | 92.7 | 94.2 | 95 | 95.1 | 94.9 | 94.6
Perfect Galaxy | PVS-135 [208V] | 135 kW, 208 Vac, 3-phase Utility Interactive Inverter | 135 | 208 | 96 | Y | N |  | 63.12 |  |  | 310 | 355 | 480 | 13.5 | 27 | 40.5 | 67.5 | 101.3 | 135 | 92.9 | 95.6 | 95.8 | 96.5 | 96.4 | 96.1 | 96.1 | 92.5 | 95.4 | 96.1 | 96.4 | 96.2 | 95.9 | 96 | 91 | 94 | 95 | 95.7 | 95.8 | 95.7 | 95.4
Perfect Galaxy | PVS-135 [240V] | 135 kW, 240 Vac, 3-phase Utility Interactive Inverter | 135 | 240 | 96 | Y | N |  | 63.7 |  |  | 320 | 360 | 480 | 13.5 | 27 | 40.5 | 67.5 | 101.3 | 135 | 92.4 | 95.6 | 95.8 | 96.6 | 96.6 | 96.3 | 96.3 | 92 | 95.3 | 96 | 96.4 | 96.4 | 96.2 | 96.1 | 91 | 94 | 95 | 95.7 | 95.8 | 95.7 | 95.4
Perfect Galaxy | PVS-135 [480V] | 135 kW, 480 Vac, 3-phase Utility Interactive Inverter | 135 | 480 | 96 | Y | N |  | 63.67 |  |  | 310 | 355 | 480 | 13.5 | 27 | 40.5 | 67.5 | 101.3 | 135 | 92.9 | 95.8 | 96.5 | 96.7 | 96.5 | 96.2 | 96.4 | 92.4 | 95.5 | 96.2 | 96.4 | 96.4 | 96.1 | 96.1 | 90.8 | 94.7 | 95.6 | 96 | 95.9 | 95.7 | 95.6
Perfect Galaxy | PVS-210-S [208V] | 210 kW, 208 Vac, 3-phase Utility Interactive Inverter | 210 | 208 | 95.5 | Y | N |  | 160.8 |  |  | 265 | 318 | 480 | 21 | 42 | 63 | 105 | 157.5 | 210 | 93.5 | 95.7 | 96.2 | 96.2 | 96.1 | 95.5 | 96 | 93.1 | 95.5 | 96 | 96 | 95.6 | 95.2 | 95.6 | 91.9 | 94.6 | 95.2 | 95.3 | 95 | 94.6 | 94.9
Perfect Galaxy | PVS-210-S [240V] | 210 kW, 240 Vac, 3-phase Utility Interactive Inverter | 210 | 240 | 95.5 | Y | N |  | 112.9 |  |  | 265 | 318 | 480 | 21 | 42 | 63 | 105 | 157.5 | 210 | 93.2 | 95.7 | 96.2 | 96.3 | 96.1 | 95.6 | 96 | 92.7 | 95.5 | 95.9 | 96 | 95.7 | 95.3 | 95.7 | 91.6 | 94.4 | 95.2 | 95.2 | 95.1 | 94.6 | 95
Perfect Galaxy | PVS-210-S [480V] | 210 kW, 480 Vac, 3-phase Utility Interactive Inverter | 210 | 480 | 95.5 | Y | N |  | 189.8 |  |  | 265 | 318 | 480 | 21 | 42 | 63 | 105 | 157.5 | 210 | 92 | 95.2 | 95.8 | 96.2 | 96 | 95.7 | 95.8 | 91.7 | 94.9 | 95.7 | 95.9 | 95.5 | 95.4 | 95.4 | 90.8 | 94.1 | 95 | 95.3 | 95.1 | 94.8 | 94.9
Perfect Galaxy | AE-225-60-PV-A [480V] | 225 kW, 480 Vac, 3-phase Utility Interactive Inverter | 225 | 480 | 94.5 | Y | N |  | 114 |  |  | 330 | 430 | 480 | 22.5 | 45 | 67.5 | 112.5 | 168.8 | 225 | 90.2 | 93.5 | 94.8 | 95.5 | 95.5 | 95.4 | 95.1 | 89 | 93 | 94.3 | 95 | 95.1 | 94.8 | 94.6 | 88.5 | 92.7 | 94 | 94.8 | 95 | 94.6 | 94.4
Perfect Galaxy | AE-225-60-PV-D [208V] | 225 kW, 208 Vac, 3-phase Utility Interactive Inverter | 225 | 208 | 95.5 | Y | N |  | 180 |  |  | 330 | 415 | 470 | 22.5 | 45 | 67.5 | 112.5 | 168.8 | 225 | 92.2 | 95 | 95.7 | 96.1 | 95.9 | 95.5 | 95.7 | 93.2 | 94.7 | 95.5 | 95.8 | 95.7 | 95.3 | 95.5 | 91.8 | 94.4 | 95.2 | 95.6 | 95.5 | 95.2 | 95.2
Perfect Galaxy | EQX0250UV480TN (P) | 250 kW, Utility Interactive Inverter | 250 |  | 96.5 | Y | N |  | 104.6 |  |  | 500 | 600 | 800 | 25 | 50 | 75 | 125 | 187.5 | 250 | 94.8 | 96.4 | 96.8 | 97 | 96.9 | 96.07 | 96.8 | 94.4 | 96.1 | 96.6 | 96.8 | 96.8 | 96.6 | 96.6 | 93.4 | 95.5 | 96.1 | 96.6 | 96.5 | 96.3 | 96.3
Perfect Galaxy | PVS-250 | 250 kW, 3-phase Inverter for Medium Voltage Transformer | 250 |  | 95.5 | Y | N |  | 151.8 |  |  | 330 | 368 | 480 | 25 | 50 | 75 | 125 | 187.5 | 250 | 93.8 | 95.4 | 96 | 96.2 | 96 | 95.4 | 95.9 | 93.3 | 95.2 | 95.8 | 96 | 95.8 | 95.2 | 95.7 | 92.1 | 94.6 | 95.3 | 95.6 | 95.2 | 94.7 | 95.1
Perfect Galaxy | PVS-250 [208V] | 250 kW, 208 Vac, 3-phase Utility Interactive Inverter | 250 | 208 | 96 | Y | N |  | 105.1 | 250 | 105.1 | 320 | 365 | 480 | 25 | 50 | 75 | 125 | 187.5 | 250 | 95.1 | 96.3 | 96.5 | 96.4 | 96.5 | 96 | 96.4 | 94.4 | 95.9 | 96.4 | 96.3 | 96.3 | 95.8 | 96.2 | 93.7 | 95.9 | 96.2 | 95.9 | 95.8 | 95.3 | 95.8
Perfect Galaxy | PVS-250 [240V] | 250 kW, 240 Vac, 3-phase Utility Interactive Inverter | 250 | 240 | 96 | Y | N |  | 100 | 250 | 100 | 322 | 365 | 480 | 25 | 50 | 75 | 125 | 187.5 | 250 | 92.5 | 95.8 | 96.4 | 96.6 | 96.5 | 96.2 | 96.3 | 92.3 | 95.6 | 96.2 | 96.4 | 96.3 | 96 | 96.1 | 91.9 | 95.1 | 95.9 | 96 | 95.9 | 95.6 | 95.7
Perfect Galaxy | PVS-250 [480V] | 250 kW, 480 Vac, 3-phase Utility Interactive Inverter | 250 | 480 | 96 | Y | N |  | 119.7 | 250 | 119.7 | 320 | 365 | 480 | 25 | 50 | 75 | 125 | 187.5 | 250 | 93.4 | 96 | 96.4 | 96.6 | 96.5 | 96 | 96.3 | 93.1 | 95.7 | 96.2 | 96.3 | 96.2 | 95.7 | 96 | 92.3 | 94.9 | 95.8 | 95.9 | 95.7 | 95.2 | 95.5
Perfect Galaxy | PVS-375 [480V] | 375 kW, 480 Vac, 3-phase Utility Interactive Inverter | 375 | 480 | 95.5 | Y | N |  | 123.5 |  |  | 320 | 365 | 480 | 37.5 | 75 | 112.5 | 187.5 | 281.3 | 375 | 92.6 | 95.4 | 96 | 96.3 | 96.2 | 95.8 | 96 | 92.1 | 95.1 | 95.7 | 96 | 95.8 | 95.6 | 95.7 | 90.9 | 94.6 | 95 | 95.5 | 95.3 | 95.1 | 95.1
Perfect Galaxy | AE-500-60-PV-A [480V] | 500 kW, 480 Vac, 3-phase Utility Interactive Inverter | 500 | 480 | 95 | Y | N |  | 208 |  |  | 330 | 405 | 480 | 50 | 100 | 150 | 250 | 375 | 500 | 93.2 | 94.9 | 95.7 | 95.8 | 95.6 | 95.2 | 95.5 | 91.8 | 94.5 | 95.4 | 95.5 | 95.4 | 94.9 | 95.2 | 91.3 | 93.7 | 94.6 | 95.1 | 95 | 94.8 | 94.8
Perfect Galaxy | EQX0500US200X-N | 500 kW, 3-phase Inverter, N for ground type | 500 |  | 96 | Y | N |  | 171.5 |  |  | 320 | 360 | 480 | 50 | 100 | 150 | 250 | 375 | 500 | 93.9 | 96.1 | 96.5 | 96.6 | 96.1 | 95.6 | 96.2 | 93.6 | 96 | 96.5 | 96.5 | 96.1 | 95.6 | 96.1 | 92.7 | 95.5 | 96.1 | 96.2 | 95.9 | 95.5 | 95.8
Perfect Galaxy | EQX0500US200X-P | 500 kW, 3-phase Inverter, P for ground type | 500 |  | 96 | Y | N |  | 171.5 |  |  | 320 | 360 | 480 | 50 | 100 | 150 | 250 | 375 | 500 | 93.9 | 96.1 | 96.5 | 96.6 | 96.1 | 95.6 | 96.2 | 93.6 | 96 | 96.5 | 96.5 | 96.1 | 95.6 | 96.1 | 92.7 | 95.5 | 96.1 | 96.2 | 95.9 | 95.5 | 95.8
Perfect Galaxy | EQX0500US480T-N | 500 kW, 3-phase Inverter, N for ground type | 500 |  | 96 | Y | N |  | 116.5 |  |  | 320 | 360 | 480 | 50 | 100 | 150 | 250 | 375 | 500 | 92 | 95.4 | 96.2 | 96.7 | 96.6 | 96.4 | 96.3 | 91.7 | 95.3 | 96.1 | 96.6 | 96.6 | 96.5 | 96.3 | 90.8 | 94.8 | 95.8 | 96.4 | 96.4 | 96.3 | 96
Perfect Galaxy | EQX0500US480T-P | 500 kW, 3-phase Inverter, P for ground type | 500 |  | 96 | Y | N |  | 116.5 |  |  | 320 | 360 | 480 | 50 | 100 | 150 | 250 | 375 | 500 | 92 | 95.4 | 96.2 | 96.7 | 96.6 | 96.4 | 96.3 | 91.7 | 95.3 | 96.1 | 96.6 | 96.6 | 96.5 | 96.3 | 90.8 | 94.8 | 95.8 | 96.4 | 96.4 | 96.3 | 96
Perfect Galaxy | EQX0500UV320XP(N) | 500 kW Utility Interactive Inverter | 500 |  | 97 | Y | N |  | 96 |  |  | 515 | 590 | 800 | 50 | 100 | 150 | 250 | 375 | 500 | 94.8 | 96.8 | 97.2 | 97.4 | 97.1 | 96.5 | 97 | 94.3 | 96.4 | 97 | 97.3 | 97 | 96.5 | 96.9 | 93.1 | 95.6 | 96.5 | 96.9 | 96.7 | 96.2 | 96.5
Perfect Galaxy | PVS-500 | 500 kW, 3-phase Inverter for Medium Voltage Transformer | 500 |  | 95.5 | Y | N |  | 2630 |  |  | 320 | 365 | 480 | 50 | 100 | 150 | 250 | 375 | 500 | 93.9 | 95.7 | 96.1 | 96 | 95.4 | 94.6 | 95.5 | 93.3 | 95.4 | 95.8 | 95.8 | 95.2 | 94.5 | 95.3 | 92.9 | 94.9 | 95.4 | 95.5 | 94.9 | 94.2 | 95
Perfect Galaxy | PVS-500 [480V] | 500 kW, 480 Vac, 3-phase Utility Interactive Inverter | 500 | 480 | 96 | Y | N |  | 131.1 |  |  | 315 | 365 | 480 | 50 | 100 | 150 | 250 | 375 | 500 | 92.9 | 95.7 | 96.2 | 96.5 | 96.4 | 96 | 96.2 | 92.4 | 95.4 | 96.1 | 96.3 | 96.2 | 95.8 | 96 | 91.8 | 95 | 95.7 | 96 | 95.8 | 95.3 | 95.6
Perfect Galaxy | SDMS0500UL320XN | 500 kW, 320 V, 3-phase Inverter with combiner, N for ground type | 500 |  | 95.5 | Y | N |  | 98 |  |  | 300 | 430 | 480 | 50 | 100 | 150 | 250 | 375 | 500 | 90.51 | 94.95 | 95.18 | 95.47 | 95.31 | 94.7 | 95.09 | 91.29 | 93.9 | 95.72 | 95.96 | 95.59 | 95.09 | 95.4 | 90.71 | 93.8 | 95.8 | 95.9 | 95.76 | 95.19 | 95.46
Perfect Galaxy | SDMS0500UL320XP | 500 kW, 320 V, 3-phase Inverter with combiner, P for ground type | 500 |  | 95.5 | Y | N |  | 98 |  |  | 300 | 430 | 480 | 50 | 100 | 150 | 250 | 375 | 500 | 90.51 | 94.95 | 95.18 | 95.47 | 95.31 | 94.7 | 95.09 | 91.29 | 93.9 | 95.72 | 95.96 | 95.59 | 95.09 | 95.4 | 90.71 | 93.8 | 95.8 | 95.9 | 95.76 | 95.19 | 95.46
Perfect Galaxy | SDMS0500UL480TN | 500 kW, 480 V, 3-phase Inverter with combiner, N for ground type | 500 |  | 96 | Y | N |  | 101 |  |  | 300 | 430 | 480 | 50 | 100 | 150 | 250 | 375 | 500 | 90.2 | 95.09 | 95.37 | 95.88 | 95.89 | 95.51 | 95.54 | 90.99 | 94.04 | 95.92 | 96.36 | 96.17 | 95.9 | 95.85 | 90.4 | 93.94 | 95.99 | 96.31 | 96.34 | 96 | 95.92
Perfect Galaxy | SDMS0500UL480TP | 500 kW, 480 V, 3-phase Inverter with combiner, P for ground type | 500 |  | 96 | Y | N |  | 101 |  |  | 300 | 430 | 480 | 50 | 100 | 150 | 250 | 375 | 500 | 90.2 | 95.09 | 95.37 | 95.88 | 95.89 | 95.51 | 95.54 | 90.99 | 94.04 | 95.92 | 96.36 | 96.17 | 95.9 | 95.85 | 90.4 | 93.94 | 95.99 | 96.31 | 96.34 | 96 | 95.92
Perfect Galaxy | PV-625-XRLS-VV-RVG | 625 kW Utility Interactive Inverter | 625 |  | 96.5 | Y | N |  | 259 |  |  | 500 | 600 | 800 | 62.5 | 125 | 187.5 | 312.5 | 468.75 | 625 | 94.45 | 96.6 | 97.05 | 97.11 | 96.78 | 96.24 | 96.75 | 93.64 | 96.19 | 96.72 | 96.86 | 96.55 | 96.02 | 96.47 | 92.24 | 95.31 | 96.07 | 96.36 | 96.13 | 95.62 | 95.95
Perfect Galaxy | PV-625-XRLS-VV-STG | 625 kW Utility Interactive Inverter | 625 |  | 96.5 | Y | N |  | 259 |  |  | 500 | 600 | 800 | 62.5 | 125 | 187.5 | 312.5 | 468.75 | 625 | 94.45 | 96.6 | 97.05 | 97.11 | 96.78 | 96.24 | 96.75 | 93.64 | 96.19 | 96.72 | 96.86 | 96.55 | 96.02 | 96.47 | 92.24 | 95.31 | 96.07 | 96.36 | 96.13 | 95.62 | 95.95
Perfect Galaxy | EQX0630UV360XP(N) | 630 KW Utility Interactive Inverter | 630 |  | 97 | Y | N |  | 102 |  |  | 585 | 640 | 800 | 63 | 126 | 189 | 315 | 472.5 | 630 | 94.9 | 96.9 | 97.4 | 97.5 | 97.1 | 96.5 | 97.1 | 94.8 | 96.8 | 97.3 | 97.4 | 97 | 96.4 | 97 | 93.7 | 96.3 | 96.9 | 97.1 | 96.8 | 96.2 | 96.7
Perfect Galaxy | PV-680-XRLS-VV-RVG | 680 kW Utility Interactive Inverter | 680 |  | 96.5 | Y | N |  | 265 |  |  | 560 | 650 | 800 | 68 | 136 | 204 | 340 | 510 | 680 | 94.55 | 96.58 | 97.1 | 97.19 | 96.93 | 96.44 | 96.87 | 93.9 | 96.22 | 96.8 | 96.98 | 96.74 | 96.25 | 96.63 | 92.87 | 95.59 | 96.32 | 96.61 | 96.43 | 95.94 | 96.24
Perfect Galaxy | PV-680-XRLS-VV-STG | 680 kW Utility Interactive Inverter | 680 |  | 96.5 | Y | N |  | 265 |  |  | 560 | 650 | 800 | 68 | 136 | 204 | 340 | 510 | 680 | 94.55 | 96.58 | 97.1 | 97.19 | 96.93 | 96.44 | 96.87 | 93.9 | 96.22 | 96.8 | 96.98 | 96.74 | 96.25 | 96.63 | 92.87 | 95.59 | 96.32 | 96.61 | 96.43 | 95.94 | 96.24
Perfect Galaxy | EQX0750UV320XP(N) | 750 kW Utility Interactive Inverter | 750 |  | 97 | Y | N |  | 121 |  |  | 500 | 600 | 800 | 75 | 150 | 225 | 375 | 562.5 | 750 | 95.4 | 97.1 | 97.7 | 97.7 | 97.3 | 96.7 | 97.3 | 94.8 | 96.9 | 97.4 | 97.5 | 97.1 | 96.6 | 97.1 | 93.7 | 96.3 | 96.9 | 97.1 | 96.8 | 96.2 | 96.7
Perfect Galaxy | EPP-1000-0600-32060-200X-U-N | 1000 kW 3-phase Inverter, N for ground type | 1000 |  | 96.5 | Y | N |  | 325.5 |  |  | 320 | 360 | 480 | 100 | 200 | 300 | 500 | 750 | 1000 | 94.53 | 96.46 | 96.79 | 96.78 | 96.35 | 95.71 | 96.4 | 94.29 | 96.32 | 96.66 | 96.68 | 96.31 | 95.7 | 96.32 | 93.53 | 95.84 | 96.32 | 96.43 | 96.12 | 95.58 | 96.07
Perfect Galaxy | EPP-1000-0600-32060-200X-U-P | 1000 kW 3-phase Inverter, P for ground type | 1000 |  | 96.5 | Y | N |  | 325.5 |  |  | 320 | 360 | 480 | 100 | 200 | 300 | 500 | 750 | 1000 | 94.53 | 96.46 | 96.79 | 96.78 | 96.35 | 95.71 | 96.4 | 94.29 | 96.32 | 96.66 | 96.68 | 96.31 | 95.7 | 96.32 | 93.53 | 95.84 | 96.32 | 96.43 | 96.12 | 95.58 | 96.07
Perfect Galaxy | EQX1000UV400XP(N) | 1 MW Utility Interactive Inverter | 1000 |  | 97.5 | Y | N |  | 124 |  |  | 615 | 700 | 800 | 100 | 200 | 300 | 500 | 750 | 1000 | 95.4 | 97.2 | 97.7 | 97.8 | 97.5 | 97 | 97.5 | 94.9 | 97.1 | 97.5 | 97.7 | 97.4 | 96.8 | 97.3 | 94.4 | 96.8 | 97.3 | 97.6 | 97.3 | 96.8 | 97.2
Perfect Galaxy | PVS-1000 | 1000 kW, 3-phase Inverter for Medium Voltage Transformer | 1000 |  | 96 | Y | N |  | 396.4 |  |  | 420 | 486 | 670 | 100 | 200 | 300 | 500 | 750 | 1000 | 93.7 | 96.1 | 96.7 | 96.9 | 96.6 | 96.1 | 96.5 | 93.2 | 95.8 | 96.4 | 96.7 | 96.5 | 96 | 96.3 | 91.7 | 94.9 | 95.7 | 96.1 | 95.9 | 95.5 | 95.7
Perfect Galaxy | EPP-1250-1000-52085-320X-U-N | 1250 kW, 3-phase Inverter, N for ground type | 1250 |  | 97 | Y | N |  | 320.4 |  |  | 525 | 595 | 800 | 125 | 250 | 375 | 625 | 937.5 | 1250 | 94.6 | 96.7 | 97.3 | 97.4 | 97.1 | 96.7 | 97 | 94.1 | 96.5 | 97.1 | 97.2 | 97 | 96.5 | 96.9 | 93 | 95.9 | 96.6 | 96.8 | 96.7 | 96.2 | 96.5
Perfect Galaxy | EPP-1250-1000-52085-320X-U-P | 1250 kW, 3-phase Inverter, P for ground type | 1250 |  | 97 | Y | N |  | 320.4 |  |  | 525 | 595 | 800 | 125 | 250 | 375 | 625 | 937.5 | 1250 | 94.6 | 96.7 | 97.3 | 97.4 | 97.1 | 96.7 | 97 | 94.1 | 96.5 | 97.1 | 97.2 | 97 | 96.5 | 96.9 | 93 | 95.9 | 96.6 | 96.8 | 96.7 | 96.2 | 96.5
Perfect Galaxy International Ltd | EQMX0500UV320XN [320V] | 500kW, 320Vac Utility Interactive Inverter, Support negative grounded at PV side | 500 | 320 | 97.5 | N | N | Efficiency data inclusive of transformer effect based on 500 kVA Low-Voltage Dry-Type Distribution Transformers Table in DOE2016. | 106.8 |  |  | 500 | 600 | 800 | 50 | 100 | 150 | 250 | 375 | 500 | 95.9 | 97.4 | 97.6 | 97.8 | 97.6 | 97.1 | 97.5 | 95.3 | 97.1 | 97.4 | 97.7 | 97.4 | 97 | 97.4 | 93.8 | 96.6 | 97.2 | 97.4 | 97.2 | 96.8 | 97 | 2017-11-15 | 2018-04-16
Perfect Galaxy International Ltd | EQMX0500UV320XP [320V] | 500kW, 320Vac Utility Interactive Inverter, Support positive grounded at PV side | 500 | 320 | 97.5 | N | N | Efficiency data inclusive of transformer effect based on 500 kVA Low-Voltage Dry-Type Distribution Transformers Table in DOE2016. | 106.8 |  |  | 500 | 600 | 800 | 50 | 100 | 150 | 250 | 375 | 500 | 95.9 | 97.4 | 97.6 | 97.8 | 97.6 | 97.1 | 97.5 | 95.3 | 97.1 | 97.4 | 97.7 | 97.4 | 97 | 97.4 | 93.8 | 96.6 | 97.2 | 97.4 | 97.2 | 96.8 | 97 | 2017-11-15 | 2018-04-16
Perfect Galaxy International Ltd | EQMX0630UV400XN [400V] | 630kW, 400Vac Utility Interactive Inverter, Support negative grounded at PV side | 630 | 400 | 97.5 | N | N | Efficiency data inclusive of transformer effect based on 630 kVA Low-Voltage Dry-Type Distribution Transformers Table in DOE2016. | 138 |  |  | 615 | 700 | 800 | 63 | 126 | 189 | 315 | 472.5 | 630 | 95.7 | 97.3 | 97.7 | 97.9 | 97.5 | 97.2 | 97.5 | 95.3 | 97.1 | 97.6 | 97.7 | 97.4 | 97.2 | 97.4 | 94.6 | 96.7 | 97.3 | 97.6 | 97.3 | 97 | 97.2 | 2017-11-15 | 2018-04-16
Perfect Galaxy International Ltd | EQMX0630UV400XP [400V] | 630kW, 400Vac Utility Interactive Inverter, Support positive grounded at PV side | 630 | 400 | 97.5 | N | N | Efficiency data inclusive of transformer effect based on 630 kVA Low-Voltage Dry-Type Distribution Transformers Table in DOE2016. | 138 |  |  | 615 | 700 | 800 | 63 | 126 | 189 | 315 | 472.5 | 630 | 95.7 | 97.3 | 97.7 | 97.9 | 97.5 | 97.2 | 97.5 | 95.3 | 97.1 | 97.6 | 97.7 | 97.4 | 97.2 | 97.4 | 94.6 | 96.7 | 97.3 | 97.6 | 97.3 | 97 | 97.2 | 2017-11-15 | 2018-04-16
Perfect Galaxy International Ltd. | EQX0500UV320XP(N) | 500 kW Utility Interactive Inverter | 500 |  | 97 | Y | N |  | 96 |  |  | 500 | 590 | 800 | 50 | 100 | 150 | 250 | 375 | 500 | 95.0415 | 97.2448 | 97.2893 | 97.1457 | 97.1723 | 96.4538 | 97.0632 | 94.3159 | 96.376 | 97.0243 | 97.3081 | 96.9975 | 96.4884 | 96.9022 | 93.126 | 95.6022 | 96.4659 | 96.9144 | 96.6959 | 96.2151 | 96.4926
Petra Solar | 103.10866.500x [120V] | 212 W, 120 Vac Inverter, where x = 1, 2, 3, or 4 | 0.2 | 120 | 93 | N | Y |  | 1.59 |  |  | 29 | 35 | 40 | 0.02 | 0.04 | 0.06 | 0.1 | 0.15 | 0.2 | 85.3 | 91.2 | 92.3 | 93.3 | 93.6 | 93.4 | 92.9 | 85.6 | 91.1 | 92.4 | 93.2 | 93.7 | 93.6 | 93 | 84.7 | 90.8 | 92.2 | 93.1 | 93.6 | 93.7 | 92.8
Petra Systems | 103.10400.0002 [240V] | 240 W, 240 Vac Utility Interactive Microinverter | 0.24 | 240 | 96 | N | Y |  | 0.14 |  |  | 30 | 35 | 40 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 91.9 | 95.3 | 96 | 96.2 | 96.4 | 96.2 | 96 | 90.9 | 95 | 95.8 | 96.2 | 96.3 | 96.3 | 96 | 89.7 | 94.7 | 95.6 | 96.2 | 96.3 | 96.3 | 95.8
Petra Systems | 103.10400.0001 [120V] | 241 W, Utility Interactive, 120 Vac Microinverter | 0.241 | 120 | 96 | N | Y |  | 0.05 |  |  | 30 | 35 | 40 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 93.4 | 95.7 | 96.1 | 95.9 | 96.1 | 95.7 | 95.9 | 92.7 | 95.5 | 96 | 96 | 96 | 95.8 | 95.9 | 91.6 | 95.2 | 95.9 | 96.1 | 96 | 95.8 | 95.8
Phoenixtec Power | PS240US3R [208V] | 4000 W, 208 Vac Utility Interactive Inverter | 4 | 208 | 95.5 | Y | N |  | 60.3 |  |  | 100 | 310 | 360 | 0.4 | 0.8 | 1.2 | 2 | 3 | 4 | 90.2 | 93.8 | 95.1 | 95.6 | 95.3 | 94.8 | 95 | 90.7 | 94.3 | 95.4 | 95.8 | 95.6 | 95.2 | 95.3 | 91.5 | 94.6 | 95.8 | 96 | 95.8 | 95.3 | 95.6
Phoenixtec Power | PS240US3R [240V] | 4000 W, 240 Vac Utility Interactive Inverter | 4 | 240 | 95.5 | Y | N |  | 39 |  |  | 100 | 310 | 360 | 0.4 | 0.8 | 1.2 | 2 | 3 | 4 | 89.6 | 93.5 | 94.9 | 95.8 | 95.7 | 95.3 | 95.2 | 90.3 | 93.9 | 95.1 | 96.1 | 96 | 95.9 | 95.6 | 90 | 93.9 | 95.5 | 95.9 | 96 | 95.9 | 95.6
Phono Solar Technology | PS240M-20/U-AC | 212 W Inverter | 0.212 |  | 94.5 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0 |  |  | 36 | 50 | 55 | 0.0212 | 0.0424 | 0.0636 | 0.106 | 0.159 | 0.212 | 87.88 | 94.35 | 95.79 | 95.73 | 94.8 | 93.45 | 94.75 | 85.23 | 92.51 | 94.56 | 95.3 | 95.12 | 94.17 | 94.52 | 83.57 | 92.02 | 94.33 | 94.87 | 94.87 | 93.91 | 94.16
Phono Solar Technology | PS240P-20/U-AC | 212 W Inverter | 0.212 |  | 94.5 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0 |  |  | 36 | 50 | 55 | 0.0212 | 0.0424 | 0.0636 | 0.106 | 0.159 | 0.212 | 87.88 | 94.35 | 95.79 | 95.73 | 94.8 | 93.45 | 94.75 | 85.23 | 92.51 | 94.56 | 95.3 | 95.12 | 94.17 | 94.52 | 83.57 | 92.02 | 94.33 | 94.87 | 94.87 | 93.91 | 94.16
Phono Solar Technology | PS245M-20/U-AC | 212 W Inverter | 0.212 |  | 94.5 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0 |  |  | 36 | 50 | 55 | 0.0212 | 0.0424 | 0.0636 | 0.106 | 0.159 | 0.212 | 87.88 | 94.35 | 95.79 | 95.73 | 94.8 | 93.45 | 94.75 | 85.23 | 92.51 | 94.56 | 95.3 | 95.12 | 94.17 | 94.52 | 83.57 | 92.02 | 94.33 | 94.87 | 94.87 | 93.91 | 94.16
Phono Solar Technology | PS245P-20/U-AC | 212 W Inverter | 0.212 |  | 94.5 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0 |  |  | 36 | 50 | 55 | 0.0212 | 0.0424 | 0.0636 | 0.106 | 0.159 | 0.212 | 87.88 | 94.35 | 95.79 | 95.73 | 94.8 | 93.45 | 94.75 | 85.23 | 92.51 | 94.56 | 95.3 | 95.12 | 94.17 | 94.52 | 83.57 | 92.02 | 94.33 | 94.87 | 94.87 | 93.91 | 94.16
Phono Solar Technology | PS250M-20/U-AC | 212 W Inverter | 0.212 |  | 94.5 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0 |  |  | 36 | 50 | 55 | 0.0212 | 0.0424 | 0.0636 | 0.106 | 0.159 | 0.212 | 87.88 | 94.35 | 95.79 | 95.73 | 94.8 | 93.45 | 94.75 | 85.23 | 92.51 | 94.56 | 95.3 | 95.12 | 94.17 | 94.52 | 83.57 | 92.02 | 94.33 | 94.87 | 94.87 | 93.91 | 94.16
Phono Solar Technology | PS250P-20/U-AC | 212 W Inverter | 0.212 |  | 94.5 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0 |  |  | 36 | 50 | 55 | 0.0212 | 0.0424 | 0.0636 | 0.106 | 0.159 | 0.212 | 87.88 | 94.35 | 95.79 | 95.73 | 94.8 | 93.45 | 94.75 | 85.23 | 92.51 | 94.56 | 95.3 | 95.12 | 94.17 | 94.52 | 83.57 | 92.02 | 94.33 | 94.87 | 94.87 | 93.91 | 94.16
Phono Solar Technology | PS255M-20/U-AC | 212 W Inverter | 0.212 |  | 94.5 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0 |  |  | 36 | 50 | 55 | 0.0212 | 0.0424 | 0.0636 | 0.106 | 0.159 | 0.212 | 87.88 | 94.35 | 95.79 | 95.73 | 94.8 | 93.45 | 94.75 | 85.23 | 92.51 | 94.56 | 95.3 | 95.12 | 94.17 | 94.52 | 83.57 | 92.02 | 94.33 | 94.87 | 94.87 | 93.91 | 94.16
Phono Solar Technology | PS255P-20/U-AC | 212 W Inverter | 0.212 |  | 94.5 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0 |  |  | 36 | 50 | 55 | 0.0212 | 0.0424 | 0.0636 | 0.106 | 0.159 | 0.212 | 87.88 | 94.35 | 95.79 | 95.73 | 94.8 | 93.45 | 94.75 | 85.23 | 92.51 | 94.56 | 95.3 | 95.12 | 94.17 | 94.52 | 83.57 | 92.02 | 94.33 | 94.87 | 94.87 | 93.91 | 94.16
Phono Solar Technology | PS260M-20/U-AC | 212 W Inverter | 0.212 |  | 94.5 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0 |  |  | 36 | 50 | 55 | 0.0212 | 0.0424 | 0.0636 | 0.106 | 0.159 | 0.212 | 87.88 | 94.35 | 95.79 | 95.73 | 94.8 | 93.45 | 94.75 | 85.23 | 92.51 | 94.56 | 95.3 | 95.12 | 94.17 | 94.52 | 83.57 | 92.02 | 94.33 | 94.87 | 94.87 | 93.91 | 94.16
Phono Solar Technology | PS260P-20/U-AC | 212 W Inverter | 0.212 |  | 94.5 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0 |  |  | 36 | 50 | 55 | 0.0212 | 0.0424 | 0.0636 | 0.106 | 0.159 | 0.212 | 87.88 | 94.35 | 95.79 | 95.73 | 94.8 | 93.45 | 94.75 | 85.23 | 92.51 | 94.56 | 95.3 | 95.12 | 94.17 | 94.52 | 83.57 | 92.02 | 94.33 | 94.87 | 94.87 | 93.91 | 94.16
Pika Energy | X3001-NA | Grid-tie Inverter for interconnection with a Rebus DC microgrid | 3 |  | 96 | Y | N |  | 2.64 |  |  | 100 | 398 | 400 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 94 | 96 | 96.3 | 96.3 | 96 | 95.6 | 96 | 93.9 | 96 | 96.3 | 96.3 | 96 | 95.5 | 96 | 93.9 | 95.9 | 96.3 | 96.3 | 96 | 95.5 | 96
Pika Energy | X7603 [240V] | 7.6 kW, 240 Vac Utility Interactive Inverter | 7.585 | 240 | 96.5 | N | N |  | 1.29 |  |  | 390 | 400 | 420 | 0.76 | 1.52 | 2.28 | 3.79 | 5.69 | 7.59 | 91.7 | 95.9 | 96.6 | 97.3 | 97.2 | 97 | 96.9 | 91 | 95.4 | 96.5 | 97.3 | 97.1 | 97 | 96.8 | 90.5 | 95.2 | 96.3 | 96.9 | 97 | 96.9 | 96.5 | 2018-04-02 | 2018-10-15
Pika Energy | X7601 [240V] | 7.6 kW, 240 Vac Utility Interactive Inverter | 7.587 | 240 | 96.5 | Y | N |  | 1.29 |  |  | 390 | 400 | 420 | 0.76 | 1.52 | 2.28 | 3.79 | 5.69 | 7.59 | 91.7 | 95.9 | 96.6 | 97.3 | 97.2 | 97 | 96.9 | 91 | 95.4 | 96.5 | 97.3 | 97.1 | 97 | 96.8 | 90.5 | 95.2 | 96.3 | 96.9 | 97 | 96.9 | 96.5 | 2017-12-15 | 2018-10-15
Pika Energy | X7602 [240V] | 7.6 kW, 240 Vac Utility Interactive Inverter | 7.587 | 240 | 96.5 | Y | N |  | 1.29 |  |  | 390 | 400 | 420 | 0.76 | 1.52 | 2.28 | 3.79 | 5.69 | 7.59 | 91.7 | 95.9 | 96.6 | 97.3 | 97.2 | 97 | 96.9 | 91 | 95.4 | 96.5 | 97.3 | 97.1 | 97 | 96.8 | 90.5 | 95.2 | 96.3 | 96.9 | 97 | 96.9 | 96.5 | 2017-12-15 | 2018-10-15
Pika Energy | X11403 [208V] | 11.4 kW, 208 Vac Utility Interactive Inverter | 11.18 | 208 | 97.5 | N | N |  | 0.13 |  |  | 390 | 400 | 420 | 1.12 | 2.24 | 3.35 | 5.59 | 8.39 | 11.18 | 97.2 | 97.4 | 97.6 | 97.6 | 97.4 | 97.1 | 97.5 | 97 | 97.3 | 97.7 | 97.5 | 97.3 | 96.9 | 97.3 | 95.8 | 97.2 | 97.3 | 97.4 | 97.1 | 96.9 | 97.1 | 2018-04-02 | 2018-10-15
Pika Energy | X11402 [208V] | 11.4 kW, 208 Vac Utility Interactive Inverter | 11.187 | 208 | 97.5 | Y | N |  | 0.13 |  |  | 390 | 400 | 420 | 1.12 | 2.24 | 3.36 | 5.59 | 8.39 | 11.19 | 97.2 | 97.4 | 97.6 | 97.6 | 97.4 | 97.1 | 97.5 | 97 | 97.3 | 97.7 | 97.5 | 97.3 | 96.9 | 97.3 | 95.8 | 97.2 | 97.3 | 97.4 | 97.1 | 96.9 | 97.1 | 2017-12-15 | 2018-10-15
Power Electronics | FS0300CU | Utility Interactive Photovoltaic Inverter | 300 |  | 96.5 | Y | N |  | 232 |  |  | 585 | 650 | 800 | 30 | 60 | 90 | 150 | 225 | 300 | 95.2 | 96.6 | 96.6 | 97.2 | 97.1 | 96.4 | 96.9 | 95.1 | 96.4 | 96.4 | 97 | 96.9 | 96.4 | 96.7 | 94.3 | 95.7 | 95.6 | 96.4 | 96.4 | 95.8 | 96.2
Power Electronics | FS0300PU | Utility Interactive Photovoltaic Inverter | 300 |  | 96.5 | Y | N |  | 232 |  |  | 585 | 650 | 800 | 30 | 60 | 90 | 150 | 225 | 300 | 95.2 | 96.6 | 96.6 | 97.2 | 97.1 | 96.4 | 96.9 | 95.1 | 96.4 | 96.4 | 97 | 96.9 | 96.4 | 96.7 | 94.3 | 95.7 | 95.6 | 96.4 | 96.4 | 95.8 | 96.2
Power Electronics | FS0450CU | Utility Interactive Photovoltaic Inverter | 450 |  | 97 | Y | N |  | 256 |  |  | 545 | 650 | 800 | 45 | 90 | 135 | 225 | 337.5 | 450 | 95 | 96.9 | 97.1 | 97.3 | 97.1 | 96.6 | 97.1 | 94.9 | 96.7 | 96.9 | 97.2 | 97 | 96.6 | 96.9 | 94.2 | 96.4 | 96.4 | 96.8 | 96.6 | 96.1 | 96.5
Power Electronics | FS0450PU | Utility Interactive Photovoltaic Inverter | 450 |  | 97 | Y | N |  | 256 |  |  | 545 | 650 | 800 | 45 | 90 | 135 | 225 | 337.5 | 450 | 95 | 96.9 | 97.1 | 97.3 | 97.1 | 96.6 | 97.1 | 94.9 | 96.7 | 96.9 | 97.2 | 97 | 96.6 | 96.9 | 94.2 | 96.4 | 96.4 | 96.8 | 96.6 | 96.1 | 96.5
Power Electronics | FS0501CU | Utility Interactive Photovoltaic Inverter | 499.9 |  | 96.5 | Y | N |  | 477.9 |  |  | 500 | 575 | 800 | 49.98 | 99.97 | 150 | 249.9 | 374.9 | 499.9 | 94.3 | 96.3 | 96.8 | 97 | 96.8 | 96.4 | 96.7 | 94 | 96.2 | 96.6 | 96.8 | 96.6 | 96.2 | 96.5 | 93.1 | 95.5 | 96 | 96.1 | 96 | 95.7 | 95.9
Power Electronics | FS0560CU | Utility Interactive Photovoltaic Inverter | 560 |  | 96 | Y | N |  | 602 |  |  | 330 | 400 | 480 | 56 | 112 | 168 | 280 | 420 | 560 | 94.3 | 95.8 | 96.2 | 96.4 | 96.1 | 95.4 | 96.1 | 94 | 95.6 | 96 | 96.1 | 95.9 | 95.3 | 95.8 | 93.8 | 95.3 | 95.6 | 95.8 | 95.6 | 95 | 95.5
Power Electronics | FS0560PU | Utility Interactive Photovoltaic Inverter | 560 |  | 96 | Y | N |  | 602 |  |  | 330 | 400 | 480 | 56 | 112 | 168 | 280 | 420 | 560 | 94.3 | 95.8 | 96.2 | 96.4 | 96.1 | 95.4 | 96.1 | 94 | 95.6 | 96 | 96.1 | 95.9 | 95.3 | 95.8 | 93.8 | 95.3 | 95.6 | 95.8 | 95.6 | 95 | 95.5
Power Electronics | FS0600PU | Utility Interactive Photovoltaic Inverter | 600 |  | 97 | Y | N |  | 281 |  |  | 585 | 650 | 800 | 60 | 120 | 180 | 300 | 450 | 600 | 95.6 | 97 | 97.4 | 97.5 | 97.3 | 96.7 | 97.3 | 95.3 | 96.7 | 97.3 | 97.4 | 97.1 | 96.7 | 97.1 | 94.9 | 96.1 | 96.9 | 97 | 96.7 | 96.4 | 96.7
Power Electronics | FS0640CU | Utility Interactive Photovoltaic Inverter | 640 |  | 96 | Y | N |  | 629 |  |  | 330 | 400 | 480 | 64 | 128 | 192 | 320 | 480 | 640 | 94.3 | 95.8 | 96.3 | 96.4 | 96.1 | 95.3 | 96.1 | 94 | 95.6 | 96 | 96.1 | 95.9 | 95.3 | 95.8 | 93.8 | 95.3 | 95.7 | 95.8 | 95.6 | 95 | 95.5
Power Electronics | FS0640PU | Utility Interactive Photovoltaic Inverter | 640 |  | 96 | Y | N |  | 629 |  |  | 330 | 400 | 480 | 64 | 128 | 192 | 320 | 480 | 640 | 94.3 | 95.8 | 96.3 | 96.4 | 96.1 | 95.3 | 96.1 | 94 | 95.6 | 96 | 96.1 | 95.9 | 95.3 | 95.8 | 93.8 | 95.3 | 95.7 | 95.8 | 95.6 | 95 | 95.5
Power Electronics | FS0600CU | Utility Interactive Photovoltaic Inverter | 680 |  | 97 | Y | N |  | 249 |  |  | 552 | 620 | 800 | 68 | 136 | 204 | 340 | 510 | 680 | 95.1 | 97 | 97.5 | 97.7 | 97.5 | 97 | 97.4 | 94.9 | 96.7 | 97.2 | 97.4 | 97.2 | 96.7 | 97.1 | 94.3 | 96.3 | 96.8 | 97 | 96.8 | 96.4 | 96.7
Power Electronics | FS0750CU | Utility Interactive Photovoltaic Inverter | 750 |  | 96.5 | Y | N |  | 506.3 |  |  | 500 | 575 | 800 | 75 | 150 | 225 | 375 | 562.5 | 750 | 95 | 96.7 | 97 | 97.1 | 97.1 | 96.6 | 96.9 | 94.8 | 96.5 | 96.8 | 96.9 | 96.8 | 96.4 | 96.7 | 94.2 | 95.8 | 96.2 | 96.3 | 96.3 | 95.9 | 96.1
Power Electronics | FS0751PU | Utility Interactive Photovoltaic Inverter | 751 |  | 97 | Y | N |  | 306 |  |  | 585 | 650 | 800 | 75.1 | 150.2 | 225.3 | 375.5 | 563.3 | 751 | 95.4 | 97 | 97.4 | 97.4 | 97.3 | 96.7 | 97.2 | 95.3 | 96.8 | 97.2 | 97.2 | 97.2 | 96.7 | 97.1 | 94.9 | 96.3 | 96.7 | 96.8 | 96.8 | 96.4 | 96.7
Power Electronics | FS0701CU [360V] | Utility Interactive modular Inverter: 360Vac, 780 kW, with MV NEMA TP1 transformer | 780 | 360 | 97 | Y | N |  | 254 |  |  | 510 | 590 | 800 | 78 | 156 | 234 | 390 | 585 | 780 | 95.3 | 97.1 | 97.5 | 97.6 | 97.4 | 96.8 | 97.3 | 95 | 96.7 | 97.1 | 97.3 | 97 | 96.4 | 96.9 | 94.5 | 96.1 | 96.6 | 96.8 | 96.5 | 96.1 | 96.4
Power Electronics | FS0830PU | Utility Interactive Photovoltaic Inverter | 830 |  | 97 | Y | N |  | 466 |  |  | 540 | 606 | 800 | 83 | 166 | 249 | 415 | 622.5 | 830 | 95.6 | 97.2 | 97.5 | 97.7 | 97.4 | 96.8 | 97.4 | 95.5 | 97 | 97.4 | 97.5 | 97.3 | 96.8 | 97.2 | 95 | 96.5 | 96.8 | 96.9 | 96.8 | 96.4 | 96.7
Power Electronics | FS0751CU | Utility Interactive Photovoltaic Inverter | 850 |  | 97 | N | N |  | 260 |  |  | 552 | 620 | 800 | 85 | 170 | 255 | 425 | 637.5 | 850 | 95.9 | 97.4 | 97.8 | 97.9 | 97.6 | 97.1 | 97.6 | 95.6 | 97.1 | 97.5 | 97.6 | 97.3 | 96.8 | 97.3 | 95.2 | 96.7 | 97 | 97.2 | 96.9 | 96.4 | 96.9
Power Electronics | FS0900PU | Utility Interactive Photovoltaic Inverter | 900 |  | 97 | Y | N |  | 332 |  |  | 545 | 615 | 332 | 90 | 180 | 270 | 450 | 675 | 900 | 95.8 | 97.2 | 97.5 | 97.6 | 97.5 | 96.9 | 97.4 | 95.6 | 97.1 | 97.3 | 97.4 | 97.3 | 96.9 | 97.2 | 95.3 | 96.6 | 96.7 | 97 | 96.9 | 96.6 | 96.8
Power Electronics | FS0830CU | Utility Interactive Photovoltaic Inverter | 930 |  | 97 | Y | N |  | 295 |  |  | 510 | 590 | 800 | 93 | 186 | 279 | 465 | 697.5 | 930 | 95.6 | 97.2 | 97.6 | 97.7 | 97.5 | 96.9 | 97.4 | 95.1 | 96.9 | 97.3 | 97.4 | 97.1 | 96.6 | 97.1 | 94.8 | 96.4 | 96.8 | 96.8 | 96.6 | 96.1 | 96.6
Power Electronics | FS0970CU | Utility Interactive Photovoltaic Inverter | 970 |  | 97 | Y | N |  | 491 |  |  | 545 | 615 | 800 | 97 | 194 | 291 | 485 | 727.5 | 970 | 95.8 | 97.2 | 97.5 | 97.6 | 97.4 | 96.8 | 97.4 | 95.5 | 97 | 97.3 | 97.5 | 97.3 | 96.8 | 97.2 | 95.1 | 96.6 | 96.7 | 96.9 | 96.8 | 96.4 | 96.7
Power Electronics | FS0970PU | Utility Interactive Photovoltaic Inverter | 970 |  | 97 | Y | N |  | 491 |  |  | 545 | 615 | 800 | 97 | 194 | 291 | 485 | 727.5 | 970 | 95.8 | 97.2 | 97.5 | 97.6 | 97.4 | 96.8 | 97.4 | 95.5 | 97 | 97.3 | 97.5 | 97.3 | 96.8 | 97.2 | 95.1 | 96.6 | 96.7 | 96.9 | 96.8 | 96.4 | 96.7
Power Electronics | FS0901CU | Utility Interactive Photovoltaic Inverter | 1000 |  | 97 | N | N |  | 266 |  |  | 584 | 650 | 800 | 100 | 200 | 300 | 500 | 750 | 1000 | 95.4 | 97 | 97.4 | 97.5 | 97.2 | 96.6 | 97.2 | 95.3 | 96.9 | 97.3 | 97.4 | 97 | 96.5 | 97 | 95 | 96.6 | 97 | 97.1 | 96.8 | 96.3 | 96.8
Power Electronics | FS1001CU | Utility Interactive Photovoltaic Inverter | 1000 |  | 97 | Y | N |  | 615.6 |  |  | 500 | 575 | 800 | 100 | 200 | 300 | 500 | 750 | 1000 | 95.4 | 97 | 97.4 | 97.5 | 97.3 | 96.9 | 97.3 | 95.2 | 96.8 | 97.2 | 97.3 | 97.1 | 96.7 | 97.1 | 94.7 | 96.2 | 96.6 | 96.7 | 96.6 | 96.2 | 96.5
Power Electronics | FS1004CU | Utility Interactive Photovoltaic Inverter | 1000 |  | 97 | N | N |  | 265.579 |  |  | 584 | 650 | 800 | 100 | 200 | 300 | 500 | 750 | 1000 | 95.4 | 97 | 97.4 | 97.5 | 97.2 | 96.6 | 97.2 | 95.3 | 96.9 | 97.3 | 97.4 | 97 | 96.5 | 97 | 95 | 96.5886 | 97 | 97.1 | 96.8 | 96.3 | 96.8
Power Electronics | FS0900CU | Utility Interactive Photovoltaic Inverter | 1020 |  | 97.5 | Y | N |  | 276 |  |  | 552 | 620 | 800 | 102 | 204 | 306 | 510 | 765 | 1020 | 95.8 | 97.5 | 97.9 | 97.9 | 97.7 | 97.2 | 97.7 | 95.5 | 97.1 | 97.5 | 97.6 | 97.3 | 96.8 | 97.3 | 94.8 | 96.6 | 97.1 | 97.2 | 96.9 | 96.4 | 96.8
Power Electronics | FS0940CU | Utility Interactive Photovoltaic Inverter | 1050 |  | 97 | N | N |  | 274 |  |  | 616 | 670 | 800 | 105 | 210 | 315 | 525 | 787.5 | 1050 | 95.3 | 97 | 97.4 | 97.5 | 97.2 | 96.7 | 97.2 | 95.2 | 96.9 | 97.3 | 97.4 | 97.1 | 96.6 | 97.1 | 94.9 | 96.6 | 97.1 | 97.2 | 96.9 | 96.4 | 96.9
Power Electronics | FS1050PU | Utility Interactive Photovoltaic Inverter | 1050 |  | 97 | Y | N |  | 356 |  |  | 545 | 615 | 800 | 120 | 240 | 360 | 600 | 900 | 1200 | 95.8 | 96.8 | 97.4 | 97.6 | 97.5 | 96.9 | 97.4 | 95.3 | 96.6 | 97.1 | 97.3 | 97.3 | 96.9 | 97.2 | 95.7 | 95.7 | 96.6 | 97 | 96.9 | 96.6 | 96.7
Power Electronics | FS1051CU | Utility Interactive Photovoltaic Inverter | 1050 |  | 97 | N | N |  | 274 |  |  | 616 | 670 | 800 | 105 | 210 | 315 | 525 | 787.5 | 1050 | 95.3 | 97 | 97.4 | 97.5 | 97.2 | 96.7 | 97.2 | 95.2 | 96.9 | 97.3 | 97.4 | 97.1 | 96.6 | 97.1 | 94.9 | 96.6 | 97.1 | 97.2 | 96.9 | 96.4 | 96.9
Power Electronics | FS1003CU | Utility Interactive Photovoltaic Inverter | 1100 |  | 97 | Y | N |  | 317 |  |  | 510 | 590 | 800 | 110 | 220 | 330 | 550 | 825 | 1100 | 95.8 | 97.3 | 97.8 | 97.8 | 97.6 | 97 | 97.6 | 95.5 | 97 | 97.4 | 97.5 | 97.2 | 96.6 | 97.2 | 94.9 | 96.6 | 96.9 | 97 | 96.7 | 96.2 | 96.7
Power Electronics | FS01110PU | Utility Interactive Photovoltaic Inverter | 1110 |  | 97 | Y | N |  | 558 |  |  | 545 | 615 | 800 | 111 | 222 | 333 | 555 | 832.5 | 1110 | 95.7 | 97.1 | 97.1 | 97.7 | 97.6 | 96.9 | 97.4 | 95.6 | 96.9 | 96.9 | 97.4 | 97.4 | 96.9 | 97.2 | 94.8 | 96.1 | 96.1 | 96.9 | 96.9 | 96.3 | 96.6
Power Electronics | FS1000CU [440V] | 1110 kW, 440 Vac Utility Interactive Inverter with Medium Voltage Transformer | 1110 | 440 | 97 | N | N |  | 281 |  |  | 642 | 690 | 800 | 111 | 222 | 333 | 555 | 832.5 | 1110 | 95.4 | 97 | 97.4 | 97.5 | 97.2 | 96.7 | 97.2 | 95.3 | 96.9 | 97.4 | 97.4 | 97.2 | 96.7 | 97.1 | 95.1 | 96.7 | 97.1 | 97.2 | 97 | 96.6 | 97
Power Electronics | FS1112CU [440V] | 1110 kW, 440 Vac Utility Interactive Inverter with Medium Voltage Transformer | 1110 | 440 | 97 | N | N |  | 281.407 |  |  | 642 | 690 | 800 | 111 | 222 | 333 | 555 | 832.5 | 1110 | 95.4 | 97 | 97.4 | 97.5 | 97.2 | 96.7 | 97.2 | 95.3 | 96.9 | 97.4 | 97.4 | 97.2 | 96.7 | 97.1 | 95.1 | 96.7 | 97.1 | 97.2 | 97 | 96.6 | 97
Power Electronics | FS1050CU15 [565V] | 1050 kW, 565 Vac Utility Interactive Inverter with combiner box | 1163.5 | 565 | 97 | N | N | Efficiency data inclusive of transformer effect based on 1050 kVA Liquid-Immeresed Distribution Transformers Table in DOE2016. | 338.51 |  |  | 800 | 900 | 1200 | 116 | 233 | 349 | 582 | 873 | 1164 | 93 | 96.2 | 96.7 | 97.5 | 97.6 | 97.5 | 97.2 | 93 | 96.1 | 96.7 | 97.4 | 97.5 | 97.3 | 97.1 | 93.2 | 96.2 | 96.6 | 97.4 | 97.6 | 97.3 | 97.2 | 2018-05-15 | 2018-10-15
Power Electronics | FS1100CU15O3 [600V] | 1100 kW, 600 Vac Utility Interactive Inverter with combiner box and a back feed power supply of 10kW to feed solar trackers on the PV power plant | 1176.44 | 600 | 98 | N | N | Efficiency data inclusive of transformer effect based on 1100 kVA Liquid-Immeresed Distribution Transformers Table in DOE2016. | 358.91 |  |  | 849 | 940 | 1200 | 118 | 235 | 353 | 588 | 882 | 1176 | 95.9 | 97.5 | 97.7 | 98 | 98 | 98 | 97.9 | 95.8 | 97.4 | 97.7 | 98 | 97.9 | 97.9 | 97.8 | 95.8 | 97.4 | 97.7 | 98 | 97.9 | 97.9 | 97.8 | 2018-05-15 | 2018-10-15
Power Electronics | FS1050CU | 1050 kW Utility Interactive Inverter with Medium Voltage NEMA TP1 transformer | 1190 |  | 97 | Y | N |  | 314 |  |  | 552 | 620 | 800 | 119 | 238 | 357 | 595 | 892.5 | 1190 | 95.9 | 97.5 | 97.8 | 97.9 | 97.7 | 97.1 | 97.6 | 95.6 | 97.1 | 97.5 | 97.5 | 97.3 | 96.8 | 97.3 | 94.9 | 96.5 | 97 | 97.1 | 96.9 | 96.4 | 96.8
Power Electronics | FS1080CU [400V] | 1200 kW, 400 Vac Utility Interactive Inverter with Medium Voltage Transformer | 1200 | 400 | 97 | N | N |  | 289 |  |  | 584 | 650 | 800 | 120 | 240 | 360 | 600 | 900 | 1200 | 95.5 | 97 | 97.4 | 97.5 | 97.2 | 96.7 | 97.2 | 95.4 | 96.9 | 97.3 | 97.4 | 97.1 | 96.5 | 97 | 95.1 | 96.6 | 97 | 97.1 | 96.8 | 96.3 | 96.8
Power Electronics | FS1200CU | 1200 kW Utility Interactive Inverter with Medium Voltage NEMA TP1 transformer | 1200 |  | 97 | Y | N |  | 630 |  |  | 545 | 615 | 800 | 120 | 240 | 360 | 600 | 900 | 1200 | 95.8 | 96.6 | 97.1 | 97.7 | 97.6 | 96.9 | 97.4 | 95 | 96.2 | 96.9 | 97.5 | 97.4 | 97 | 97.2 | 95.6 | 95.4 | 96.2 | 97.1 | 96.9 | 96.5 | 96.7
Power Electronics | FS1200PU | 1200 kW Utility Interactive Inverter with Medium Voltage NEMA TP1 transformer | 1200 |  | 97 | Y | N |  | 630 |  |  | 545 | 615 | 800 | 120 | 240 | 360 | 600 | 900 | 1200 | 95.8 | 96.6 | 97.1 | 97.7 | 97.6 | 96.9 | 97.4 | 95 | 96.2 | 96.9 | 97.5 | 97.4 | 97 | 97.2 | 95.6 | 95.4 | 96.2 | 97.1 | 96.9 | 96.5 | 96.7
Power Electronics | FS1201CU [400V] | 1200 kW, 400 Vac Utility Interactive Inverter with Medium Voltage Transformer | 1200 | 400 | 98 | N | N |  | 289 |  |  | 584 | 650 | 800 | 120 | 240 | 360 | 600 | 900 | 1200 | 98.1 | 98.3 | 98.4 | 98.4 | 98.2 | 98.1 | 98.3 | 98 | 98.2 | 98.2 | 98.3 | 98.1 | 97.9 | 98.2 | 97.7 | 97.9 | 97.9 | 98 | 97.9 | 97.7 | 97.9
Power Electronics | FS1100CU15 [600V] | 1100 kW, 600 Vac Utility Interactive Inverter with combiner box | 1209.25 | 600 | 97 | N | N | Efficiency data inclusive of transformer effect based on 1100 kVA Liquid-Immeresed Distribution Transformers Table in DOE2016. | 347.22 |  |  | 849 | 940 | 1200 | 121 | 242 | 363 | 605 | 907 | 1209 | 93.1 | 96.2 | 96.8 | 97.5 | 97.8 | 97.7 | 97.3 | 93.1 | 96.1 | 96.8 | 97.5 | 97.6 | 97.6 | 97.2 | 93.2 | 96.2 | 96.7 | 97.5 | 97.7 | 97.5 | 97.2 | 2018-05-15 | 2018-10-15
Power Electronics | FS01110CU | Utility Interactive Photovoltaic Inverter | 1250 |  | 97 | Y | N |  | 340 |  |  | 510 | 590 | 800 | 125 | 250 | 375 | 625 | 937.5 | 1250 | 95.7 | 97.4 | 97.8 | 97.8 | 97.5 | 96.9 | 97.5 | 95.3 | 97 | 97.4 | 97.4 | 97.1 | 96.6 | 97.1 | 94.6 | 96.5 | 96.9 | 96.9 | 96.6 | 96.1 | 96.6
Power Electronics | FS1250PU | 1250 kW Utility Interactive Inverter with Medium Voltage NEMA TP1 transformer | 1250 |  | 97 | Y | N |  | 630 |  |  | 585 | 650 | 800 | 125 | 250 | 375 | 625 | 937.5 | 1250 | 95 | 96.7 | 97.2 | 97.4 | 97.2 | 96.6 | 97.1 | 94.7 | 96.6 | 97 | 97.1 | 97 | 96.6 | 96.9 | 94.3 | 96.1 | 96.6 | 96.7 | 96.6 | 96.2 | 96.5
Power Electronics | FS1140CU [420V] | 1270 kW, 420 Vac Utility Interactive Inverter with Medium Voltage Transformer | 1270 | 420 | 97 | N | N | Weighted Efficiency includes MV TP1 Transformer efficiency. | 296 |  |  | 616 | 670 | 800 | 127 | 254 | 381 | 653 | 952.2 | 1270 | 95.6 | 97 | 97.4 | 97.6 | 97.2 | 96.7 | 97.2 | 95.5 | 96.9 | 97.3 | 97.5 | 97.1 | 96.6 | 97.1 | 95.2 | 96.7 | 97.1 | 97.2 | 96.9 | 96.4 | 96.9 |  | 2018-02-15
Power Electronics | FS1271CU [420V] | 1270 kW, 420 Vac Utility Interactive Inverter with Medium Voltage Transformer | 1270 | 420 | 98 | N | N |  | 296 |  |  | 616 | 670 | 800 | 127 | 254 | 381 | 635 | 952.5 | 1270 | 98.2 | 98.3 | 98.4 | 98.5 | 98.3 | 98.1 | 98.3 | 98.1 | 98.2 | 98.3 | 98.4 | 98.2 | 98 | 98.2 | 97.8 | 98 | 98.1 | 98.1 | 98 | 97.8 | 98
Power Electronics | FS1290CU [330V] | 1290.0 kW, 330 Vac Utility Interactive Inverter with Medium Voltage Transformer | 1290 | 330 | 97 | Y | N |  | 603 |  |  | 500 | 575 | 800 | 129 | 258 | 387 | 645 | 967.5 | 1290 | 95.3 | 97 | 97.4 | 97.5 | 97.2 | 96.6 | 97.2 | 95.1 | 96.7 | 97.2 | 97.2 | 97 | 96.5 | 97 | 94.4 | 96.2 | 96.5 | 96.6 | 96.4 | 96 | 96.3
Power Electronics | FS1200CU15 [645V] | 1200 kW, 645 Vac Utility Interactive Inverter with combiner box | 1300.9 | 645 | 97.5 | N | N | Efficiency data inclusive of transformer effect based on 1200 kVA Liquid-Immeresed Distribution Transformers Table in DOE2016. | 348.45 |  |  | 913 | 980 | 1200 | 130 | 260 | 390 | 650 | 976 | 1301 | 93.5 | 96.5 | 97 | 97.7 | 97.8 | 97.7 | 97.5 | 93.5 | 96.5 | 96.9 | 97.6 | 97.7 | 97.6 | 97.4 | 93.5 | 96.5 | 96.9 | 97.6 | 97.8 | 97.6 | 97.4 | 2018-05-15 | 2018-10-15
Power Electronics | FS1190CU [440V] | 1330 kW, 440 Vac Utility Interactive Inverter with Medium Voltage Transformer | 1330 | 440 | 97 | N | N |  | 302 |  |  | 642 | 690 | 800 | 133 | 266 | 399 | 665 | 997.5 | 1330 | 95.6 | 97.1 | 97.5 | 97.7 | 97.4 | 96.8 | 97.3 | 95.5 | 97 | 97.5 | 97.6 | 97.3 | 96.7 | 97.3 | 95.3 | 96.9 | 97.3 | 97.4 | 97.1 | 96.6 | 97.1
Power Electronics | FS1331CU [440V] | 1330 kW, 440 Vac Utility Interactive Inverter with Medium Voltage Transformer | 1330 | 440 | 97 | N | N | Weighted Efficiency includes MV TP1 Transformer efficiency. | 302 |  |  | 642 | 690 | 800 | 133 | 266 | 399 | 665 | 997.5 | 1330 | 95.6 | 97.1 | 97.5 | 97.7 | 97.4 | 96.8 | 97.3 | 95.5 | 97 | 97.5 | 97.6 | 97.3 | 96.7 | 97.3 | 95.3 | 96.9 | 97.3 | 97.4 | 97.1 | 96.6 | 97.1 |  | 2018-02-15
Power Electronics | FS1250CU | 1250 kW Utility Interactive Inverter with Medium Voltage NEMA TP1 transformer | 1362 |  | 97.5 | Y | N |  | 548.9 |  |  | 552 | 615 | 800 | 136.2 | 272.3 | 408.5 | 680.8 | 1021 | 1362 | 96 | 97.5 | 97.9 | 98.1 | 97.9 | 97.4 | 97.8 | 95.6 | 97.2 | 97.6 | 97.8 | 97.5 | 97.1 | 97.5 | 95.2 | 96.8 | 97.2 | 97.3 | 97.1 | 96.7 | 97
Power Electronics | FS1275CU15 [690V] | 1275 kW, 690 Vac Utility Interactive Inverter with combiner box | 1389.08 | 690 | 97 | N | N | Efficiency data inclusive of transformer effect based on 1275 kVA Liquid-Immeresed Distribution Transformers Table in DOE2016. | 353.05 |  |  | 976 | 1030 | 1200 | 139 | 278 | 417 | 695 | 1042 | 1389 | 91.8 | 95.5 | 96.2 | 97.7 | 97.9 | 97.8 | 97.3 | 91.7 | 95.5 | 96.3 | 97.6 | 97.8 | 97.6 | 97.2 | 91.9 | 95.6 | 96.3 | 97.6 | 97.8 | 97.6 | 97.2 | 2018-05-15 | 2018-10-15
Power Electronics | FS1260CU [400V] | 1400 kW, 400 Vac Utility Interactive Inverter with Medium Voltage Transformer | 1400 | 400 | 97 | N | N |  | 308 |  |  | 584 | 650 | 800 | 140 | 580 | 420 | 700 | 1050 | 1400 | 95.5 | 97.1 | 97.6 | 97.6 | 97.3 | 96.8 | 97.3 | 95.4 | 97 | 97.4 | 97.5 | 97.2 | 96.6 | 97.2 | 95 | 96.7 | 97.2 | 97.2 | 96.9 | 96.4 | 96.9
Power Electronics | FS1401CU [400V] | 1400 kW, 400 Vac Utility Interactive Inverter with Medium Voltage Transformer | 1400 | 400 | 97 | Y | N |  | 307.65 |  |  | 584 | 650 | 800 | 140 | 280 | 420 | 700 | 1050 | 1400 | 95.5326 | 97.1484 | 97.5516 | 97.6456 | 97.297 | 96.7531 | 97.2956 | 95.3842 | 97.0123 | 97.4152 | 97.5174 | 97.1653 | 96.6103 | 97.1626 | 95.0314 | 96.721 | 97.1543 | 97.2453 | 96.9218 | 96.4089 | 96.9063
Power Electronics | FS1430CU [330V] | 1430.0 kW, 330 Vac Utility Interactive Inverter with Medium Voltage Transformer | 1430 | 330 | 97 | Y | N |  | 604 |  |  | 500 | 575 | 800 | 143 | 286 | 429 | 715 | 1073 | 1430 | 95.4 | 96.9 | 97.4 | 97.5 | 97.3 | 96.7 | 97.2 | 95.2 | 96.7 | 97.2 | 97.3 | 97.1 | 96.5 | 97 | 94.6 | 96.2 | 96.6 | 96.6 | 96.5 | 96 | 96.4
Power Electronics | FS1330CU [420V] | 1480 kW, 420 Vac Utility Interactive Inverter with Medium Voltage Transformer | 1480 | 420 | 97 | N | N |  | 318 |  |  | 616 | 670 | 800 | 148 | 296 | 444 | 740 | 1110 | 1480 | 95.5 | 97.2 | 97.6 | 97.7 | 97.4 | 96.8 | 97.3 | 95.4 | 97.1 | 97.5 | 97.6 | 97.3 | 96.7 | 97.2 | 95.1 | 96.8 | 97.2 | 97.3 | 97 | 96.5 | 97
Power Electronics | FS1480CU [420V] | 1480 kW, 420 Vac Utility Interactive Inverter with Medium Voltage Transformer | 1480 | 420 | 97 | N | N | Weighted Efficiency includes MV TP1 Transformer efficiency. | 318 |  |  | 616 | 670 | 800 | 148 | 296 | 444 | 740 | 1110 | 1480 | 95.5 | 97.2 | 97.6 | 97.7 | 97.4 | 96.8 | 97.3 | 95.4 | 97.1 | 97.5 | 97.6 | 97.3 | 96.7 | 97.2 | 95.1 | 96.8 | 97.2 | 97.3 | 97 | 96.5 | 97 |  | 2018-02-15
Power Electronics | FS1400CU15 [565V] | 1400 kW, 565 Vac Utility Interactive Inverter with combiner box | 1517.09 | 565 | 97.5 | N | N | Efficiency data inclusive of transformer effect based on 1400 kVA Liquid-Immeresed Distribution Transformers Table in DOE2016. | 359.56 |  |  | 800 | 900 | 1200 | 152 | 303 | 455 | 759 | 1138 | 1517 | 94.3 | 96.5 | 97.3 | 97.7 | 97.8 | 97.6 | 97.5 | 94.3 | 96.4 | 97.2 | 97.7 | 97.7 | 97.5 | 97.4 | 94.4 | 96.5 | 97.2 | 97.6 | 97.7 | 97.5 | 97.5 | 2018-05-15 | 2018-10-15
Power Electronics | FS1530CU [390V] | 1530.0 kW, 390 Vac Utility Interactive Inverter with Medium Voltage Transformer | 1530 | 390 | 97 | Y | N |  | 345 |  |  | 585 | 640 | 800 | 153 | 306 | 459 | 765 | 1148 | 1530 | 95.6 | 97.2 | 97.6 | 97.7 | 97.4 | 96.9 | 97.4 | 95.4 | 97 | 97.4 | 97.5 | 97.3 | 96.8 | 97.2 | 95 | 96.7 | 97 | 97.1 | 96.9 | 96.5 | 96.8
Power Electronics | FS1390CU [440V] | 1550 kW, 440 Vac Utility Interactive Inverter with Medium Voltage Transformer | 1550 | 440 | 97 | N | N |  | 328 |  |  | 642 | 690 | 800 | 155 | 310 | 465 | 775 | 1162.5 | 1550 | 95.7 | 97.2 | 97.5 | 97.6 | 97.4 | 96.8 | 97.2 | 95.5 | 97.1 | 97.5 | 97.6 | 97.3 | 96.8 | 97.2 | 95.2 | 96.9 | 97.3 | 97.4 | 97.1 | 96.6 | 97.1
Power Electronics | FS1550CU [440V] | 1550 kW, 440 Vac Utility Interactive Inverter with Medium Voltage Transformer | 1550 | 440 | 97 | Y | N |  | 327.743 |  |  | 642 | 690 | 800 | 155 | 310 | 465 | 775 | 1162.5 | 1550 | 95.6552 | 97.1814 | 97.5474 | 97.644 | 97.3543 | 96.8248 | 97.3352 | 95.4619 | 97.0913 | 97.4707 | 97.5601 | 97.2682 | 96.7572 | 97.2472 | 95.1767 | 96.8769 | 97.2822 | 97.3862 | 97.0885 | 96.5985 | 97.0627
Power Electronics | FS1500CU15O3 [600V] | 1500 kW, 600 Vac Utility Interactive Inverter with combiner box and a back feed power supply of 10kW to feed solar trackers on the PV power plant | 1594.72 | 600 | 98 | N | N | Efficiency data inclusive of transformer effect based on 1500 kVA Liquid-Immeresed Distribution Transformers Table in DOE2016. | 379.71 |  |  | 849 | 940 | 1200 | 159 | 319 | 478 | 797 | 1196 | 1595 | 96.9 | 97.6 | 97.9 | 98.1 | 98 | 97.9 | 97.9 | 96.6 | 97.5 | 97.8 | 98 | 98 | 97.8 | 97.9 | 96.7 | 97.5 | 97.8 | 98 | 98 | 97.8 | 97.9 | 2018-05-15 | 2018-10-15
Power Electronics | FS1440CU [400V] | 1600 kW, 400 Vac Utility Interactive Inverter with Medium Voltage Transformer | 1600 | 400 | 97 | N | N |  | 340 |  |  | 584 | 650 | 800 | 160 | 320 | 480 | 800 | 1200 | 1600 | 95.6 | 97.2 | 97.6 | 97.6 | 97.3 | 96.7 | 97.3 | 95.5 | 97.1 | 97.4 | 97.5 | 97.2 | 96.6 | 97.2 | 95.2 | 96.8 | 97.2 | 97.2 | 96.9 | 96.4 | 96.9
Power Electronics | FS1600CU [400V] | 1600 kW, 400 Vac Utility Interactive Inverter with Medium Voltage Transformer | 1600 | 400 | 97 | N | N |  | 339.859 |  |  | 584 | 650 | 800 | 160 | 320 | 480 | 800 | 1200 | 1600 | 95.6333 | 97.1795 | 97.5646 | 97.6168 | 97.274 | 96.6975 | 97.2817 | 95.4879 | 97.0566 | 97.4397 | 97.4707 | 97.1501 | 96.5652 | 97.1518 | 95.1515 | 96.7995 | 97.1599 | 97.1889 | 96.9098 | 96.3818 | 96.8962
Power Electronics | FS1475CU15 [600V] | 1475 kW, 600 Vac Utility Interactive Inverter with combiner box | 1610.37 | 600 | 97.5 | N | N | Efficiency data inclusive of transformer effect based on 1475 kVA Liquid-Immeresed Distribution Transformers Table in DOE2016. | 368.71 |  |  | 849 | 940 | 1200 | 161 | 322 | 483 | 805 | 1208 | 1610 | 94.5 | 96.7 | 97.5 | 97.8 | 97.9 | 97.6 | 97.6 | 94.5 | 96.6 | 97.4 | 97.8 | 97.8 | 97.6 | 97.5 | 94.6 | 96.6 | 97.4 | 97.7 | 97.8 | 97.5 | 97.5 | 2018-05-15 | 2018-10-15
Power Electronics | FS1590CU [440V] | 1617 kW, 440 Vac Utility Interactive Inverter with Medium Voltage Transformer | 1617.5 | 440 | 97 | N | N |  | 351 |  |  | 642 | 690 | 800 | 161.75 | 323.49 | 485.24 | 808.74 | 1213.1 | 1617.47 | 95.7 | 97.2 | 97.5 | 97.6 | 97.3 | 96.8 | 97.3 | 95.7 | 97.1 | 97.5 | 97.6 | 97.3 | 96.7 | 97.2 | 95.3 | 96.9 | 97.3 | 97.3 | 97.1 | 96.6 | 97.1
Power Electronics | FS1520CU [420V] | 1690 kW, 420 Vac Utility Interactive Inverter with Medium Voltage Transformer | 1690 | 420 | 97 | N | N |  | 343 |  |  | 616 | 670 | 800 | 169 | 338 | 507 | 845 | 1267.5 | 1690 | 95.7 | 97.2 | 97.6 | 97.6 | 97.3 | 96.7 | 97.3 | 95.6 | 97.1 | 97.5 | 97.5 | 97.3 | 96.7 | 97.2 | 95.3 | 96.9 | 97.2 | 97.3 | 97 | 96.5 | 97
Power Electronics | FS1690CU [420V] | 1690 kW, 420 Vac Utility Interactive Inverter with Medium Voltage Transformer | 1690 | 420 | 97 | N | N |  | 342.523 |  |  | 616 | 670 | 800 | 169 | 338 | 507 | 845 | 1267.5 | 1690 | 95.6594 | 97.2312 | 97.5788 | 97.6328 | 97.345 | 96.7419 | 97.3302 | 95.5735 | 97.1191 | 97.4823 | 97.5387 | 97.2611 | 96.669 | 97.2417 | 95.2881 | 96.8732 | 97.2431 | 97.3128 | 97.0207 | 96.484 | 97.0052
Power Electronics | FS1700CU [390V] | 1700.0 kW, 390 Vac Utility Interactive Inverter with Medium Voltage Transformer | 1700 | 390 | 97 | Y | N |  | 346 |  |  | 585 | 640 | 800 | 170 | 340 | 510 | 850 | 1275 | 1700 | 95.7 | 97.2 | 97.5 | 97.6 | 97.4 | 96.9 | 97.4 | 95.4 | 97 | 97.4 | 97.5 | 97.3 | 96.8 | 97.2 | 94.9 | 96.5 | 97 | 97 | 96.9 | 96.5 | 96.8
Power Electronics | FS1600CU15 [645V] | 1600 kW, 645 Vac Utility Interactive Inverter with combiner box | 1734.81 | 645 | 97.5 | N | N | Efficiency data inclusive of transformer effect based on 1600 kVA Liquid-Immeresed Distribution Transformers Table in DOE2016. | 373.96 |  |  | 913 | 980 | 1200 | 173 | 347 | 520 | 867 | 1301 | 1735 | 94.7 | 96.8 | 97.5 | 98 | 98 | 97.8 | 97.7 | 94.7 | 96.8 | 97.5 | 97.9 | 97.9 | 97.7 | 97.6 | 94.7 | 96.8 | 97.5 | 97.8 | 97.9 | 97.7 | 97.6 | 2018-05-15 | 2018-10-15
Power Electronics | FS1770CU [440V] | 1770 kW, 440 Vac Utility Interactive Inverter with Medium Voltage Transformer | 1770 | 440 | 97 | N | N |  | 351.244 |  |  | 642 | 690 | 800 | 177 | 354 | 531 | 885 | 1327.5 | 1770 | 95.7353 | 97.1908 | 97.5406 | 97.636 | 97.3334 | 96.7563 | 97.3 | 95.664 | 97.1112 | 97.462 | 97.5505 | 97.2678 | 96.6876 | 97.2495 | 95.3184 | 96.9036 | 97.2617 | 97.3465 | 97.1073 | 96.558 | 97.0668
Power Electronics | FS1620CU [400V] | 1800 kW, 400 Vac Utility Interactive Inverter with Medium Voltage Transformer | 1800 | 400 | 97 | N | N |  | 356 |  |  | 584 | 650 | 800 | 180 | 360 | 540 | 900 | 1350 | 1800 | 95.7 | 97.2 | 97.6 | 97.6 | 97.3 | 93.7 | 97.3 | 95.6 | 97.1 | 97.4 | 97.5 | 97.3 | 96.6 | 97.2 | 95.3 | 96.8 | 97.2 | 97.2 | 96.9 | 96.4 | 96.9
Power Electronics | FS1801CU [400V] | 1801 kW, 400 Vac Utility Interactive Inverter with Medium Voltage Transformer | 1800 | 400 | 97 | N | N |  | 355.84 |  |  | 584 | 650 | 800 | 180 | 360 | 540 | 900 | 1350 | 1800 | 95.7155 | 97.1881 | 97.5572 | 97.6193 | 97.2912 | 96.709 | 97.2947 | 95.5786 | 97.0669 | 97.4345 | 97.4902 | 97.1718 | 96.5729 | 97.1713 | 95.2764 | 96.8074 | 97.1822 | 97.2104 | 96.9306 | 96.3813 | 96.9198
Power Electronics | FS1700CU15 [690V] | 1700 kW, 690 Vac Utility Interactive Inverter with combiner box | 1850.63 | 690 | 98 | N | N | Efficiency data inclusive of transformer effect based on 1700 kVA Liquid-Immeresed Distribution Transformers Table in DOE2016. | 368.51 |  |  | 976 | 1030 | 1200 | 185 | 370 | 555 | 925 | 1388 | 1851 | 95 | 97 | 97.7 | 98.1 | 98.2 | 97.9 | 97.9 | 94.9 | 97 | 97.6 | 98.1 | 98 | 97.9 | 97.8 | 94.9 | 96.9 | 97.6 | 98 | 98.1 | 97.8 | 97.8 | 2018-05-15 | 2018-10-15
Power Electronics | FS1750CU15 [565V] | 1750 kW, 565 Vac Utility Interactive Inverter with combiner box | 1896.53 | 565 | 97.5 | N | N | Efficiency data inclusive of transformer effect based on 1750 kVA Liquid-Immeresed Distribution Transformers Table in DOE2016. | 378.47 |  |  | 800 | 900 | 1200 | 190 | 379 | 569 | 948 | 1422 | 1897 | 94.8 | 96.6 | 97.4 | 98 | 97.9 | 97.7 | 97.6 | 94.8 | 96.5 | 97.3 | 97.8 | 97.8 | 97.6 | 97.5 | 94.7 | 96.4 | 97.3 | 97.8 | 97.8 | 97.5 | 97.5 | 2018-05-15 | 2018-10-15
Power Electronics | FS1710CU [420V] | 1900 kW, 420 Vac Utility Interactive Inverter with Medium Voltage Transformer | 1900 | 420 | 97 | N | N |  | 363 |  |  | 616 | 670 | 800 | 190 | 380 | 570 | 950 | 1425 | 1900 | 95.7 | 97.2 | 97.6 | 97.6 | 97.3 | 96.7 | 97.3 | 95.6 | 97.1 | 97.5 | 97.5 | 97.2 | 96.7 | 97.2 | 95.4 | 96.8 | 97.2 | 97.3 | 97 | 96.5 | 97
Power Electronics | FS1901CU [420V] | 1901 kW, 420 Vac Utility Interactive Inverter with Medium Voltage Transformer | 1900 | 420 | 97 | N | N |  | 362.802 |  |  | 616 | 670 | 800 | 190 | 380 | 570 | 950 | 1425 | 1900 | 95.7244 | 97.1882 | 97.5627 | 97.6299 | 97.3026 | 96.7121 | 97.3042 | 95.6152 | 97.089 | 97.4872 | 97.5311 | 97.2134 | 96.6755 | 97.2159 | 95.3576 | 96.8401 | 97.2392 | 97.2703 | 97.0404 | 96.4615 | 97.0063
Power Electronics | FS1850CU15O3 [600V] | 1850 kW, 600 Vac Utility Interactive Inverter with combiner box and a back feed power supply of 10kW to feed solar trackers on the PV power plant | 1974.29 | 600 | 98 | N | N | Efficiency data inclusive of transformer effect based on 1850 kVA Liquid-Immeresed Distribution Transformers Table in DOE2016. | 397.3 |  |  | 849 | 940 | 1200 | 197 | 395 | 592 | 987 | 1481 | 1974 | 96.9 | 97.7 | 97.9 | 98.1 | 98.1 | 97.9 | 98 | 96.7 | 97.5 | 97.8 | 98 | 98 | 97.8 | 97.9 | 96.8 | 97.6 | 97.9 | 98 | 98 | 97.8 | 97.9 | 2018-05-15 | 2018-10-15
Power Electronics | FS1790CU [440V] | 1990 kW, 440 Vac Utility Interactive Inverter with Medium Voltage Transformer | 1990 | 440 | 97 | N | N |  | 371 |  |  | 642 | 690 | 800 | 199 | 398 | 597 | 995 | 1492.5 | 1990 | 95.7 | 97.2 | 97.6 | 97.6 | 97.3 | 96.6 | 97.3 | 95.6 | 97.1 | 97.5 | 97.5 | 97.2 | 96.5 | 97.2 | 95.4 | 96.9 | 97.3 | 97.3 | 97 | 96.4 | 97
Power Electronics | FS1991CU [440V] | 1990 kW, 440 Vac Utility Interactive Inverter with Medium Voltage Transformer | 1990 | 440 | 97 | N | N |  | 370.81 |  |  | 642 | 690 | 800 | 199 | 398 | 597 | 995 | 1492.5 | 1990 | 95.713 | 97.176 | 97.5652 | 97.6151 | 97.3002 | 96.5736 | 97.2921 | 95.6172 | 97.1016 | 97.4866 | 97.5364 | 97.2267 | 96.5224 | 97.217 | 95.4006 | 96.9315 | 97.3019 | 97.3425 | 97.0467 | 96.3857 | 97.0348
Power Electronics | FS1800CU [400V] | 2000 kW, 400 Vac Utility Interactive Inverter with Medium Voltage Transformer | 2000 | 400 | 97 | N | N |  | 381 |  |  | 584 | 650 | 800 | 200 | 400 | 600 | 1000 | 1500 | 2000 | 95.8 | 97.2 | 97.6 | 97.6 | 97.2 | 96.6 | 97.3 | 95.6 | 97.1 | 97.4 | 97.5 | 97.1 | 96.4 | 97.1 | 95.4 | 96.8 | 97.2 | 97.2 | 96.9 | 96.2 | 96.9
Power Electronics | FS2000CU [400V] | 2000 kW, 400 Vac Utility Interactive Inverter with Medium Voltage Transformer | 2000 | 400 | 97 | N | N | Weighted Efficiency includes MV TP1 Transformer efficiency. | 381 |  |  | 548 | 650 | 800 | 200 | 400 | 600 | 1000 | 1500 | 2000 | 95.8 | 97.2 | 97.6 | 97.6 | 97.2 | 96.6 | 97.3 | 95.6 | 97.1 | 97.4 | 97.5 | 97.1 | 96.4 | 97.1 | 95.4 | 96.8 | 97.2 | 97.2 | 96.9 | 96.2 | 96.9 |  | 2018-02-15
Power Electronics | FS1850CU15 [600V] | 1850 kW, 600 Vac Utility Interactive Inverter with combiner box | 2020.96 | 600 | 97.5 | N | N | Efficiency data inclusive of transformer effect based on 1850 kVA Liquid-Immeresed Distribution Transformers Table in DOE2016. | 388.77 |  |  | 849 | 940 | 1200 | 202 | 404 | 606 | 1010 | 1516 | 2021 | 95.1 | 96.7 | 97.5 | 98 | 98 | 97.8 | 97.8 | 95 | 96.6 | 97.5 | 97.9 | 97.9 | 97.7 | 97.7 | 95 | 96.6 | 97.4 | 97.9 | 97.9 | 97.6 | 97.7 | 2018-05-15 | 2018-10-15
Power Electronics | FS2000K [600V] | 2100 kW, 600 Vac Utility Interactive Inverter | 2103.416 | 600 | 98 | N | N | Efficiency data inclusive of transformer effect based on 2100 kVA Liquid-Immeresed Distribution Transformers Table in DOE2016. The inverter is central control composed by 4 modules. |  |  |  | 849 | 940 | 1200 | 210.3416 | 420.6832 | 631.0248 | 1051.708 | 1577.562 | 2103.416 | 96.0919 | 97.5238 | 97.9704 | 98.3806 | 98.2078 | 97.9134 | 98.082 | 96.1235 | 97.504 | 97.9438 | 98.2085 | 98.1306 | 97.7279 | 97.9928 | 96.1964 | 97.4535 | 97.9859 | 98.3557 | 98.141 | 97.7477 | 98.0356 | 2019-04-02
Power Electronics | FS1900CU [420V] | 2110 kW, 420 Vac Utility Interactive Inverter with Medium Voltage Transformer | 2110 | 420 | 97 | N | N |  | 388 |  |  | 616 | 670 | 800 | 211 | 422 | 633 | 1055 | 1582.5 | 2110 | 95.7 | 97.2 | 97.6 | 97.6 | 97.2 | 96.6 | 97.3 | 95.7 | 97.1 | 97.5 | 97.5 | 97.1 | 96.6 | 97.2 | 95.4 | 96.9 | 97.3 | 97.3 | 96.9 | 96.4 | 97
Power Electronics | FS2110CU [420V] | 2110 kW, 420 Vac Utility Interactive Inverter with Medium Voltage Transformer | 2110 | 420 | 97 | N | N | Weighted Efficiency includes MV TP1 Transformer efficiency. | 388 |  |  | 616 | 670 | 800 | 211 | 422 | 633 | 1055 | 1582.5 | 2110 | 95.7 | 97.2 | 97.6 | 97.6 | 97.2 | 96.6 | 97.3 | 95.7 | 97.3 | 97.5 | 97.5 | 97.1 | 96.6 | 97.2 | 95.4 | 96.9 | 97.3 | 97.3 | 96.9 | 96.4 | 97 |  | 2018-02-15
Power Electronics | FS2000CU15 [645V] | 2000 kW, 645 Vac Utility Interactive Inverter with combiner box | 2162.42 | 645 | 98 | N | N | Efficiency data inclusive of transformer effect based on 2000 kVA Liquid-Immeresed Distribution Transformers Table in DOE2016. | 388.97 |  |  | 913 | 980 | 1200 | 216 | 432 | 649 | 1081 | 1622 | 2162 | 95.2 | 96.9 | 97.6 | 98.1 | 98.1 | 97.9 | 97.9 | 95.2 | 96.8 | 97.5 | 98 | 98 | 97.8 | 97.8 | 95.2 | 96.8 | 97.5 | 98 | 98 | 97.8 | 97.7 | 2018-05-15 | 2018-10-15
Power Electronics | FS2000M [34000V] | 2000 kW, 34 kV, Utility Interactive Inverter with internal transformer | 2178.068 | 34500 | 97 | N | N | Inverters are modular and can be composed by 4 or 6 modules. No differences between modules, they use the same components. Each module can have a different internal working voltage (600V, 615V, 630V, 645V, 660V) but the equipment always incorporates internal Medium Voltage transformer (ABB Model: 1LES500018-000), in order to provide the same maximum output voltage (34.5 kV + or - 10%). |  |  |  | 849 | 940 | 1200 | 217.8068 | 435.6136 | 653.4204 | 1089.034 | 1633.551 | 2178.068 | 93.4983 | 95.9935 | 96.8011 | 97.4581 | 97.6572 | 97.5548 | 97.258 | 93.3492 | 95.8983 | 96.8261 | 97.396 | 97.5629 | 97.4223 | 97.1806 | 93.4114 | 95.9287 | 96.709 | 97.3923 | 97.6181 | 97.4835 | 97.2021 | 2019-03-15
Power Electronics | FS1980CU [440V] | 2200 kW, 440 Vac Utility Interactive Inverter with Medium Voltage Transformer | 2200 | 440 | 97 | N | N |  | 396 |  |  | 642 | 690 | 800 | 220 | 440 | 660 | 1100 | 1650 | 2200 | 95.7 | 97.2 | 97.6 | 97.6 | 97.3 | 96.7 | 97.3 | 95.7 | 97.1 | 97.5 | 97.5 | 97.2 | 96.7 | 97.2 | 95.5 | 97 | 97.3 | 97.4 | 97.1 | 96.5 | 97.1
Power Electronics | FS2200CU [440V] | 2200 kW, 440 Vac Utility Interactive Inverter with Medium Voltage Transformer | 2200 | 440 | 97 | N | N | Weighted Efficiency includes MV TP1 Transformer efficiency. | 396 |  |  | 642 | 690 | 800 | 220 | 440 | 660 | 1100 | 1650 | 2200 | 95.8 | 97.2 | 97.6 | 97.6 | 97.3 | 96.7 | 97.3 | 95.7 | 97.1 | 97.5 | 97.5 | 97.2 | 96.7 | 97.2 | 95.5 | 97 | 97.3 | 97.4 | 97.1 | 96.5 | 97.1 |  | 2018-02-15
Power Electronics | FS2100CU15 [565V] | 2100 kW, 565 Vac Utility Interactive Inverter with combiner box | 2275.89 | 565 | 97.5 | N | N | Efficiency data inclusive of transformer effect based on 2100 kVA Liquid-Immeresed Distribution Transformers Table in DOE2016. | 398.85 |  |  | 800 | 900 | 1200 | 228 | 455 | 683 | 1138 | 1707 | 2276 | 95.4 | 97.2 | 97.6 | 98 | 98 | 97.7 | 97.8 | 95.2 | 97.1 | 97.6 | 97.9 | 97.8 | 97.6 | 97.7 | 95.3 | 97 | 97.5 | 97.9 | 97.8 | 97.6 | 97.7 | 2018-05-15 | 2018-10-15
Power Electronics | FS2125CU15 [690V] | 2125 kW, 690 Vac Utility Interactive Inverter with combiner box | 2306.41 | 690 | 98 | N | N | Efficiency data inclusive of transformer effect based on 2125 kVA Liquid-Immeresed Distribution Transformers Table in DOE2016. | 390.63 |  |  | 976 | 1030 | 1200 | 231 | 461 | 692 | 1153 | 1730 | 2306 | 95.6 | 97.1 | 97.8 | 98.2 | 98.2 | 98 | 98 | 95.6 | 97.1 | 97.7 | 98.1 | 98.1 | 97.9 | 97.9 | 95.5 | 97 | 97.6 | 98.1 | 98.1 | 97.8 | 97.9 | 2018-05-15 | 2018-10-15
Power Electronics | FS2225CU15 [600V] | 2225 kW, 600 Vac Utility Interactive Inverter with combiner box | 2417.08 | 600 | 97.5 | N | N | Efficiency data inclusive of transformer effect based on 2225 kVA Liquid-Immeresed Distribution Transformers Table in DOE2016. | 403.32 |  |  | 849 | 940 | 1200 | 242 | 483 | 725 | 1209 | 1813 | 2417 | 95.5 | 97.2 | 97.7 | 98.1 | 98.1 | 97.8 | 97.9 | 95.5 | 97.2 | 97.7 | 98 | 98 | 97.7 | 97.8 | 95.4 | 97.1 | 97.6 | 98 | 98 | 97.7 | 97.8 | 2018-05-15 | 2018-10-15
Power Electronics | FS2250CU15O3 [600V] | 2250 kW, 600 Vac Utility Interactive Inverter with combiner box and a back feed power supply of 10kW to feed solar trackers on the PV power plant | 2420.37 | 600 | 98 | N | N | Efficiency data inclusive of transformer effect based on 2250 kVA Liquid-Immeresed Distribution Transformers Table in DOE2016. | 416.47 |  |  | 849 | 940 | 1200 | 242 | 484 | 726 | 1210 | 1815 | 2420 | 97.2 | 97.8 | 98 | 98.2 | 98.1 | 97.9 | 98 | 96.9 | 97.8 | 98 | 98 | 98 | 97.7 | 97.9 | 96.9 | 97.7 | 97.9 | 98.1 | 98 | 97.8 | 97.9 | 2018-05-15 | 2018-10-15
Power Electronics | FS2150CU15 [645V] | 2150 kW, 645 Vac Utility Interactive Inverter with combiner box | 2558.48 | 645 | 98 | N | N | Efficiency data inclusive of transformer effect based on 2150 kVA Liquid-Immeresed Distribution Transformers Table in DOE2016. | 409.99 |  |  | 913 | 980 | 1200 | 256 | 512 | 768 | 1279 | 1919 | 2558 | 95.7 | 97.4 | 97.8 | 98.1 | 98.1 | 97.9 | 97.9 | 95.6 | 97.3 | 97.8 | 98.1 | 98.1 | 97.8 | 97.9 | 95.6 | 97.3 | 97.7 | 98.1 | 98.1 | 97.8 | 97.9 | 2018-05-15 | 2018-10-15
Power Electronics | FS2400CU15 [645V] | 2400 kW, 645 Vac Utility Interactive Inverter with combiner box | 2583.76 | 645 | 98 | N | N | Efficiency data inclusive of transformer effect based on 2400 kVA Liquid-Immeresed Distribution Transformers Table in DOE2016. | 407.44 |  |  | 913 | 980 | 1200 | 258 | 517 | 775 | 1292 | 1938 | 2584 | 95.8 | 97.4 | 97.9 | 98.1 | 98.1 | 97.9 | 98 | 95.8 | 97.4 | 97.7 | 98.1 | 98.1 | 97.8 | 97.9 | 95.7 | 97.3 | 97.7 | 98.1 | 98 | 97.8 | 97.9 | 2018-05-15 | 2018-10-15
Power Electronics | FS2450CU15 [565V] | 2450 kW, 565 Vac Utility Interactive Inverter with combiner box | 2664.07 | 565 | 97.5 | N | N | Efficiency data inclusive of transformer effect based on 2450 kVA Liquid-Immeresed Distribution Transformers Table in DOE2016. | 417.35 |  |  | 800 | 900 | 1200 | 266 | 533 | 799 | 1332 | 1998 | 2664 | 95.7 | 97.3 | 97.6 | 98 | 98 | 97.7 | 97.8 | 95.6 | 97.2 | 97.6 | 97.9 | 97.9 | 97.6 | 97.7 | 95.6 | 97.2 | 97.5 | 97.9 | 97.9 | 97.6 | 97.7 | 2018-05-15 | 2018-10-15
Power Electronics | FS2550CU15 [690V] | 2250 kW, 690 Vac Utility Interactive Inverter with combiner box | 2759.39 | 690 | 98 | N | N | Efficiency data inclusive of transformer effect based on 2550 kVA Liquid-Immeresed Distribution Transformers Table in DOE2016. | 408.29 |  |  | 976 | 1030 | 1200 | 276 | 552 | 828 | 1380 | 2070 | 2759 | 96 | 97.5 | 97.9 | 98.2 | 98.2 | 97.9 | 98 | 95.9 | 97.4 | 97.8 | 98.2 | 98.1 | 97.8 | 97.9 | 95.9 | 97.4 | 97.8 | 98.1 | 98.1 | 97.9 | 98 | 2018-05-15 | 2018-10-15
Power Electronics | FS2300CU15 [690V] | 2300 kW, 690 Vac Utility Interactive Inverter with combiner box | 2759.49 | 690 | 98 | N | N | Efficiency data inclusive of transformer effect based on 2300 kVA Liquid-Immeresed Distribution Transformers Table in DOE2016. | 408.67 |  |  | 976 | 1030 | 1200 | 276 | 552 | 828 | 1380 | 2070 | 2759 | 95.9 | 97.5 | 97.9 | 98.2 | 98.2 | 98 | 98 | 95.8 | 97.4 | 97.8 | 98.1 | 98.2 | 97.9 | 98 | 95.8 | 97.4 | 97.8 | 98.2 | 98.1 | 97.9 | 98 | 2018-05-15 | 2018-10-15
Power Electronics | FS2600CU15O3 [600V] | 2600 kW, 600 Vac Utility Interactive Inverter with combiner box and a back feed power supply of 10kW to feed solar trackers on the PV power plant | 2770.2 | 600 | 98 | N | N | Efficiency data inclusive of transformer effect based on 2600 kVA Liquid-Immeresed Distribution Transformers Table in DOE2016. | 433.54 |  |  | 849 | 940 | 1200 | 277 | 554 | 831 | 1385 | 2078 | 2770 | 97.2 | 97.9 | 98.1 | 98.2 | 98.1 | 97.9 | 98 | 97.1 | 97.8 | 98 | 98 | 98 | 97.8 | 98 | 97.1 | 97.8 | 98 | 98.1 | 98 | 97.8 | 98 | 2018-05-15 | 2018-10-15
Power Electronics | FS2600CU15 [600V] | 2600 kW, 600 Vac Utility Interactive Inverter with combiner box | 2821.84 | 600 | 98 | N | N | Efficiency data inclusive of transformer effect based on 2600 kVA Liquid-Immeresed Distribution Transformers Table in DOE2016. | 423.67 |  |  | 849 | 940 | 1200 | 282 | 564 | 847 | 1411 | 2116 | 2822 | 95.7 | 97.4 | 97.9 | 98.1 | 98 | 97.8 | 97.9 | 95.7 | 97.3 | 97.8 | 98.1 | 98 | 97.7 | 97.8 | 95.7 | 97.2 | 97.7 | 98 | 98 | 97.7 | 97.8 | 2018-05-15 | 2018-10-15
Power Electronics | FS2840M [34000V] | 2840 kW, 34 kV, Utility Interactive Inverter with internal transformer | 2844.7 | 34500 | 97.5 | N | N | Inverters are modular and can be composed by 4 or 6 modules. No differences between modules, they use the same components. Each module can have a different internal working voltage (600V, 615V, 630V, 645V, 660V) but the equipment always incorporates internal Medium Voltage transformer (ABB Model: 1LES500018-000), in order to provide the same maximum output voltage (34.5 kV + or - 10%). |  |  |  | 849 | 940 | 1200 | 284.47 | 568.94 | 853.41 | 1422.35 | 2133.525 | 2844.7 | 94.4413 | 96.5602 | 97.2233 | 97.6279 | 97.7507 | 97.6516 | 97.4648 | 94.3535 | 96.4533 | 97.1235 | 97.5301 | 97.6348 | 97.5292 | 97.3559 | 94.3096 | 96.5127 | 97.1355 | 97.5968 | 97.707 | 97.5485 | 97.4118 | 2019-03-15
Power Electronics | FS3001M [34000V] | 3000 kW, 34 kV, Utility Interactive Inverter with internal transformer | 3017.848 | 34500 | 97.5 | N | N | Inverters are modular and can be composed by 4 or 6 modules. No differences between modules, they use the same components. Each module can have a different internal working voltage (600V, 615V, 630V, 645V, 660V) but the equipment always incorporates internal Medium Voltage transformer (ABB Model: 1LES500018-000), in order to provide the same maximum output voltage (34.5 kV + or - 10%). |  |  |  | 849 | 940 | 1200 | 301.7848 | 603.5696 | 905.3544 | 1508.924 | 2263.386 | 3017.848 | 94.6253 | 96.6462 | 97.2747 | 97.6765 | 97.7113 | 97.5625 | 97.4675 | 94.5552 | 96.5905 | 97.182 | 97.5764 | 97.6672 | 97.4448 | 97.4005 | 94.5184 | 96.5838 | 97.1884 | 97.6148 | 97.7037 | 97.4863 | 97.4289 | 2019-03-15
Power Electronics | FS2800CU15 [645V] | 2800 kW, 645 Vac Utility Interactive Inverter with combiner box | 3024.91 | 645 | 98 | N | N | Efficiency data inclusive of transformer effect based on 2800 kVA Liquid-Immeresed Distribution Transformers Table in DOE2016. | 427.54 |  |  | 913 | 940 | 1200 | 302 | 605 | 907 | 1512 | 2269 | 3025 | 96 | 97.4 | 97.9 | 98.1 | 98.1 | 97.9 | 98 | 95.9 | 97.4 | 97.8 | 98.1 | 98.1 | 97.8 | 97.9 | 95.9 | 97.3 | 97.7 | 98.1 | 98 | 97.8 | 97.9 | 2018-05-15 | 2018-10-15
Power Electronics | FS3000M [34000V] | 3000 kW, 34 kV, Utility Interactive Inverter with internal transformer | 3109.266 | 34500 | 97.5 | N | N | Inverters are modular and can be composed by 4 or 6 modules. No differences between modules, they use the same components. Each module can have a different internal working voltage (600V, 615V, 630V, 645V, 660V) but the equipment always incorporates internal Medium Voltage transformer (ABB Model: 1LES500018-000), in order to provide the same maximum output voltage (34.5 kV + or - 10%). |  |  |  | 849 | 940 | 1200 | 310.9266 | 621.8532 | 932.7798 | 1554.633 | 2331.9495 | 3109.266 | 94.9749 | 96.8471 | 97.3723 | 97.6775 | 97.6602 | 97.3399 | 97.4652 | 94.9428 | 96.7736 | 97.3237 | 97.6181 | 97.528 | 97.2027 | 97.365 | 94.9123 | 96.8194 | 97.3539 | 97.6385 | 97.5917 | 97.2755 | 97.4114 | 2019-03-15
Power Electronics | FS3000CU15 [690V] | 3000 kW, 690 Vac Utility Interactive Inverter with combiner box | 3201.17 | 690 | 98 | N | N | Efficiency data inclusive of transformer effect based on 3000 kVA Liquid-Immeresed Distribution Transformers Table in DOE2016. | 426.4 |  |  | 976 | 1030 | 1200 | 320 | 640 | 960 | 1601 | 2401 | 3201 | 96.1 | 97.5 | 97.9 | 98.2 | 98.3 | 98.1 | 98.1 | 96 | 97.5 | 97.9 | 98.1 | 98.2 | 98 | 98 | 95.9 | 97.5 | 97.9 | 98.2 | 98.2 | 97.9 | 98 | 2018-05-15 | 2018-10-15
Power Electronics | FS3150M [34000V] | 3150 kW, 34 kV, Utility Interactive Inverter with internal transformer | 3307.98 | 34500 | 97.5 | N | N | Inverters are modular and can be composed by 4 or 6 modules. No differences between modules, they use the same components. Each module can have a different internal working voltage (600V, 615V, 630V, 645V, 660V) but the equipment always incorporates internal Medium Voltage transformer (ABB Model: 1LES500018-000), in order to provide the same maximum output voltage (34.5 kV + or - 10%). |  |  |  | 891 | 970 | 1200 | 330.798 | 661.596 | 992.394 | 1653.99 | 2480.985 | 3307.98 | 95.0211 | 96.9027 | 97.4342 | 97.7515 | 97.6422 | 97.3662 | 97.4845 | 94.9579 | 96.7802 | 97.3562 | 97.6708 | 97.5884 | 97.2348 | 97.4145 | 94.9742 | 96.7828 | 97.3475 | 97.6939 | 97.6 | 97.309 | 97.429 | 2019-03-15
Power Electronics | FS3225M [34000V] | 3225 kW, 34 kV, Utility Interactive Inverter with internal transformer | 3367.326 | 34500 | 97.5 | N | N | Inverters are modular and can be composed by 4 or 6 modules. No differences between modules, they use the same components. Each module can have a different internal working voltage (600V, 615V, 630V, 645V, 660V) but the equipment always incorporates internal Medium Voltage transformer (ABB Model: 1LES500018-000), in order to provide the same maximum output voltage (34.5 kV + or - 10%). |  |  |  | 913 | 980 | 1200 | 336.7326 | 673.4652 | 1010.1978 | 1683.663 | 2525.4945 | 3367.326 | 95.0183 | 96.8928 | 97.3979 | 97.7634 | 97.7231 | 96.9255 | 97.503 | 94.9704 | 96.8221 | 97.331 | 97.6393 | 97.6318 | 96.8405 | 97.4108 | 94.9604 | 96.7692 | 97.3276 | 97.6807 | 97.6328 | 97.003 | 97.4246 | 2019-03-15
Powercom | SLK-1500 [208V] | 1.5 kW, 208 Vac Utility Interactive Inverter | 1.55 | 208 | 94.5 | Y | N |  | 0.21 |  |  | 100 | 325 | 360 | 0.155 | 0.31 | 0.465 | 0.775 | 1.163 | 1.55 | 84.46 | 90.49 | 92.52 | 94.25 | 94.92 | 95.02 | 93.86 | 85.04 | 91.04 | 93.19 | 94.79 | 95.41 | 95.53 | 94.38 | 85.31 | 91.19 | 93.54 | 95.02 | 95.55 | 95.76 | 94.58
Powercom | SLK-1500 [240V] | 1.5 kW, 240 Vac Utility Interactive Inverter | 1.55 | 240 | 94.5 | Y | N |  | 0.32 |  |  | 100 | 325 | 360 | 0.155 | 0.31 | 0.465 | 0.775 | 1.163 | 1.55 | 84.62 | 90.46 | 92.57 | 94.42 | 95.07 | 95.25 | 93.99 | 84.89 | 90.97 | 93.04 | 94.81 | 95.51 | 95.73 | 94.42 | 85.22 | 91.38 | 93.44 | 95.12 | 95.65 | 95.93 | 94.66
Powercom | SLK-2000 [208V] | 2 kW, 208 Vac Utility Interactive Inverter | 2.06 | 208 | 95.5 | Y | N |  | 0.29 |  |  | 100 | 325 | 360 | 0.206 | 0.412 | 0.618 | 1.03 | 1.545 | 2.06 | 88.28 | 93.12 | 94.41 | 95.27 | 95.43 | 95.37 | 94.87 | 89.63 | 93.68 | 94.91 | 95.73 | 95.84 | 95.8 | 95.34 | 89.74 | 94.01 | 95.11 | 96.13 | 96.38 | 96.07 | 95.77
Powercom | SLK-2000 [240V] | 2 kW, 240 Vac Utility Interactive Inverter | 2.06 | 240 | 95 | Y | N |  | 0.36 |  |  | 100 | 325 | 360 | 0.206 | 0.412 | 0.618 | 1.03 | 1.545 | 2.06 | 86.91 | 92.14 | 93.78 | 94.94 | 95.3 | 95.37 | 94.55 | 87.84 | 92.87 | 94.26 | 95.56 | 95.79 | 95.73 | 95.09 | 88.1 | 93.05 | 94.37 | 95.71 | 96 | 95.94 | 95.28
Powercom | SLK-3000 [208V] | 3 kW, 208 Vac Utility Interactive Inverter | 3 | 208 | 95.5 | Y | N |  | 0.18 |  |  | 100 | 325 | 360 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 91.57 | 94.41 | 95.16 | 95.47 | 95.31 | 94.62 | 95.1 | 92.05 | 94.92 | 95.58 | 95.89 | 95.76 | 95.37 | 95.56 | 92.22 | 95.17 | 95.79 | 96.25 | 95.93 | 95.8 | 95.78
Powercom | SLK-3000 [240V] | 3 kW, 240 Vac Utility Interactive Inverter | 3.01 | 240 | 95.5 | Y | N |  | 0.25 |  |  | 100 | 325 | 360 | 0.301 | 0.602 | 0.903 | 1.505 | 2.258 | 3.01 | 90 | 93.9 | 94.85 | 95.4 | 95.31 | 94.83 | 94.97 | 90.64 | 94.34 | 95.34 | 95.79 | 95.87 | 95.6 | 95.49 | 91 | 94.59 | 95.44 | 95.97 | 96.01 | 95.77 | 95.65
Powercom | SLK-4000 [208V] | 4 kW, 208 Vac Utility Interactive Inverter | 3.98 | 208 | 95.5 | Y | N |  | 0.18 |  |  | 100 | 325 | 360 | 0.398 | 0.796 | 1.194 | 1.99 | 2.985 | 3.98 | 90.53 | 94.32 | 95.17 | 95.44 | 95.41 | 95.16 | 95.13 | 91.58 | 94.87 | 95.63 | 96.05 | 96 | 95.45 | 95.7 | 91.82 | 95.03 | 95.8 | 96.45 | 96.31 | 95.76 | 96.01
Powercom | SLK-4000 [240V] | 4 kW, 240 Vac Utility Interactive Inverter | 3.99 | 240 | 96 | Y | N |  | 0.25 |  |  | 100 | 325 | 360 | 0.399 | 0.798 | 1.197 | 1.995 | 2.993 | 3.99 | 90.55 | 94.3 | 95.24 | 95.69 | 95.74 | 95.56 | 95.38 | 91.53 | 94.95 | 95.81 | 96.33 | 96.33 | 96.05 | 95.99 | 91.95 | 95.23 | 95.96 | 96.4 | 96.48 | 96.25 | 96.15
Powercom | SLK-4000 [277V] | 4 kW, 277 Vac Utility Interactive Inverter | 4.02 | 277 | 95.5 | Y | N |  | 0.29 |  |  | 100 | 332 | 360 | 0.4 | 0.8 | 1.21 | 2.01 | 3.02 | 4.02 | 89.9 | 93.4 | 94.5 | 95.2 | 95.3 | 95.2 | 94.9 | 90.8 | 94.1 | 95 | 95.7 | 95.8 | 95.8 | 95.4 | 91 | 94.3 | 95.3 | 95.9 | 96 | 96 | 95.6
Power-One | MICRO-0.25-I-OUTD-US-208 [208V] | 250 W Utility Interactive Inverter | 0.25 | 208 | 96 | N | Y | Multiple Listing of ABB | 0.02 |  |  | 30 | 40 | 50 | 0.03 | 0.05 | 0.08 | 0.13 | 0.19 | 0.25 | 91.2 | 94.5 | 95.4 | 96 | 96.2 | 96.2 | 95.8 | 91.5 | 94.4 | 95.5 | 96.2 | 96.3 | 96.4 | 95.9 | 91.2 | 94.3 | 95.3 | 96.2 | 96.2 | 96.4 | 95.8
Power-One | MICRO-0.25-I-OUTD-US-240 [240V] | 250 W Utility Interactive Inverter | 0.25 | 240 | 96 | N | Y | Multiple Listing of ABB | 0.05 |  |  | 30 | 40 | 50 | 0.03 | 0.05 | 0.08 | 0.13 | 0.19 | 0.25 | 90.8 | 94.2 | 95.4 | 96 | 96.1 | 96.2 | 95.7 | 91.2 | 94.2 | 95.3 | 96.3 | 96.2 | 96.5 | 95.8 | 90.5 | 94 | 95.3 | 96.3 | 96.1 | 96.5 | 95.8
Power-One | MICRO-0.3HV-I-OUTD-US-208 [208V] | 300 W Utility Interactive Inverter | 0.3 | 208 | 96 | N | Y | Multiple Listing of ABB | 0.06 |  |  | 30 | 45 | 60 | 0.03 | 0.06 | 0.09 | 0.15 | 0.225 | 0.3 | 92.8 | 95.2 | 95.8 | 96.1 | 96 | 95.6 | 95.8 | 92.3 | 95 | 95.8 | 96.2 | 96.3 | 96.3 | 96 | 91.9 | 94.9 | 95.7 | 96.2 | 96.2 | 96.2 | 95.9
Power-One | MICRO-0.3HV-I-OUTD-US-240 [240V] | 300 W Utility Interactive Inverter | 0.3 | 240 | 96 | N | Y | Multiple Listing of ABB | 0.06 |  |  | 30 | 45 | 60 | 0.03 | 0.06 | 0.09 | 0.15 | 0.225 | 0.3 | 92.4 | 95 | 95.7 | 96 | 96 | 95.7 | 95.8 | 91.8 | 94.7 | 95.8 | 96.2 | 96.4 | 96.4 | 96 | 91.7 | 94.6 | 95.6 | 96.1 | 96.2 | 96.4 | 95.8
Power-One | MICRO-0.3-I-OUTD-US-208 [208V] | 300 W Utility Interactive Inverter | 0.3 | 208 | 96 | N | Y | Multiple Listing of ABB | 0.02 |  |  | 30 | 40 | 50 | 0.03 | 0.06 | 0.09 | 0.15 | 0.23 | 0.3 | 92 | 95 | 95.8 | 96 | 96.2 | 96 | 95.9 | 92.2 | 94.9 | 95.8 | 96.3 | 96.4 | 96.4 | 96 | 91.7 | 94.8 | 95.6 | 96.2 | 96.3 | 96.4 | 96
Power-One | MICRO-0.3-I-OUTD-US-240 [240V] | 300 W Utility Interactive Inverter | 0.3 | 240 | 96 | N | Y | Multiple Listing of ABB | 0.05 |  |  | 30 | 40 | 50 | 0.03 | 0.06 | 0.09 | 0.15 | 0.23 | 0.3 | 91.7 | 94.8 | 95.8 | 96 | 96.1 | 96 | 95.8 | 92 | 94.8 | 95.7 | 96.3 | 96.4 | 96.4 | 96 | 91.6 | 94.7 | 95.6 | 96.3 | 96.4 | 96.5 | 96
Power-One | UNO-2.0-I-OUTD-S-US [208V] | 2 kW, 208 Vac Utility Interactive Inverter. Model Number may include -W | 2 | 208 | 95.5 | Y | N | Multiple Listing of ABB | 0.4 | 2 | 0.4 | 100 | 330 | 416 | 0.2 | 0.4 | 0.6 | 1 | 1.5 | 2 | 90.4 | 94.2 | 95.5 | 95.9 | 95.6 | 95 | 95.4 | 88.3 | 94.1 | 95.3 | 96.1 | 96.1 | 96 | 95.6 | 85.6 | 92.5 | 94.3 | 95.6 | 95.8 | 95.8 | 95
Power-One | UNO-2.0-I-OUTD-S-US [240V] | 2 kW, 240 Vac Utility Interactive Inverter. Model Number may include -W | 2 | 240 | 95.5 | Y | N | Multiple Listing of ABB | 0.4 | 2 | 0.4 | 100 | 340 | 416 | 0.2 | 0.4 | 0.6 | 1 | 1.5 | 2 | 89.2 | 94.5 | 95.4 | 96 | 96 | 95.5 | 95.5 | 88.3 | 94.1 | 95.5 | 96.4 | 96.5 | 96.5 | 95.9 | 85.5 | 92.8 | 94.6 | 95.9 | 96.2 | 96.3 | 95.4
Power-One | UNO-2.0-I-OUTD-S-US [277V] | 2 kW, 277 Vac Utility Interactive Inverter. Model Number may include -W | 2 | 277 | 95.5 | Y | N | Multiple Listing of ABB | 0.5 | 2 | 0.5 | 100 | 360 | 416 | 0.2 | 0.4 | 0.6 | 1 | 1.5 | 2 | 87.6 | 94.2 | 95.1 | 95.9 | 96 | 95.7 | 95.4 | 87.8 | 93.7 | 95.1 | 96.2 | 96.6 | 96.6 | 95.8 | 85.8 | 93 | 94.7 | 96.1 | 96.4 | 96.6 | 95.6
Power-One | UNO-2.5-I-OUTD-S-US [208V] | 2.5 kW, 208 Vac Utility Interactive Inverter. Model Number may include -W | 2.5 | 208 | 95.5 | Y | N | Multiple Listing of ABB | 0.4 | 2.5 | 0.4 | 100 | 330 | 416 | 0.25 | 0.5 | 0.75 | 1.25 | 1.88 | 2.5 | 91.9 | 95.2 | 95.8 | 95.8 | 95.2 | 94.2 | 95.2 | 89.6 | 94.9 | 95.8 | 96.1 | 96 | 95.7 | 95.7 | 87.5 | 93.6 | 94.9 | 95.8 | 95.8 | 95.6 | 95.2
Power-One | UNO-2.5-I-OUTD-S-US [240V] | 2.5 kW, 240 Vac Utility Interactive Inverter. Model Number may include -W | 2.5 | 240 | 96 | Y | N | Multiple Listing of ABB | 0.4 | 2.5 | 0.4 | 100 | 340 | 416 | 0.25 | 0.5 | 0.75 | 1.25 | 1.88 | 2.5 | 91 | 95.1 | 95.8 | 96.1 | 95.7 | 95 | 95.5 | 89.8 | 95 | 96 | 96.5 | 96.5 | 96.3 | 96.1 | 87.8 | 94 | 95.3 | 96.3 | 96.3 | 96.3 | 95.7
Power-One | UNO-2.5-I-OUTD-S-US [277V] | 2.5 kW, 277 Vac Utility Interactive Inverter. Model Number may include -W | 2.5 | 277 | 96 | Y | N | Multiple Listing of ABB | 0.5 | 2.5 | 0.5 | 100 | 360 | 416 | 0.25 | 0.5 | 0.75 | 1.25 | 1.88 | 2.5 | 89.7 | 94.7 | 95.6 | 96 | 95.9 | 95.3 | 95.5 | 89 | 94.6 | 95.7 | 96.4 | 96.6 | 96.6 | 96.1 | 87.9 | 94.1 | 95.4 | 96.4 | 96.6 | 96.6 | 95.9
Power-One | PVI-3000-I-OUTD-US [208V] | 3 kW, 150-600 Vdc Utility Interactive Inverter | 2.7 | 208 | 90.5 | Y | N |  | 0.4 | 2.5 | 0.4 | 100 | 330 | 480 | 0.27 | 0.54 | 0.81 | 1.35 | 2.03 | 2.7 | 86.2 | 90.4 | 91.1 | 90.9 | 90.1 | 88.9 | 90.2 | 87 | 91.9 | 92.5 | 92.1 | 91.2 | 90.1 | 91.4 | 81.7 | 89.2 | 90.6 | 90.6 | 89.9 | 88.9 | 89.7
Power-One | PVI-3000-I-OUTD-US-F [208V] | 3 kW, 150-600 Vdc Utility Interactive Inverter | 2.7 | 208 | 90.5 | Y | N |  | 0.4 | 2.7 | 0.4 | 100 | 330 | 480 | 0.27 | 0.54 | 0.81 | 1.35 | 2.03 | 2.7 | 86.2 | 90.4 | 91.2 | 91 | 90.1 | 88.9 | 90.2 | 87 | 91.9 | 92.5 | 92.3 | 91.1 | 90 | 91.4 | 81.7 | 89.2 | 90.6 | 90.8 | 89.9 | 88.8 | 89.7
Power-One | PVI-3.0-OUTD-S-US [208V] | 3 kW, 208 Vac Utility Interactive Inverter | 3 | 208 | 96 | Y | N | Multiple Listing of ABB | 0.1 | 3 | 0.1 | 100 | 310 | 480 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 93.1 | 95.5 | 96 | 95.9 | 95.7 | 95.1 | 95.6 | 93.3 | 95.9 | 96.4 | 96.4 | 96.2 | 95.8 | 96.1 | 91 | 94.9 | 95.7 | 96 | 95.8 | 95.5 | 95.6
Power-One | PVI-3.0-OUTD-S-US [240V] | 3 kW, 240 Vac Utility Interactive Inverter | 3 | 240 | 96 | Y | N | Multiple Listing of ABB | 0.1 | 3 | 0.1 | 100 | 340 | 480 | 0.25 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 92.5 | 95.2 | 95.9 | 96.1 | 95.9 | 95.5 | 95.7 | 93.1 | 95.9 | 96.5 | 96.7 | 96.7 | 96.4 | 96.5 | 91.1 | 95.1 | 96 | 96.4 | 96.4 | 96.2 | 96.1
Power-One | PVI-3.0-OUTD-S-US [277V] | 3 kW, 277 Vac Utility Interactive Inverter | 3 | 277 | 96 | Y | N | Multiple Listing of ABB | 0.2 | 3 | 0.2 | 100 | 390 | 480 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 91.4 | 94.7 | 95.5 | 96.1 | 95.9 | 95.6 | 95.7 | 92.5 | 95.8 | 96.5 | 96.9 | 96.9 | 96.8 | 96.6 | 91.1 | 95.2 | 96.2 | 96.7 | 96.8 | 96.7 | 96.4
Power-One | PVI-3.0-OUTD-S-US-A [208V] | 3 kW, 208 Vac Utility Interactive Inverter with arc detector | 3 | 208 | 96 | Y | N | Multiple Listing of ABB | 0.1 | 3 | 0.1 | 100 | 310 | 480 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 93.1 | 95.5 | 96 | 95.9 | 95.7 | 95.1 | 95.6 | 93.3 | 95.9 | 96.4 | 96.4 | 96.2 | 95.8 | 96.1 | 91 | 94.9 | 95.7 | 96 | 95.8 | 95.5 | 95.6
Power-One | PVI-3.0-OUTD-S-US-A [240V] | 3 kW, 240 Vac Utility Interactive Inverter with arc detector | 3 | 240 | 96 | Y | N | Multiple Listing of ABB | 0.1 | 3 | 0.1 | 100 | 340 | 480 | 0.25 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 92.5 | 95.2 | 95.9 | 96.1 | 95.9 | 95.5 | 95.7 | 93.1 | 95.9 | 96.5 | 96.7 | 96.7 | 96.4 | 96.5 | 91.1 | 95.1 | 96 | 96.4 | 96.4 | 96.2 | 96.1
Power-One | PVI-3.0-OUTD-S-US-A [277V] | 3 kW, 277 Vac Utility Interactive Inverter with arc detector | 3 | 277 | 96 | Y | N | Multiple Listing of ABB | 0.2 | 3 | 0.2 | 100 | 390 | 480 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 91.4 | 94.7 | 95.5 | 96.1 | 95.9 | 95.6 | 95.7 | 92.5 | 95.8 | 96.5 | 96.9 | 96.9 | 96.8 | 96.6 | 91.1 | 95.2 | 96.2 | 96.7 | 96.8 | 96.7 | 96.4
Power-One | PVI-3.0-OUTD-S-US-Z [208V] | 3 kW, 208 Vac Utility Interactive Inverter with Zigbee | 3 | 208 | 96 | Y | N |  | 0.1 | 3 | 0.1 | 100 | 310 | 480 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 93.1 | 95.5 | 96 | 95.9 | 95.7 | 95.1 | 95.6 | 93.3 | 95.9 | 96.4 | 96.4 | 96.2 | 95.8 | 96.1 | 91 | 94.9 | 95.7 | 96 | 95.8 | 95.5 | 95.6
Power-One | PVI-3.0-OUTD-S-US-Z [240V] | 3 kW, 240 Vac Utility Interactive Inverter with Zigbee | 3 | 240 | 96 | Y | N |  | 0.1 | 3 | 0.1 | 100 | 340 | 480 | 0.25 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 92.5 | 95.2 | 95.9 | 96.1 | 95.9 | 95.5 | 95.7 | 93.1 | 95.9 | 96.5 | 96.7 | 96.7 | 96.4 | 96.5 | 91.1 | 95.1 | 96 | 96.4 | 96.4 | 96.2 | 96.1
Power-One | PVI-3.0-OUTD-S-US-Z [277V] | 3 kW, 277 Vac Utility Interactive Inverter with Zigbee | 3 | 277 | 96 | Y | N |  | 0.2 | 3 | 0.2 | 100 | 390 | 480 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 91.4 | 94.7 | 95.5 | 96.1 | 95.9 | 95.6 | 95.7 | 92.5 | 95.8 | 96.5 | 96.9 | 96.9 | 96.8 | 96.6 | 91.1 | 95.2 | 96.2 | 96.7 | 96.8 | 96.7 | 96.4
Power-One | PVI-3.0-OUTD-S-US-Z-A [208V] | 3 kW, 208 Vac Utility Interactive Inverter with Zigbee and arc detector | 3 | 208 | 96 | Y | N | Multiple Listing of ABB | 0.1 | 3 | 0.1 | 100 | 310 | 480 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 93.1 | 95.5 | 96 | 95.9 | 95.7 | 95.1 | 95.6 | 93.3 | 95.9 | 96.4 | 96.4 | 96.2 | 95.8 | 96.1 | 91 | 94.9 | 95.7 | 96 | 95.8 | 95.5 | 95.6
Power-One | PVI-3.0-OUTD-S-US-Z-A [240V] | 3 kW, 240 Vac Utility Interactive Inverter with Zigbee and arc detector | 3 | 240 | 96 | Y | N | Multiple Listing of ABB | 0.1 | 3 | 0.1 | 100 | 340 | 480 | 0.25 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 92.5 | 95.2 | 95.9 | 96.1 | 95.9 | 95.5 | 95.7 | 93.1 | 95.9 | 96.5 | 96.7 | 96.7 | 96.4 | 96.5 | 91.1 | 95.1 | 96 | 96.4 | 96.4 | 96.2 | 96.1
Power-One | PVI-3.0-OUTD-S-US-Z-A [277V] | 3 kW, 277 Vac Utility Interactive Inverter with Zigbee and arc detector | 3 | 277 | 96 | Y | N | Multiple Listing of ABB | 0.2 | 3 | 0.2 | 100 | 390 | 480 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 91.4 | 94.7 | 95.5 | 96.1 | 95.9 | 95.6 | 95.7 | 92.5 | 95.8 | 96.5 | 96.9 | 96.9 | 96.8 | 96.6 | 91.1 | 95.2 | 96.2 | 96.7 | 96.8 | 96.7 | 96.4
Power-One | PVI-3.0-OUTD-US [208V] | 3 kW, 208 Vac Utility Interactive Inverter | 3 | 208 | 96 | Y | N | Multiple Listing of ABB | 0.1 | 3 | 0.1 | 100 | 310 | 480 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 93.1 | 95.5 | 96 | 95.9 | 95.7 | 95.1 | 95.6 | 93.3 | 95.9 | 96.4 | 96.4 | 96.2 | 95.8 | 96.1 | 91 | 94.9 | 95.7 | 96 | 95.8 | 95.5 | 95.6
Power-One | PVI-3.0-OUTD-US [240V] | 3 kW, 240 Vac Utility Interactive Inverter. Model Number may include -S- or -W | 3 | 240 | 96 | Y | N | Multiple Listing of ABB | 0.1 | 3 | 0.1 | 100 | 340 | 480 | 0.25 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 92.5 | 95.2 | 95.9 | 96.1 | 95.9 | 95.5 | 95.7 | 93.1 | 95.9 | 96.5 | 96.7 | 96.7 | 96.4 | 96.5 | 91.1 | 95.1 | 96 | 96.4 | 96.4 | 96.2 | 96.1
Power-One | PVI-3.0-OUTD-US [277V] | 3 kW, 277 Vac Utility Interactive Inverter. Model Number may include -S- or -W | 3 | 277 | 96 | Y | N | Multiple Listing of ABB | 0.2 | 3 | 0.2 | 100 | 390 | 480 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 91.4 | 94.7 | 95.5 | 96.1 | 95.9 | 95.6 | 95.7 | 92.5 | 95.8 | 96.5 | 96.9 | 96.9 | 96.8 | 96.6 | 91.1 | 95.2 | 96.2 | 96.7 | 96.8 | 96.7 | 96.4
Power-One | PVI-3000-I-OUTD-US [240V] | 3 kW, 150-600 Vdc Utility Interactive Inverter | 3 | 240 | 92 | Y | N |  | 0.4 | 2.516 | 0.4 | 100 | 360 | 480 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 85.6 | 89.8 | 91.3 | 91.7 | 91 | 89.7 | 90.8 | 86.9 | 91.3 | 92.6 | 92.9 | 92.1 | 91.1 | 92 | 83.3 | 89.6 | 91.4 | 92.2 | 91.7 | 90.6 | 91.3
Power-One | PVI-3000-I-OUTD-US-F [240V] | 3 kW, 150-600 Vdc Utility Interactive Inverter | 3 | 240 | 91 | Y | N |  | 0.4 | 3 | 0.4 | 100 | 380 | 480 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 85.6 | 90 | 91.1 | 91.1 | 90.7 | 89.6 | 90.5 | 87.1 | 92 | 92.7 | 92.7 | 91.9 | 90.9 | 91.9 | 83.9 | 90.3 | 91.3 | 91.7 | 91.1 | 90.2 | 90.9
Power-One | PVI-3.8-1-OUTD-x-US-y [208V] | 3.8 kW, 208 Vac Inverter, where x = (blank) or -S and y = -PG or -NG | 3.3 | 208 | 96 | Y | N |  | 0.1 | 3.3 | 0.1 | 100 | 310 | 416 | 0.33 | 0.66 | 0.99 | 1.65 | 2.475 | 3.3 | 93.58 | 95.7 | 96.16 | 96.41 | 96.34 | 95.99 | 96.17 | 92.51 | 95.59 | 96.33 | 96.63 | 96.66 | 96.54 | 96.39 | 89.49 | 94.02 | 95.28 | 96.08 | 96.29 | 96.05 | 95.73
Power-One | PVI-3600-OUTD-US-F [208V] | 3.3 kW, 150-600 Vdc Utility Interactive Inverter | 3.3 | 208 | 94.5 | Y | N |  | 0.24 | 3.3 | 0.24 | 100 | 330 | 480 | 0.33 | 0.66 | 0.99 | 1.65 | 2.48 | 3.3 | 89.4 | 93.1 | 94.4 | 94.9 | 94.8 | 94.5 | 94.5 | 90.5 | 94.1 | 95.2 | 95.6 | 95.6 | 95.2 | 95.2 | 85.9 | 91.8 | 93.4 | 94.4 | 94.6 | 94.3 | 93.9
Power-One | PVI-3600-US [208V] | 3.3 kW, 150-600 Vdc Utility Interactive Inverter | 3.3 | 208 | 94 | Y | N |  | 0.24 | 3.3 | 0.24 | 100 | 380 | 480 | 0.33 | 0.66 | 0.99 | 1.65 | 2.48 | 3.3 | 88.7 | 92.7 | 93.9 | 94.6 | 94.5 | 94.1 | 94.1 | 89.9 | 94 | 95 | 95.5 | 95.3 | 95 | 95 | 84.3 | 91.1 | 92.8 | 94 | 94 | 93.9 | 93.3
Power-One | PVI-3.6-OUTD-S-US [208V] | 3.6 kW, 208 Vac Utility Interactive Inverter | 3.6 | 208 | 96 | Y | N | Multiple Listing of ABB | 0.1 | 3.6 | 0.1 | 100 | 310 | 480 | 0.36 | 0.72 | 1.08 | 1.8 | 2.7 | 3.6 | 92.2 | 94.7 | 95.4 | 95.9 | 95.9 | 95.6 | 95.6 | 92.7 | 95.5 | 96.1 | 96.4 | 96.4 | 96.1 | 96.1 | 90.3 | 94.5 | 95.3 | 95.9 | 96 | 95.7 | 95.6
Power-One | PVI-3.6-OUTD-S-US [240V] | 3.6 kW, 240 Vac Utility Interactive Inverter | 3.6 | 240 | 96 | Y | N | Multiple Listing of ABB | 0.2 | 3.6 | 0.2 | 100 | 340 | 480 | 0.3 | 0.72 | 1.08 | 1.8 | 2.7 | 3.6 | 91.1 | 94.1 | 94.9 | 95.6 | 95.8 | 95.7 | 95.4 | 92.4 | 95.5 | 96.3 | 96.7 | 96.7 | 96.6 | 96.5 | 90.2 | 94.6 | 95.6 | 96.2 | 96.4 | 96.3 | 95.9
Power-One | PVI-3.6-OUTD-S-US [277V] | 3.6 kW, 277 Vac Utility Interactive Inverter | 3.6 | 277 | 96 | Y | N | Multiple Listing of ABB | 0.2 | 3.6 | 0.2 | 100 | 395 | 480 | 0.36 | 0.72 | 1.08 | 1.8 | 2.7 | 3.6 | 90 | 93.4 | 94.4 | 95.4 | 95.7 | 95.6 | 95.1 | 91.9 | 95.4 | 96.3 | 96.9 | 97 | 96.9 | 96.6 | 90.4 | 94.9 | 95.9 | 96.6 | 96.8 | 96.8 | 96.3
Power-One | PVI-3.6-OUTD-S-US-A [208V] | 3.6 kW, 208 Vac Utility Interactive Inverter with arc detector | 3.6 | 208 | 96 | Y | N | Multiple Listing of ABB | 0.1 | 3.6 | 0.1 | 100 | 310 | 480 | 0.36 | 0.72 | 1.08 | 1.8 | 2.7 | 3.6 | 92.2 | 94.7 | 95.4 | 95.9 | 95.9 | 95.6 | 95.6 | 92.7 | 95.5 | 96.1 | 96.4 | 96.4 | 96.1 | 96.1 | 90.3 | 94.5 | 95.3 | 95.9 | 96 | 95.7 | 95.6
Power-One | PVI-3.6-OUTD-S-US-A [240V] | 3.6 kW, 240 Vac Utility Interactive Inverter with arc detector | 3.6 | 240 | 96 | Y | N | Multiple Listing of ABB | 0.2 | 3.6 | 0.2 | 100 | 340 | 480 | 0.3 | 0.72 | 1.08 | 1.8 | 2.7 | 3.6 | 91.1 | 94.1 | 94.9 | 95.6 | 95.8 | 95.7 | 95.4 | 92.4 | 95.5 | 96.3 | 96.7 | 96.7 | 96.6 | 96.5 | 90.2 | 94.6 | 95.6 | 96.2 | 96.4 | 96.3 | 95.9
Power-One | PVI-3.6-OUTD-S-US-A [277V] | 3.6 kW, 277 Vac Utility Interactive Inverter with arc detector | 3.6 | 277 | 96 | Y | N | Multiple Listing of ABB | 0.2 | 3.6 | 0.2 | 100 | 395 | 480 | 0.36 | 0.72 | 1.08 | 1.8 | 2.7 | 3.6 | 90 | 93.4 | 94.4 | 95.4 | 95.7 | 95.6 | 95.1 | 91.9 | 95.4 | 96.3 | 96.9 | 97 | 96.9 | 96.6 | 90.4 | 94.9 | 95.9 | 96.6 | 96.8 | 96.8 | 96.3
Power-One | PVI-3.6-OUTD-S-US-Z [208V] | 3.6 kW, 208 Vac Utility Interactive Inverter with Zigbee | 3.6 | 208 | 96 | Y | N |  | 0.1 | 3.6 | 0.1 | 100 | 310 | 480 | 0.36 | 0.72 | 1.08 | 1.8 | 2.7 | 3.6 | 92.2 | 94.7 | 95.4 | 95.9 | 95.9 | 95.6 | 95.6 | 92.7 | 95.5 | 96.1 | 96.4 | 96.4 | 96.1 | 96.1 | 90.3 | 94.5 | 95.3 | 95.9 | 96 | 95.7 | 95.6
Power-One | PVI-3.6-OUTD-S-US-Z [240V] | 3.6 kW, 240 Vac Utility Interactive Inverter with Zigbee | 3.6 | 240 | 96 | Y | N |  | 0.2 | 3.6 | 0.2 | 100 | 340 | 480 | 0.3 | 0.72 | 1.08 | 1.8 | 2.7 | 3.6 | 91.1 | 94.1 | 94.9 | 95.6 | 95.8 | 95.7 | 95.4 | 92.4 | 95.5 | 96.3 | 96.7 | 96.7 | 96.6 | 96.5 | 90.2 | 94.6 | 95.6 | 96.2 | 96.4 | 96.3 | 95.9
Power-One | PVI-3.6-OUTD-S-US-Z [277V] | 3.6 kW, 277 Vac Utility Interactive Inverter with Zigbee | 3.6 | 277 | 96 | Y | N |  | 0.2 | 3.6 | 0.2 | 100 | 395 | 480 | 0.36 | 0.72 | 1.08 | 1.8 | 2.7 | 3.6 | 90 | 93.4 | 94.4 | 95.4 | 95.7 | 95.6 | 95.1 | 91.9 | 95.4 | 96.3 | 96.9 | 97 | 96.9 | 96.6 | 90.4 | 94.9 | 95.9 | 96.6 | 96.8 | 96.8 | 96.3
Power-One | PVI-3.6-OUTD-S-US-Z-A [208V] | 3.6 kW, 208 Vac Utility Interactive Inverter with arc detector | 3.6 | 208 | 96 | Y | N | Multiple Listing of ABB | 0.1 | 3.6 | 0.1 | 100 | 310 | 480 | 0.36 | 0.72 | 1.08 | 1.8 | 2.7 | 3.6 | 92.2 | 94.7 | 95.4 | 95.9 | 95.9 | 95.6 | 95.6 | 92.7 | 95.5 | 96.1 | 96.4 | 96.4 | 96.1 | 96.1 | 90.3 | 94.5 | 95.3 | 95.9 | 96 | 95.7 | 95.6
Power-One | PVI-3.6-OUTD-S-US-Z-A [240V] | 3.6 kW, 240 Vac Utility Interactive Inverter with arc detector | 3.6 | 240 | 96 | Y | N | Multiple Listing of ABB | 0.2 | 3.6 | 0.2 | 100 | 340 | 480 | 0.3 | 0.72 | 1.08 | 1.8 | 2.7 | 3.6 | 91.1 | 94.1 | 94.9 | 95.6 | 95.8 | 95.7 | 95.4 | 92.4 | 95.5 | 96.3 | 96.7 | 96.7 | 96.6 | 96.5 | 90.2 | 94.6 | 95.6 | 96.2 | 96.4 | 96.3 | 95.9
Power-One | PVI-3.6-OUTD-S-US-Z-A [277V] | 3.6 kW, 277 Vac Utility Interactive Inverter with arc detector | 3.6 | 277 | 96 | Y | N | Multiple Listing of ABB | 0.2 | 3.6 | 0.2 | 100 | 395 | 480 | 0.36 | 0.72 | 1.08 | 1.8 | 2.7 | 3.6 | 90 | 93.4 | 94.4 | 95.4 | 95.7 | 95.6 | 95.1 | 91.9 | 95.4 | 96.3 | 96.9 | 97 | 96.9 | 96.6 | 90.4 | 94.9 | 95.9 | 96.6 | 96.8 | 96.8 | 96.3
Power-One | PVI-3.6-OUTD-US [208V] | 3.6 kW, 208 Vac Utility Interactive Inverter. Model number may include -S- or -W | 3.6 | 208 | 96 | Y | N | Multiple Listing of ABB | 0.1 | 3.6 | 0.1 | 100 | 310 | 480 | 0.36 | 0.72 | 1.08 | 1.8 | 2.7 | 3.6 | 92.2 | 94.7 | 95.4 | 95.9 | 95.9 | 95.6 | 95.6 | 92.7 | 95.5 | 96.1 | 96.4 | 96.4 | 96.1 | 96.1 | 90.3 | 94.5 | 95.3 | 95.9 | 96 | 95.7 | 95.6
Power-One | PVI-3.6-OUTD-US [240V] | 3.6 kW, 240 Vac Utility Interactive Inverter. Model number may include -S- or -W | 3.6 | 240 | 96 | Y | N | Multiple Listing of ABB | 0.2 | 3.6 | 0.2 | 100 | 340 | 480 | 0.3 | 0.72 | 1.08 | 1.8 | 2.7 | 3.6 | 91.1 | 94.1 | 94.9 | 95.6 | 95.8 | 95.7 | 95.4 | 92.4 | 95.5 | 96.3 | 96.7 | 96.7 | 96.6 | 96.5 | 90.2 | 94.6 | 95.6 | 96.2 | 96.4 | 96.3 | 95.9
Power-One | PVI-3.6-OUTD-US [277V] | 3.6 kW, 277 Vac Utility Interactive Inverter. Model number may include -S- or -W | 3.6 | 277 | 96 | Y | N | Multiple Listing of ABB | 0.2 | 3.6 | 0.2 | 100 | 395 | 480 | 0.36 | 0.72 | 1.08 | 1.8 | 2.7 | 3.6 | 90 | 93.4 | 94.4 | 95.4 | 95.7 | 95.6 | 95.1 | 91.9 | 95.4 | 96.3 | 96.9 | 97 | 96.9 | 96.6 | 90.4 | 94.9 | 95.9 | 96.6 | 96.8 | 96.8 | 96.3
Power-One | PVI-3600-OUTD-US-F [240V] | 3.6 kW, 150-600 Vdc Utility Interactive Inverter | 3.6 | 240 | 95 | Y | N |  | 0.34 | 3.6 | 0.34 | 100 | 380 | 480 | 0.36 | 0.72 | 1.08 | 1.8 | 2.7 | 3.6 | 88.8 | 92.9 | 94.1 | 94.8 | 94.8 | 94.6 | 94.4 | 90.1 | 94.3 | 95.2 | 95.8 | 95.9 | 95.6 | 95.4 | 87.3 | 92.8 | 94.2 | 95.1 | 95.4 | 95.1 | 94.7
Power-One | PVI-3600-US [240V] | 3.6 kW, 150-600 Vdc Utility Interactive Inverter | 3.6 | 240 | 94.5 | Y | N |  | 0.34 | 3.6 | 0.34 | 100 | 380 | 480 | 0.36 | 0.72 | 1.08 | 1.8 | 2.7 | 3.6 | 88.1 | 92 | 93.5 | 94.4 | 94.4 | 94.1 | 93.9 | 89.4 | 93.9 | 95 | 95.6 | 95.6 | 95.3 | 95.2 | 85.9 | 91.9 | 93.6 | 94.7 | 94.9 | 94.7 | 94.2
Power-One | PVI-3.8-1-OUTD-x-US-y [240V] | 3.8 kW, 240 Vac Inverter, where x = (blank) or S and y = PG or NG | 3.8 | 240 | 96.5 | Y | N |  | 0.1 | 3.8 | 0.1 | 100 | 340 | 416 | 0.38 | 0.76 | 1.14 | 1.9 | 2.85 | 3.8 | 93.72 | 95.75 | 96.23 | 96.47 | 96.44 | 96.09 | 96.26 | 92.77 | 95.88 | 96.59 | 96.88 | 96.84 | 96.81 | 96.6 | 90.71 | 94.81 | 95.88 | 96.53 | 96.5 | 96.49 | 96.12
Power-One | PVI-3.8-1-OUTD-x-US-y [277V] | 3.8 kW, 277 Vac Inverter, where x = (blank) or S and y = PG or NG | 3.8 | 277 | 96.5 | Y | N |  | 0.1 | 3.8 | 0.1 | 100 | 362 | 416 | 0.38 | 0.76 | 1.14 | 1.9 | 2.85 | 3.8 | 92.86 | 95.37 | 95.99 | 96.34 | 96.38 | 96.14 | 96.12 | 92.27 | 95.6 | 96.41 | 96.92 | 96.88 | 96.93 | 96.59 | 91.34 | 95.21 | 96.22 | 96.83 | 96.8 | 96.85 | 96.44
Power-One | PVI-3.8-OUTD-S-US [208V] | 3.3 kW, 208 Vac Utility Interactive Inverter | 3.8 | 208 | 95.5 | Y | N | Multiple Listing of ABB | 0.12 |  |  | 100 | 310 | 480 | 0.33 | 0.66 | 0.99 | 1.65 | 2.48 | 3.3 | 91.5 | 94.3 | 95.1 | 95.6 | 95.6 | 95.4 | 95.3 | 92.1 | 95.1 | 95.9 | 96.3 | 96.4 | 96.2 | 96.1 | 89.1 | 93.9 | 95 | 95.7 | 95.9 | 95.8 | 95.4
Power-One | PVI-3.8-OUTD-S-US [240V] | 3.8 kW, 240 Vac Utility Interactive Inverter | 3.8 | 240 | 96 | Y | N | Multiple Listing of ABB | 0.16 |  |  | 100 | 340 | 480 | 0.38 | 0.76 | 1.14 | 1.9 | 2.85 | 3.8 | 91.4 | 94.2 | 94.9 | 95.5 | 95.6 | 95.5 | 95.3 | 92.6 | 95.5 | 96.2 | 96.6 | 96.7 | 96.6 | 96.4 | 90.3 | 94.5 | 95.5 | 96.2 | 96.3 | 96.3 | 95.9
Power-One | PVI-3.8-OUTD-S-US [277V] | 3.8 kW, 277 Vac Utility Interactive Inverter | 3.8 | 277 | 96 | Y | N | Multiple Listing of ABB | 0.22 |  |  | 100 | 395 | 480 | 0.38 | 0.76 | 1.14 | 1.9 | 2.85 | 3.8 | 90.3 | 93.6 | 94.5 | 95.3 | 95.6 | 95.5 | 95.1 | 92 | 95.3 | 96.2 | 96.8 | 96.9 | 96.9 | 96.5 | 90.4 | 94.7 | 95.8 | 96.5 | 96.7 | 96.8 | 96.2
Power-One | PVI-3.8-OUTD-S-US-A [208V] | 3.3 kW, 208 Vac Utility Interactive Inverter with arc detector | 3.8 | 208 | 95.5 | Y | N | Multiple Listing of ABB | 0.12 |  |  | 100 | 310 | 480 | 0.33 | 0.66 | 0.99 | 1.65 | 2.48 | 3.3 | 91.5 | 94.3 | 95.1 | 95.6 | 95.6 | 95.4 | 95.3 | 92.1 | 95.1 | 95.9 | 96.3 | 96.4 | 96.2 | 96.1 | 89.1 | 93.9 | 95 | 95.7 | 95.9 | 95.8 | 95.4
Power-One | PVI-3.8-OUTD-S-US-A [240V] | 3.8 kW, 240 Vac Utility Interactive Inverter with arc detector | 3.8 | 240 | 96 | Y | N | Multiple Listing of ABB | 0.16 |  |  | 100 | 340 | 480 | 0.38 | 0.76 | 1.14 | 1.9 | 2.85 | 3.8 | 91.4 | 94.2 | 94.9 | 95.5 | 95.6 | 95.5 | 95.3 | 92.6 | 95.5 | 96.2 | 96.6 | 96.7 | 96.6 | 96.4 | 90.3 | 94.5 | 95.5 | 96.2 | 96.3 | 96.3 | 95.9
Power-One | PVI-3.8-OUTD-S-US-A [277V] | 3.8 kW, 277 Vac Utility Interactive Inverter with arc detector | 3.8 | 277 | 96 | Y | N | Multiple Listing of ABB | 0.22 |  |  | 100 | 395 | 480 | 0.38 | 0.76 | 1.14 | 1.9 | 2.85 | 3.8 | 90.3 | 93.6 | 94.5 | 95.3 | 95.6 | 95.5 | 95.1 | 92 | 95.3 | 96.2 | 96.8 | 96.9 | 96.9 | 96.5 | 90.4 | 94.7 | 95.8 | 96.5 | 96.7 | 96.8 | 96.2
Power-One | PVI-3.8-OUTD-S-US-Z [208V] | 3.3 kW, 208 Vac Utility Interactive Inverter | 3.8 | 208 | 95.5 | Y | N | Multiple Listing of ABB | 0.12 |  |  | 100 | 310 | 480 | 0.33 | 0.66 | 0.99 | 1.65 | 2.48 | 3.3 | 91.5 | 94.3 | 95.1 | 95.6 | 95.6 | 95.4 | 95.3 | 92.1 | 95.1 | 95.9 | 96.3 | 96.4 | 96.2 | 96.1 | 89.1 | 93.9 | 95 | 95.7 | 95.9 | 95.8 | 95.4
Power-One | PVI-3.8-OUTD-S-US-Z [240V] | 3.3 kW, 240 Vac Utility Interactive Inverter | 3.8 | 240 | 96 | Y | N | Multiple Listing of ABB | 0.16 |  |  | 100 | 340 | 480 | 0.38 | 0.76 | 1.14 | 1.9 | 2.85 | 3.8 | 91.4 | 94.2 | 94.9 | 95.5 | 95.6 | 95.5 | 95.3 | 92.6 | 95.5 | 96.2 | 96.6 | 96.7 | 96.6 | 96.4 | 90.3 | 94.5 | 95.5 | 96.2 | 96.3 | 96.3 | 95.9 |  | 2018-03-05
Power-One | PVI-3.8-OUTD-S-US-Z [277V] | 3.3 kW, 277 Vac Utility Interactive Inverter | 3.8 | 277 | 96 | Y | N | Multiple Listing of ABB | 0.22 |  |  | 100 | 395 | 480 | 0.38 | 0.76 | 1.14 | 1.9 | 2.85 | 3.8 | 90.3 | 93.6 | 94.5 | 95.3 | 95.6 | 95.5 | 95.1 | 92 | 95.3 | 96.2 | 96.8 | 96.9 | 96.9 | 96.5 | 90.4 | 94.7 | 95.8 | 96.5 | 96.7 | 96.8 | 96.2 |  | 2018-03-05
Power-One | PVI-3.8-OUTD-S-US-Z-A [208V] | 3.3 kW, 208 Vac Utility Interactive Inverter with arc detector | 3.8 | 208 | 95.5 | Y | N | Multiple Listing of ABB | 0.12 |  |  | 100 | 310 | 480 | 0.33 | 0.66 | 0.99 | 1.65 | 2.48 | 3.3 | 91.5 | 94.3 | 95.1 | 95.6 | 95.6 | 95.4 | 95.3 | 92.1 | 95.1 | 95.9 | 96.3 | 96.4 | 96.2 | 96.1 | 89.1 | 93.9 | 95 | 95.7 | 95.9 | 95.8 | 95.4
Power-One | PVI-3.8-OUTD-S-US-Z-A [240V] | 3.8 kW, 240 Vac Utility Interactive Inverter with arc detector | 3.8 | 240 | 96 | Y | N | Multiple Listing of ABB | 0.16 |  |  | 100 | 340 | 480 | 0.38 | 0.76 | 1.14 | 1.9 | 2.85 | 3.8 | 91.4 | 94.2 | 94.9 | 95.5 | 95.6 | 95.5 | 95.3 | 92.6 | 95.5 | 96.2 | 96.6 | 96.7 | 96.6 | 96.4 | 90.3 | 94.5 | 95.5 | 96.2 | 96.3 | 96.3 | 95.9
Power-One | PVI-3.8-OUTD-S-US-Z-A [277V] | 3.8 kW, 277 Vac Utility Interactive Inverter with arc detector | 3.8 | 277 | 96 | Y | N | Multiple Listing of ABB | 0.22 |  |  | 100 | 395 | 480 | 0.38 | 0.76 | 1.14 | 1.9 | 2.85 | 3.8 | 90.3 | 93.6 | 94.5 | 95.3 | 95.6 | 95.5 | 95.1 | 92 | 95.3 | 96.2 | 96.8 | 96.9 | 96.9 | 96.5 | 90.4 | 94.7 | 95.8 | 96.5 | 96.7 | 96.8 | 96.2
Power-One | PVI-3.8-OUTD-US [208V] | 3.3 kW, 208 Vac Utility Interactive Inverter | 3.8 | 208 | 95.5 | Y | N | Multiple Listing of ABB | 0.12 |  |  | 100 | 310 | 480 | 0.33 | 0.66 | 0.99 | 1.65 | 2.48 | 3.3 | 91.5 | 94.3 | 95.1 | 95.6 | 95.6 | 95.4 | 95.3 | 92.1 | 95.1 | 95.9 | 96.3 | 96.4 | 96.2 | 96.1 | 89.1 | 93.9 | 95 | 95.7 | 95.9 | 95.8 | 95.4
Power-One | PVI-3.8-OUTD-US [240V] | 3.8 kW, 240 Vac Utility Interactive Inverter | 3.8 | 240 | 96 | Y | N | Multiple Listing of ABB | 0.16 |  |  | 100 | 340 | 480 | 0.38 | 0.76 | 1.14 | 1.9 | 2.85 | 3.8 | 91.4 | 94.2 | 94.9 | 95.5 | 95.6 | 95.5 | 95.3 | 92.6 | 95.5 | 96.2 | 96.6 | 96.7 | 96.6 | 96.4 | 90.3 | 94.5 | 95.5 | 96.2 | 96.3 | 96.3 | 95.9
Power-One | PVI-3.8-OUTD-US [277V] | 3.8 kW, 277 Vac Utility Interactive Inverter | 3.8 | 277 | 96 | Y | N | Multiple Listing of ABB | 0.22 |  |  | 100 | 395 | 480 | 0.38 | 0.76 | 1.14 | 1.9 | 2.85 | 3.8 | 90.3 | 93.6 | 94.5 | 95.3 | 95.6 | 95.5 | 95.1 | 92 | 95.3 | 96.2 | 96.8 | 96.9 | 96.9 | 96.5 | 90.4 | 94.7 | 95.8 | 96.5 | 96.7 | 96.8 | 96.2
Power-One | PVI-4.2-OUTD-S-US [208V] | 4.2 kW, 208 Vac Utility Interactive Inverter | 4.2 | 208 | 96 | Y | N | Multiple Listing of ABB | 0.1 | 4.2 | 0.1 | 100 | 310 | 480 | 0.42 | 0.84 | 1.26 | 2.1 | 3.15 | 4.2 | 92.94 | 95.03 | 95.58 | 95.92 | 95.78 | 95.39 | 95.62 | 93.47 | 95.8 | 96.25 | 96.39 | 96.26 | 95.9 | 96.14 | 91.39 | 94.89 | 95.55 | 95.94 | 95.83 | 95.47 | 95.58
Power-One | PVI-4.2-OUTD-S-US [240V] | 4.2 kW, 240 Vac Utility Interactive Inverter | 4.2 | 240 | 96 | Y | N | Multiple Listing of ABB | 0.2 | 4.2 | 0.2 | 100 | 340 | 480 | 0.42 | 0.84 | 1.26 | 2.1 | 3.15 | 4.2 | 91.83 | 94.43 | 95.2 | 95.75 | 95.79 | 95.42 | 95.47 | 93.26 | 95.9 | 96.5 | 96.69 | 96.7 | 96.45 | 96.48 | 91.29 | 95.06 | 95.86 | 96.32 | 96.37 | 96.19 | 96.02
Power-One | PVI-4.2-OUTD-S-US [277V] | 4.2 kW, 277 Vac Utility Interactive Inverter | 4.2 | 277 | 96 | Y | N | Multiple Listing of ABB | 0.2 | 4.2 | 0.2 | 100 | 395 | 480 | 0.42 | 0.84 | 1.26 | 2.1 | 3.15 | 4.2 | 90.84 | 93.88 | 94.81 | 95.56 | 95.7 | 95.55 | 95.27 | 92.78 | 95.81 | 96.56 | 96.99 | 96.97 | 96.88 | 96.7 | 91.63 | 95.36 | 96.18 | 96.72 | 96.8 | 96.74 | 96.43
Power-One | PVI-4.2-OUTD-S-US-A [208V] | 4.2 kW, 208 Vac Utility Interactive Inverter with arc detector | 4.2 | 208 | 96 | Y | N | Multiple Listing of ABB | 0.1 | 4.2 | 0.1 | 100 | 310 | 480 | 0.42 | 0.84 | 1.26 | 2.1 | 3.15 | 4.2 | 92.94 | 95.03 | 95.58 | 95.92 | 95.78 | 95.39 | 95.62 | 93.47 | 95.8 | 96.25 | 96.39 | 96.26 | 95.9 | 96.14 | 91.39 | 94.89 | 95.55 | 95.94 | 95.83 | 95.47 | 95.58
Power-One | PVI-4.2-OUTD-S-US-A [240V] | 4.2 kW, 240 Vac Utility Interactive Inverter with arc detector | 4.2 | 240 | 96 | Y | N | Multiple Listing of ABB | 0.2 | 4.2 | 0.2 | 100 | 340 | 480 | 0.42 | 0.84 | 1.26 | 2.1 | 3.15 | 4.2 | 91.83 | 94.43 | 95.2 | 95.75 | 95.79 | 95.42 | 95.47 | 93.26 | 95.9 | 96.5 | 96.69 | 96.7 | 96.45 | 96.48 | 91.29 | 95.06 | 95.86 | 96.32 | 96.37 | 96.19 | 96.02
Power-One | PVI-4.2-OUTD-S-US-A [277V] | 4.2 kW, 277 Vac Utility Interactive Inverter with arc detector | 4.2 | 277 | 96 | Y | N | Multiple Listing of ABB | 0.2 | 4.2 | 0.2 | 100 | 395 | 480 | 0.42 | 0.84 | 1.26 | 2.1 | 3.15 | 4.2 | 90.84 | 93.88 | 94.81 | 95.56 | 95.7 | 95.55 | 95.27 | 92.78 | 95.81 | 96.56 | 96.99 | 96.97 | 96.88 | 96.7 | 91.63 | 95.36 | 96.18 | 96.72 | 96.8 | 96.74 | 96.43
Power-One | PVI-4.2-OUTD-S-US-Z [208V] | 4.2 kW, 208 Vac Utility Interactive Inverter with Zigbee | 4.2 | 208 | 96 | Y | N |  | 0.1 | 4.2 | 0.1 | 100 | 310 | 480 | 0.42 | 0.84 | 1.26 | 2.1 | 3.15 | 4.2 | 92.9 | 95 | 95.6 | 95.9 | 95.8 | 95.4 | 95.6 | 93.5 | 95.8 | 96.3 | 96.4 | 96.3 | 95.9 | 96.1 | 91.4 | 94.9 | 95.6 | 95.9 | 95.8 | 95.5 | 95.6
Power-One | PVI-4.2-OUTD-S-US-Z [240V] | 4.2 kW, 240 Vac Utility Interactive Inverter with Zigbee | 4.2 | 240 | 96 | Y | N |  | 0.2 | 4.2 | 0.2 | 100 | 340 | 480 | 0.42 | 0.84 | 1.26 | 2.1 | 3.15 | 4.2 | 91.8 | 94.4 | 95.2 | 95.8 | 95.8 | 95.4 | 95.5 | 93.3 | 95.9 | 96.5 | 96.7 | 96.7 | 96.5 | 96.5 | 91.3 | 95.1 | 95.9 | 96.3 | 96.4 | 96.2 | 96
Power-One | PVI-4.2-OUTD-S-US-Z [277V] | 4.2 kW, 277 Vac Utility Interactive Inverter with Zigbee | 4.2 | 277 | 96 | Y | N |  | 0.2 | 4.2 | 0.2 | 100 | 395 | 480 | 0.42 | 0.84 | 1.26 | 2.1 | 3.15 | 4.2 | 90.8 | 93.9 | 94.8 | 95.6 | 95.7 | 95.6 | 95.3 | 92.8 | 95.8 | 96.6 | 97 | 97 | 96.9 | 96.7 | 91.6 | 95.4 | 96.2 | 96.7 | 96.8 | 96.7 | 96.4
Power-One | PVI-4.2-OUTD-S-US-Z-A [208V] | 4.2 kW, 208 Vac Utility Interactive Inverter with Zigbee and arc detector | 4.2 | 208 | 96 | Y | N | Multiple Listing of ABB | 0.1 | 4.2 | 0.1 | 100 | 310 | 480 | 0.42 | 0.84 | 1.26 | 2.1 | 3.15 | 4.2 | 92.9 | 95 | 95.6 | 95.9 | 95.8 | 95.4 | 95.6 | 93.5 | 95.8 | 96.3 | 96.4 | 96.3 | 95.9 | 96.1 | 91.4 | 94.9 | 95.6 | 95.9 | 95.8 | 95.5 | 95.6
Power-One | PVI-4.2-OUTD-S-US-Z-A [240V] | 4.2 kW, 240 Vac Utility Interactive Inverter with Zigbee and arc detector | 4.2 | 240 | 96 | Y | N | Multiple Listing of ABB | 0.2 | 4.2 | 0.2 | 100 | 340 | 480 | 0.42 | 0.84 | 1.26 | 2.1 | 3.15 | 4.2 | 91.8 | 94.4 | 95.2 | 95.8 | 95.8 | 95.4 | 95.5 | 93.3 | 95.9 | 96.5 | 96.7 | 96.7 | 96.5 | 96.5 | 91.3 | 95.1 | 95.9 | 96.3 | 96.4 | 96.2 | 96
Power-One | PVI-4.2-OUTD-S-US-Z-A [277V] | 4.2 kW, 277 Vac Utility Interactive Inverter with Zigbee and arc detector | 4.2 | 277 | 96 | Y | N | Multiple Listing of ABB | 0.2 | 4.2 | 0.2 | 100 | 395 | 480 | 0.42 | 0.84 | 1.26 | 2.1 | 3.15 | 4.2 | 90.8 | 93.9 | 94.8 | 95.6 | 95.7 | 95.6 | 95.3 | 92.8 | 95.8 | 96.6 | 97 | 97 | 96.9 | 96.7 | 91.6 | 95.4 | 96.2 | 96.7 | 96.8 | 96.7 | 96.4
Power-One | PVI-4.2-OUTD-US [208V] | 4.2 kW, 208 Vac Utility Interactive Inverter. Model Number may include -S- or -W | 4.2 | 208 | 96 | Y | N | Multiple Listing of ABB | 0.1 | 4.2 | 0.1 | 100 | 310 | 480 | 0.42 | 0.84 | 1.26 | 2.1 | 3.15 | 4.2 | 92.94 | 95.03 | 95.58 | 95.92 | 95.78 | 95.39 | 95.62 | 93.47 | 95.8 | 96.25 | 96.39 | 96.26 | 95.9 | 96.14 | 91.39 | 94.89 | 95.55 | 95.94 | 95.83 | 95.47 | 95.58
Power-One | PVI-4.2-OUTD-US [240V] | 4.2 kW, 240 Vac Utility Interactive Inverter. Model Number may include -S- or -W | 4.2 | 240 | 96 | Y | N | Multiple Listing of ABB | 0.2 | 4.2 | 0.2 | 100 | 340 | 480 | 0.42 | 0.84 | 1.26 | 2.1 | 3.15 | 4.2 | 91.83 | 94.43 | 95.2 | 95.75 | 95.79 | 95.42 | 95.47 | 93.26 | 95.9 | 96.5 | 96.69 | 96.7 | 96.45 | 96.48 | 91.29 | 95.06 | 95.86 | 96.32 | 96.37 | 96.19 | 96.02
Power-One | PVI-4.2-OUTD-US [277V] | 4.2 kW, 277 Vac Utility Interactive Inverter. Model Number may include -S- or -W | 4.2 | 277 | 96 | Y | N | Multiple Listing of ABB | 0.2 | 4.2 | 0.2 | 100 | 395 | 480 | 0.42 | 0.84 | 1.26 | 2.1 | 3.15 | 4.2 | 90.84 | 93.88 | 94.81 | 95.56 | 95.7 | 95.55 | 95.27 | 92.78 | 95.81 | 96.56 | 96.99 | 96.97 | 96.88 | 96.7 | 91.63 | 95.36 | 96.18 | 96.72 | 96.8 | 96.74 | 96.43
Power-One | PVI-4.6-1-OUTD-x-US-y [208V] | 4.6 kW, 208 Vac Inverter, where x = (blank) or S and y = PG or NG | 4.6 | 208 | 96 | Y | N | Multiple Listing of ABB | 0.1 | 4.6 | 0.1 | 100 | 310 | 416 | 0.46 | 0.92 | 1.38 | 2.3 | 3.45 | 4.6 | 94.57 | 96.13 | 96.17 | 96.4 | 95.91 | 95.12 | 95.96 | 94.12 | 96.25 | 96.59 | 96.68 | 96.51 | 96.15 | 96.43 | 91.78 | 95.13 | 95.92 | 96.31 | 96 | 95.92 | 95.84
Power-One | PVI-4.6-1-OUTD-x-US-y [240V] | 4.6 kW, 240 Vac Inverter, where x = (blank) or S and y = PG or NG | 4.6 | 240 | 96.5 | Y | N | Multiple Listing of ABB | 0.1 | 4.6 | 0.1 | 100 | 340 | 416 | 0.46 | 0.92 | 1.38 | 2.3 | 3.45 | 4.6 | 94.08 | 96.02 | 96.23 | 96.45 | 96.18 | 95.56 | 96.12 | 93.82 | 96.27 | 96.7 | 96.87 | 96.79 | 96.64 | 96.64 | 92 | 95.4 | 96.18 | 96.62 | 96.45 | 96.48 | 96.22
Power-One | PVI-4.6-1-OUTD-x-US-y [277V] | 4.6 kW, 277 Vac Inverter, where x = (blank) or S and y = PG or NG | 4.6 | 277 | 96.5 | Y | N | Multiple Listing of ABB | 0.1 | 4.6 | 0.1 | 100 | 360 | 416 | 0.46 | 0.92 | 1.38 | 2.3 | 3.45 | 4.6 | 93.41 | 95.73 | 96.14 | 96.42 | 96.31 | 95.85 | 96.14 | 93.31 | 96.05 | 96.63 | 96.96 | 96.93 | 96.89 | 96.71 | 92.56 | 95.76 | 96.55 | 96.95 | 96.8 | 96.84 | 96.58
Power-One | PVI-5000-OUTD-S-US-Z [208V] | 5 kW, 208 Vac Utility Interactive Inverter with Zigbee | 5 | 208 | 96 | Y | N | Multiple Listing of ABB | 0.18 |  |  | 100 | 310 | 480 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 93.4 | 95.7 | 96.2 | 96.4 | 96.2 | 95.8 | 96.1 | 93.6 | 95.9 | 96.5 | 96.7 | 96.6 | 96.3 | 96.4 | 90.9 | 94.7 | 95.6 | 96.1 | 96.1 | 95.9 | 95.8
Power-One | PVI-5000-OUTD-S-US-Z [240V] | 5 kW, 240 Vac Utility Interactive Inverter with Zigbee | 5 | 240 | 96.5 | Y | N | Multiple Listing of ABB | 0.24 |  |  | 100 | 345 | 480 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 92.5 | 95.5 | 96.1 | 96.4 | 96.3 | 96 | 96.1 | 93.8 | 96.2 | 96.7 | 97 | 96.9 | 96.6 | 96.7 | 91.5 | 95 | 95.9 | 96.4 | 96.5 | 96.3 | 96.1
Power-One | PVI-5000-OUTD-S-US-Z [277V] | 5 kW, 277 Vac Utility Interactive Inverter with Zigbee | 5 | 277 | 96.5 | Y | N | Multiple Listing of ABB | 0.32 |  |  | 100 | 400 | 480 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 91.6 | 95 | 95.9 | 96.4 | 96.5 | 96.3 | 96.1 | 92.5 | 95.7 | 96.5 | 97.1 | 97.1 | 97 | 96.8 | 90.9 | 95 | 95.9 | 96.7 | 96.9 | 96.9 | 96.4
Power-One | PVI-5000-OUTD-S-US-Z-A [208V] | 5 kW, 208 Vac Utility Interactive Inverter with Zigbee and arc detector | 5 | 208 | 96 | Y | N | Multiple Listing of ABB | 0.18 |  |  | 100 | 310 | 480 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 93.4 | 95.7 | 96.2 | 96.4 | 96.2 | 95.8 | 96.1 | 93.6 | 95.9 | 96.5 | 96.7 | 96.6 | 96.3 | 96.4 | 90.9 | 94.7 | 95.6 | 96.1 | 96.1 | 95.9 | 95.8
Power-One | PVI-5000-OUTD-S-US-Z-A [240V] | 5 kW, 240 Vac Utility Interactive Inverter with Zigbee and arc detector | 5 | 240 | 96.5 | Y | N | Multiple Listing of ABB | 0.24 |  |  | 100 | 345 | 480 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 92.5 | 95.5 | 96.1 | 96.4 | 96.3 | 96 | 96.1 | 93.8 | 96.2 | 96.7 | 97 | 96.9 | 96.6 | 96.7 | 91.5 | 95 | 95.9 | 96.4 | 96.5 | 96.3 | 96.1
Power-One | PVI-5000-OUTD-S-US-Z-A [277V] | 5 kW, 277 Vac Utility Interactive Inverter with Zigbee and arc detector | 5 | 277 | 96.5 | Y | N | Multiple Listing of ABB | 0.32 |  |  | 100 | 400 | 480 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 91.6 | 95 | 95.9 | 96.4 | 96.5 | 96.3 | 96.1 | 92.5 | 95.7 | 96.5 | 97.1 | 97.1 | 97 | 96.8 | 90.9 | 95 | 95.9 | 96.7 | 96.9 | 96.9 | 96.4
Power-One | PVI-5000-OUTD-US [208V] | 5 kW, 208 Vac Utility Interactive Inverter | 5 | 208 | 96 | Y | N | Multiple Listing of ABB | 0.18 |  |  | 100 | 310 | 480 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 93.4 | 95.7 | 96.2 | 96.4 | 96.2 | 95.8 | 96.1 | 93.6 | 95.9 | 96.5 | 96.7 | 96.6 | 96.3 | 96.4 | 90.9 | 94.7 | 95.6 | 96.1 | 96.1 | 95.9 | 95.8
Power-One | PVI-5000-OUTD-US [240V] | 5 kW, 240 Vac Utility Interactive Inverter | 5 | 240 | 96.5 | Y | N | Multiple Listing of ABB | 0.24 |  |  | 100 | 345 | 480 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 92.5 | 95.5 | 96.1 | 96.4 | 96.3 | 96 | 96.1 | 93.8 | 96.2 | 96.7 | 97 | 96.9 | 96.6 | 96.7 | 91.5 | 95 | 95.9 | 96.4 | 96.5 | 96.3 | 96.1
Power-One | PVI-5000-OUTD-US [277V] | 5 kW, 277 Vac Utility Interactive Inverter | 5 | 277 | 96.5 | Y | N | Multiple Listing of ABB | 0.32 |  |  | 100 | 400 | 480 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 91.6 | 95 | 95.9 | 96.4 | 96.5 | 96.3 | 96.1 | 92.5 | 95.7 | 96.5 | 97.1 | 97.1 | 97 | 96.8 | 90.9 | 95 | 95.9 | 96.7 | 96.9 | 96.9 | 96.4
Power-One | PVI-5000-OUTD-US-A [208V] | 5 kW, 208 Vac Utility Interactive Inverter with arc detector | 5 | 208 | 96 | Y | N | Multiple Listing of ABB | 0.18 |  |  | 100 | 310 | 480 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 93.4 | 95.7 | 96.2 | 96.4 | 96.2 | 95.8 | 96.1 | 93.6 | 95.9 | 96.5 | 96.7 | 96.6 | 96.3 | 96.4 | 90.9 | 94.7 | 95.6 | 96.1 | 96.1 | 95.9 | 95.8
Power-One | PVI-5000-OUTD-US-A [240V] | 5 kW, 240 Vac Utility Interactive Inverter with arc detector | 5 | 240 | 96.5 | Y | N | Multiple Listing of ABB | 0.24 |  |  | 100 | 345 | 480 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 92.5 | 95.5 | 96.1 | 96.4 | 96.3 | 96 | 96.1 | 93.8 | 96.2 | 96.7 | 97 | 96.9 | 96.6 | 96.7 | 91.5 | 95 | 95.9 | 96.4 | 96.5 | 96.3 | 96.1
Power-One | PVI-5000-OUTD-US-A [277V] | 5 kW, 277 Vac Utility Interactive Inverter with arc detector | 5 | 277 | 96.5 | Y | N | Multiple Listing of ABB | 0.32 |  |  | 100 | 400 | 480 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 91.6 | 95 | 95.9 | 96.4 | 96.5 | 96.3 | 96.1 | 92.5 | 95.7 | 96.5 | 97.1 | 97.1 | 97 | 96.8 | 90.9 | 95 | 95.9 | 96.7 | 96.9 | 96.9 | 96.4
Power-One | PVI-5000-OUTD-US-Z [208V] | 5 kW, 208 Vac Utility Interactive Inverter | 5 | 208 | 96 | Y | N | Multiple Listing of ABB | 0.18 |  |  | 100 | 310 | 480 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 93.4 | 95.7 | 96.2 | 96.4 | 96.2 | 95.8 | 96.1 | 93.6 | 95.9 | 96.5 | 96.7 | 96.6 | 96.3 | 96.4 | 90.9 | 94.7 | 95.6 | 96.1 | 96.1 | 95.9 | 95.8
Power-One | PVI-5000-OUTD-US-Z [240V] | 5 kW, 240 Vac Utility Interactive Inverter | 5 | 240 | 96.5 | Y | N | Multiple Listing of ABB | 0.24 |  |  | 100 | 345 | 480 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 92.5 | 95.5 | 96.1 | 96.4 | 96.3 | 96 | 96.1 | 93.8 | 96.2 | 96.7 | 97 | 96.9 | 96.6 | 96.7 | 91.5 | 95 | 95.9 | 96.4 | 96.5 | 96.3 | 96.1
Power-One | PVI-5000-OUTD-US-Z [277V] | 5 kW, 277 Vac Utility Interactive Inverter | 5 | 277 | 96.5 | Y | N | Multiple Listing of ABB | 0.32 |  |  | 100 | 400 | 480 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 91.6 | 95 | 95.9 | 96.4 | 96.5 | 96.3 | 96.1 | 92.5 | 95.7 | 96.5 | 97.1 | 97.1 | 97 | 96.8 | 90.9 | 95 | 95.9 | 96.7 | 96.9 | 96.9 | 96.4
Power-One | PVI-5000-OUTD-US-Z-A [208V] | 5 kW, 208 Vac Utility Interactive Inverter | 5 | 208 | 96 | Y | N | Multiple Listing of ABB | 0.18 |  |  | 100 | 310 | 480 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 93.4 | 95.7 | 96.2 | 96.4 | 96.2 | 95.8 | 96.1 | 93.6 | 95.9 | 96.5 | 96.7 | 96.6 | 96.3 | 96.4 | 90.9 | 94.7 | 95.6 | 96.1 | 96.1 | 95.9 | 95.8
Power-One | PVI-5000-OUTD-US-Z-A [240V] | 5 kW, 240 Vac Utility Interactive Inverter | 5 | 240 | 96.5 | Y | N | Multiple Listing of ABB | 0.24 |  |  | 100 | 345 | 480 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 92.5 | 95.5 | 96.1 | 96.4 | 96.3 | 96 | 96.1 | 93.8 | 96.2 | 96.7 | 97 | 96.9 | 96.6 | 96.7 | 91.5 | 95 | 95.9 | 96.4 | 96.5 | 96.3 | 96.1
Power-One | PVI-5000-OUTD-US-Z-A [277V] | 5 kW, 277 Vac Utility Interactive Inverter | 5 | 277 | 96.5 | Y | N | Multiple Listing of ABB | 0.32 |  |  | 100 | 400 | 480 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 91.6 | 95 | 95.9 | 96.4 | 96.5 | 96.3 | 96.1 | 92.5 | 95.7 | 96.5 | 97.1 | 97.1 | 97 | 96.8 | 90.9 | 95 | 95.9 | 96.7 | 96.9 | 96.9 | 96.4
Power-One | PVI-6000-OUTD-S-US-A [208V] | 6 kW, 208 Vac Utility Interactive Inverter with arc detector | 6 | 208 | 96 | Y | N | Multiple Listing of ABB | 0.18 |  |  | 100 | 310 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 94 | 96 | 96.4 | 96.3 | 96 | 95.5 | 96 | 94.3 | 96.2 | 96.6 | 96.7 | 96.4 | 96 | 96.4 | 92.1 | 95.1 | 95.9 | 96.1 | 96 | 95.7 | 95.8
Power-One | PVI-6000-OUTD-S-US-A [240V] | 6 kW, 240 Vac Utility Interactive Inverter with arc detector | 6 | 240 | 96.5 | Y | N | Multiple Listing of ABB | 0.24 |  |  | 100 | 345 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 93.5 | 95.8 | 96.3 | 96.4 | 96.2 | 95.8 | 96.1 | 94.6 | 96.5 | 96.9 | 96.9 | 96.8 | 96.5 | 96.7 | 92.6 | 95.5 | 96.1 | 96.5 | 96.4 | 96.2 | 96.2
Power-One | PVI-6000-OUTD-S-US-A [277V] | 6 kW, 277 Vac Utility Interactive Inverter with arc detector | 6 | 277 | 96.5 | Y | N | Multiple Listing of ABB | 0.32 |  |  | 100 | 400 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 92.5 | 95.5 | 96.2 | 96.4 | 96.4 | 96.1 | 96.1 | 93.5 | 96.2 | 96.8 | 97.1 | 97.1 | 97 | 96.9 | 92.2 | 95.5 | 96.3 | 96.8 | 96.9 | 96.9 | 96.5
Power-One | PVI-6000-OUTD-S-US-Z [208V] | 6 kW, 208 Vac Utility Interactive Inverter with Zigbee | 6 | 208 | 96 | Y | N | Multiple Listing of ABB | 0.18 |  |  | 100 | 310 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 94 | 96 | 96.4 | 96.3 | 96 | 95.5 | 96 | 94.3 | 96.2 | 96.6 | 96.7 | 96.4 | 96 | 96.4 | 92.1 | 95.1 | 95.9 | 96.1 | 96 | 95.7 | 95.8
Power-One | PVI-6000-OUTD-S-US-Z [240V] | 6 kW, 240 Vac Utility Interactive Inverter with Zigbee | 6 | 240 | 96.5 | Y | N | Multiple Listing of ABB | 0.24 |  |  | 100 | 345 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 93.5 | 95.8 | 96.3 | 96.4 | 96.2 | 95.8 | 96.1 | 94.6 | 96.5 | 96.9 | 96.9 | 96.8 | 96.5 | 96.7 | 92.6 | 95.5 | 96.1 | 96.5 | 96.4 | 96.2 | 96.2
Power-One | PVI-6000-OUTD-S-US-Z [277V] | 6 kW, 277 Vac Utility Interactive Inverter with Zigbee | 6 | 277 | 96.5 | Y | N | Multiple Listing of ABB | 0.32 |  |  | 100 | 400 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 92.5 | 95.5 | 96.2 | 96.4 | 96.4 | 96.1 | 96.1 | 93.5 | 96.2 | 96.8 | 97.1 | 97.1 | 97 | 96.9 | 92.2 | 95.5 | 96.3 | 96.8 | 96.9 | 96.9 | 96.5
Power-One | PVI-6000-OUTD-S-US-Z-A [208V] | 6 kW, 208 Vac Utility Interactive Inverter with Zigbee and arc detector | 6 | 208 | 96 | Y | N | Multiple Listing of ABB | 0.18 |  |  | 100 | 310 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 94 | 96 | 96.4 | 96.3 | 96 | 95.5 | 96 | 94.3 | 96.2 | 96.6 | 96.7 | 96.4 | 96 | 96.4 | 92.1 | 95.1 | 95.9 | 96.1 | 96 | 95.7 | 95.8
Power-One | PVI-6000-OUTD-S-US-Z-A [240V] | 6 kW, 240 Vac Utility Interactive Inverter with Zigbee and arc detector | 6 | 240 | 96.5 | Y | N | Multiple Listing of ABB | 0.24 |  |  | 100 | 345 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 93.5 | 95.8 | 96.3 | 96.4 | 96.2 | 95.8 | 96.1 | 94.6 | 96.5 | 96.9 | 96.9 | 96.8 | 96.5 | 96.7 | 92.6 | 95.5 | 96.1 | 96.5 | 96.4 | 96.2 | 96.2
Power-One | PVI-6000-OUTD-S-US-Z-A [277V] | 6 kW, 277 Vac Utility Interactive Inverter with Zigbee and arc detector | 6 | 277 | 96.5 | Y | N | Multiple Listing of ABB | 0.32 |  |  | 100 | 400 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 92.5 | 95.5 | 96.2 | 96.4 | 96.4 | 96.1 | 96.1 | 93.5 | 96.2 | 96.8 | 97.1 | 97.1 | 97 | 96.9 | 92.2 | 95.5 | 96.3 | 96.8 | 96.9 | 96.9 | 96.5
Power-One | PVI-6000-OUTD-US [208V] | 6 kW, 208 Vac Utility Interactive Inverter | 6 | 208 | 96 | Y | N | Multiple Listing of ABB | 0.18 |  |  | 100 | 310 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 94 | 96 | 96.4 | 96.3 | 96 | 95.5 | 96 | 94.3 | 96.2 | 96.6 | 96.7 | 96.4 | 96 | 96.4 | 92.1 | 95.1 | 95.9 | 96.1 | 96 | 95.7 | 95.8
Power-One | PVI-6000-OUTD-US [240V] | 6 kW, 240 Vac Utility Interactive Inverter | 6 | 240 | 96.5 | Y | N | Multiple Listing of ABB | 0.24 |  |  | 100 | 345 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 93.5 | 95.8 | 96.3 | 96.4 | 96.2 | 95.8 | 96.1 | 94.6 | 96.5 | 96.9 | 96.9 | 96.8 | 96.5 | 96.7 | 92.6 | 95.5 | 96.1 | 96.5 | 96.4 | 96.2 | 96.2
Power-One | PVI-6000-OUTD-US [277V] | 6 kW, 277 Vac Utility Interactive Inverter | 6 | 277 | 96.5 | Y | N | Multiple Listing of ABB | 0.32 |  |  | 100 | 400 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 92.5 | 95.5 | 96.2 | 96.4 | 96.4 | 96.1 | 96.1 | 93.5 | 96.2 | 96.8 | 97.1 | 97.1 | 97 | 96.9 | 92.2 | 95.5 | 96.3 | 96.8 | 96.9 | 96.9 | 96.5
Power-One | PVI-6000-OUTD-US-A [208V] | 6 kW, 208 Vac Utility Interactive Inverter with arc detector | 6 | 208 | 96 | Y | N | Multiple Listing of ABB | 0.18 |  |  | 100 | 310 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 94 | 96 | 96.4 | 96.3 | 96 | 95.5 | 96 | 94.3 | 96.2 | 96.6 | 96.7 | 96.4 | 96 | 96.4 | 92.1 | 95.1 | 95.9 | 96.1 | 96 | 95.7 | 95.8
Power-One | PVI-6000-OUTD-US-A [240V] | 6 kW, 240 Vac Utility Interactive Inverter with arc detector | 6 | 240 | 96.5 | Y | N | Multiple Listing of ABB | 0.24 |  |  | 100 | 345 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 93.5 | 95.8 | 96.3 | 96.4 | 96.2 | 95.8 | 96.1 | 94.6 | 96.5 | 96.9 | 96.9 | 96.8 | 96.5 | 96.7 | 92.6 | 95.5 | 96.1 | 96.5 | 96.4 | 96.2 | 96.2
Power-One | PVI-6000-OUTD-US-A [277V] | 6 kW, 277 Vac Utility Interactive Inverter with arc detector | 6 | 277 | 96.5 | Y | N | Multiple Listing of ABB | 0.32 |  |  | 100 | 400 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 92.5 | 95.5 | 96.2 | 96.4 | 96.4 | 96.1 | 96.1 | 93.5 | 96.2 | 96.8 | 97.1 | 97.1 | 97 | 96.9 | 92.2 | 95.5 | 96.3 | 96.8 | 96.9 | 96.9 | 96.5
Power-One | PVI-6000-OUTD-US-Z [208V] | 6 kW, 208 Vac Utility Interactive Inverter | 6 | 208 | 96 | Y | N | Multiple Listing of ABB | 0.18 |  |  | 100 | 310 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 94 | 96 | 96.4 | 96.3 | 96 | 95.5 | 96 | 94.3 | 96.2 | 96.6 | 96.7 | 96.4 | 96 | 96.4 | 92.1 | 95.1 | 95.9 | 96.1 | 96 | 95.7 | 95.8
Power-One | PVI-6000-OUTD-US-Z [240V] | 6 kW, 240 Vac Utility Interactive Inverter | 6 | 240 | 96.5 | Y | N | Multiple Listing of ABB | 0.24 |  |  | 100 | 345 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 93.5 | 95.8 | 96.3 | 96.4 | 96.2 | 95.8 | 96.1 | 94.6 | 96.5 | 96.9 | 96.9 | 96.8 | 96.5 | 96.7 | 92.6 | 95.5 | 96.1 | 96.5 | 96.4 | 96.2 | 96.2
Power-One | PVI-6000-OUTD-US-Z [277V] | 6 kW, 277 Vac Utility Interactive Inverter | 6 | 277 | 96.5 | Y | N | Multiple Listing of ABB | 0.32 |  |  | 100 | 400 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 92.5 | 95.5 | 96.2 | 96.4 | 96.4 | 96.1 | 96.1 | 93.5 | 96.2 | 96.8 | 97.1 | 97.1 | 97 | 96.9 | 92.2 | 95.5 | 96.3 | 96.8 | 96.9 | 96.9 | 96.5
Power-One | PVI-6000-OUTD-US-Z-A [208V] | 6 kW, 208 Vac Utility Interactive Inverter | 6 | 208 | 96 | Y | N | Multiple Listing of ABB | 0.18 |  |  | 100 | 310 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 94 | 96 | 96.4 | 96.3 | 96 | 95.5 | 96 | 94.3 | 96.2 | 96.6 | 96.7 | 96.4 | 96 | 96.4 | 92.1 | 95.1 | 95.9 | 96.1 | 96 | 95.7 | 95.8
Power-One | PVI-6000-OUTD-US-Z-A [240V] | 6 kW, 240 Vac Utility Interactive Inverter | 6 | 240 | 96.5 | Y | N | Multiple Listing of ABB | 0.24 |  |  | 100 | 345 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 93.5 | 95.8 | 96.3 | 96.4 | 96.2 | 95.8 | 96.1 | 94.6 | 96.5 | 96.9 | 96.9 | 96.8 | 96.5 | 96.7 | 92.6 | 95.5 | 96.1 | 96.5 | 96.4 | 96.2 | 96.2
Power-One | PVI-6000-OUTD-US-Z-A [277V] | 6 kW, 277 Vac Utility Interactive Inverter | 6 | 277 | 96.5 | Y | N | Multiple Listing of ABB | 0.32 |  |  | 100 | 400 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 92.5 | 95.5 | 96.2 | 96.4 | 96.4 | 96.1 | 96.1 | 93.5 | 96.2 | 96.8 | 97.1 | 97.1 | 97 | 96.9 | 92.2 | 95.5 | 96.3 | 96.8 | 96.9 | 96.9 | 96.5
Power-One | UNO-7.6-TL-OUTD-S-US-A [208V] | transformerless Utility Interactive Inverter with arc detector | 7.6 | 208 | 96.5 | Y | N |  | 1.33 |  |  | 100 | 380 | 480 | 0.76 | 1.52 | 2.28 | 3.8 | 5.7 | 7.6 | 93.3 | 95.3 | 95.8 | 95.9 | 95.8 | 95.6 | 95.7 | 95.2 | 96.8 | 97.1 | 97.2 | 97.1 | 96.9 | 97 | 93.2 | 96 | 96.4 | 96.8 | 96.8 | 96.6 | 96.5
Power-One | UNO-7.6-TL-OUTD-S-US-A [240V] | transformerless Utility Interactive Inverter with arc detector | 7.6 | 240 | 96.5 | Y | N |  | 1.4 |  |  | 100 | 380 | 480 | 0.76 | 1.52 | 2.28 | 3.8 | 5.7 | 7.6 | 92.5 | 95 | 95.7 | 96 | 96 | 95.8 | 95.7 | 95 | 96.9 | 97.3 | 97.5 | 97.5 | 97.3 | 97.3 | 93.3 | 96.2 | 96.8 | 97.2 | 97.2 | 97.1 | 96.9
Power-One | UNO-7.6-TL-OUTD-S-US-A [277V] | transformerless Utility Interactive Inverter with arc detector | 7.6 | 277 | 96.5 | Y | N |  | 1.5 |  |  | 100 | 380 | 480 | 0.76 | 1.52 | 2.28 | 3.8 | 5.7 | 7.6 | 91.5 | 94.6 | 95.4 | 95.9 | 95.9 | 95.9 | 95.6 | 93.1 | 95.7 | 96.3 | 96.8 | 96.9 | 96.9 | 96.6 | 93.6 | 96.4 | 97 | 97.5 | 97.6 | 97.5 | 97.3
Power-One | UNO-7.6-TL-OUTD-S-US-Z-A [208V] | transformerless Utility Interactive Inverter with arc detector | 7.6 | 208 | 96.5 | Y | N |  | 1.33 |  |  | 100 | 380 | 480 | 0.76 | 1.52 | 2.28 | 3.8 | 5.7 | 7.6 | 93.3 | 95.3 | 95.8 | 95.9 | 95.8 | 95.6 | 95.7 | 95.2 | 96.8 | 97.1 | 97.2 | 97.1 | 96.9 | 97 | 93.2 | 96 | 96.4 | 96.8 | 96.8 | 96.6 | 96.5
Power-One | UNO-7.6-TL-OUTD-S-US-Z-A [240V] | transformerless Utility Interactive Inverter with arc detector | 7.6 | 240 | 96.5 | Y | N |  | 1.4 |  |  | 100 | 380 | 480 | 0.76 | 1.52 | 2.28 | 3.8 | 5.7 | 7.6 | 92.5 | 95 | 95.7 | 96 | 96 | 95.8 | 95.7 | 95 | 96.9 | 97.3 | 97.5 | 97.5 | 97.3 | 97.3 | 93.3 | 96.2 | 96.8 | 97.2 | 97.2 | 97.1 | 96.9
Power-One | UNO-7.6-TL-OUTD-S-US-Z-A [277V] | transformerless Utility Interactive Inverter with arc detector | 7.6 | 277 | 96.5 | Y | N |  | 1.5 |  |  | 100 | 380 | 480 | 0.76 | 1.52 | 2.28 | 3.8 | 5.7 | 7.6 | 91.5 | 94.6 | 95.4 | 95.9 | 95.9 | 95.9 | 95.6 | 93.1 | 95.7 | 96.3 | 96.8 | 96.9 | 96.9 | 96.6 | 93.6 | 96.4 | 97 | 97.5 | 97.6 | 97.5 | 97.3
Power-One | UNO-8.6-TL-OUTD-S-US-A [240V] | transformerless Utility Interactive Inverter with arc detector | 8.6 | 240 | 96.5 | Y | N |  | 1.5 |  |  | 100 | 380 | 480 | 0.86 | 1.72 | 2.58 | 4.3 | 6.45 | 8.6 | 92.1 | 94.9 | 95.6 | 95.9 | 95.9 | 95.8 | 95.7 | 93.6 | 95.9 | 96.5 | 96.8 | 96.9 | 96.8 | 96.6 | 94.2 | 96.7 | 97.2 | 97.5 | 97.6 | 97.5 | 97.3
Power-One | UNO-8.6-TL-OUTD-S-US-A [277V] | transformerless Utility Interactive Inverter with arc detector | 8.6 | 277 | 96.5 | Y | N |  | 1.4 |  |  | 100 | 380 | 480 | 0.86 | 1.72 | 2.58 | 4.3 | 6.45 | 8.6 | 93 | 95.2 | 95.8 | 96 | 95.9 | 95.7 | 95.8 | 95.4 | 97 | 97.4 | 97.5 | 97.5 | 97.3 | 97.3 | 94 | 96.4 | 96.9 | 97.2 | 97.2 | 97 | 97
Power-One | UNO-8.6-TL-OUTD-S-US-Z-A [240V] | transformerless Utility Interactive Inverter with arc detector | 8.6 | 240 | 96.5 | Y | N |  | 1.5 |  |  | 100 | 380 | 480 | 0.86 | 1.72 | 2.58 | 4.3 | 6.45 | 8.6 | 92.1 | 94.9 | 95.6 | 95.9 | 95.9 | 95.8 | 95.7 | 93.6 | 95.9 | 96.5 | 96.8 | 96.9 | 96.8 | 96.6 | 94.2 | 96.7 | 97.2 | 97.5 | 97.6 | 97.5 | 97.3
Power-One | UNO-8.6-TL-OUTD-S-US-Z-A [277V] | transformerless Utility Interactive Inverter with arc detector | 8.6 | 277 | 96.5 | Y | N |  | 1.4 |  |  | 100 | 380 | 480 | 0.86 | 1.72 | 2.58 | 4.3 | 6.45 | 8.6 | 93 | 95.2 | 95.8 | 96 | 95.9 | 95.7 | 95.8 | 95.4 | 97 | 97.4 | 97.5 | 97.5 | 97.3 | 97.3 | 94 | 96.4 | 96.9 | 97.2 | 97.2 | 97 | 97
Power-One | PVI-10.0-I-OUTD-x-US-208-y [208V] | 10 kW, 208 Vac Inverter, x may be empty, S, S1 or S2; y either PG or NG | 10 | 208 | 96 | Y | N | Multiple Listing of ABB | 0.1 | 10 | 0.1 | 220 | 320 | 416 | 1 | 2 | 3 | 5 | 7.5 | 10 | 94.5 | 96.1 | 96.2 | 96.3 | 95.7 | 94.8 | 95.8 | 94.4 | 96.3 | 96.5 | 96.5 | 96.3 | 95.7 | 96.2 | 93.1 | 95.7 | 96.2 | 96.2 | 95.9 | 95.5 | 95.8
Power-One | PVI-10.0-I-OUTD-x-US-480-y-z [480V] | 10 kW, 480 Vac Inverter, x may be empty, S, S1 or S2; y either PG or NG; z may be empty or 12A | 10 | 480 | 97 | Y | N | Multiple Listing of ABB | 0.4 | 10 | 0.4 | 220 | 362 | 416 | 1 | 2 | 3 | 5 | 7.5 | 10 | 92.7 | 95.4 | 96.2 | 96.9 | 96.8 | 96.4 | 96.5 | 92.6 | 96 | 96.8 | 97.2 | 97.3 | 97.3 | 97 | 92.3 | 95.9 | 96.8 | 97.3 | 97.3 | 97.3 | 97
Power-One | PVI-12.0-I-OUTD-x-US-480-y [480V] | 12 kW, 480 Vac Inverter, x may be empty, S, S1 or S2; y either PG or NG | 12 | 480 | 97 | Y | N | Multiple Listing of ABB | 0.4 | 12 | 0.4 | 250 | 370 | 416 | 1.2 | 2.4 | 3.6 | 6 | 9 | 12 | 93.7 | 96 | 96.5 | 97 | 96.9 | 96.4 | 96.7 | 93.6 | 96.3 | 97 | 97.2 | 97.3 | 97.2 | 97 | 93.4 | 96.4 | 97 | 97.2 | 97.3 | 97.3 | 97.1
Power-One | TRIO-20.0-TL-OUTD-S1-480-A [480V] | 20 kW, 480 Vac Inverter with arc detector | 20 | 480 | 97.5 | Y | N |  | 0.61 |  |  | 450 | 700 | 800 | 2 | 4 | 6 | 10 | 15 | 20 | 93.5 | 95.4 | 96.3 | 96.9 | 97 | 97 | 96.7 | 94.5 | 96.7 | 97.3 | 97.7 | 97.7 | 97.7 | 97.5 | 95.4 | 97.2 | 97.8 | 98.1 | 98.2 | 98.1 | 97.9
Power-One | TRIO-20.0-TL-OUTD-S1A-480-A [480V] | 20 kW, 480 Vac Inverter with arc detector | 20 | 480 | 97.5 | Y | N |  | 0.61 |  |  | 450 | 700 | 800 | 2 | 4 | 6 | 10 | 15 | 20 | 93.5 | 95.4 | 96.3 | 96.9 | 97 | 97 | 96.7 | 94.5 | 96.7 | 97.3 | 97.7 | 97.7 | 97.7 | 97.5 | 95.4 | 97.2 | 97.8 | 98.1 | 98.2 | 98.1 | 97.9
Power-One | TRIO-20.0-TL-OUTD-S1A-US-480 [480V] | 20 kW, 480 Vac Inverter with arc detector | 20 | 480 | 97.5 | Y | N | Multiple Listing of ABB | 0.61 |  |  | 450 | 700 | 800 | 2 | 4 | 6 | 10 | 15 | 20 | 93.5 | 95.4 | 96.3 | 96.9 | 97 | 97 | 96.7 | 94.5 | 96.7 | 97.3 | 97.7 | 97.7 | 97.7 | 97.5 | 95.4 | 97.2 | 97.8 | 98.1 | 98.2 | 98.1 | 97.9
Power-One | TRIO-20.0-TL-OUTD-S1B-480-A [480V] | 20 kW, 480 Vac Inverter with arc detector | 20 | 480 | 97.5 | Y | N |  | 0.61 |  |  | 450 | 700 | 800 | 2 | 4 | 6 | 10 | 15 | 20 | 93.5 | 95.4 | 96.3 | 96.9 | 97 | 97 | 96.7 | 94.5 | 96.7 | 97.3 | 97.7 | 97.7 | 97.7 | 97.5 | 95.4 | 97.2 | 97.8 | 98.1 | 98.2 | 98.1 | 97.9
Power-One | TRIO-20.0-TL-OUTD-S1B-US-480 [480V] | 20 kW, 480 Vac Inverter with arc detector | 20 | 480 | 97.5 | Y | N | Multiple Listing of ABB | 0.61 |  |  | 450 | 700 | 800 | 2 | 4 | 6 | 10 | 15 | 20 | 93.5 | 95.4 | 96.3 | 96.9 | 97 | 97 | 96.7 | 94.5 | 96.7 | 97.3 | 97.7 | 97.7 | 97.7 | 97.5 | 95.4 | 97.2 | 97.8 | 98.1 | 98.2 | 98.1 | 97.9
Power-One | TRIO-20.0-TL-OUTD-S1-US-480 [480V] | 20 kW, 480 Vac Inverter with arc detector | 20 | 480 | 97.5 | Y | N | Multiple Listing of ABB | 0.61 |  |  | 450 | 700 | 800 | 2 | 4 | 6 | 10 | 15 | 20 | 93.5 | 95.4 | 96.3 | 96.9 | 97 | 97 | 96.7 | 94.5 | 96.7 | 97.3 | 97.7 | 97.7 | 97.7 | 97.5 | 95.4 | 97.2 | 97.8 | 98.1 | 98.2 | 98.1 | 97.9
Power-One | TRIO-20.0-TL-OUTD-S-480-A [480V] | 20 kW, 480 Vac Inverter with arc detector | 20 | 480 | 97.5 | Y | N |  | 0.61 |  |  | 450 | 700 | 800 | 2 | 4 | 6 | 10 | 15 | 20 | 93.5 | 95.4 | 96.3 | 96.9 | 97 | 97 | 96.7 | 94.5 | 96.7 | 97.3 | 97.7 | 97.7 | 97.7 | 97.5 | 95.4 | 97.2 | 97.8 | 98.1 | 98.2 | 98.1 | 97.9
Power-One | TRIO-20.0-TL-OUTD-S-US-480 [480V] | 20 kW, 480 Vac Inverter with arc detector | 20 | 480 | 97.5 | Y | N | Multiple Listing of ABB | 0.61 |  |  | 450 | 700 | 800 | 2 | 4 | 6 | 10 | 15 | 20 | 93.5 | 95.4 | 96.3 | 96.9 | 97 | 97 | 96.7 | 94.5 | 96.7 | 97.3 | 97.7 | 97.7 | 97.7 | 97.5 | 95.4 | 97.2 | 97.8 | 98.1 | 98.2 | 98.1 | 97.9
Power-One | TRIO-27.6-TL-OUTD-S1-480-A [480V] | 27.6 kW, 480 Vac Inverter with arc detector | 27.6 | 480 | 97.5 | Y | N |  | 0.61 |  |  | 520 | 715 | 800 | 2.76 | 5.52 | 8.28 | 13.8 | 20.7 | 27.6 | 94.8 | 96.4 | 97 | 97.4 | 97.4 | 97.3 | 97.2 | 95.4 | 97.1 | 97.6 | 97.8 | 97.9 | 97.8 | 97.7 | 96.1 | 97.6 | 98 | 98.2 | 98.2 | 98.2 | 98.1
Power-One | TRIO-27.6-TL-OUTD-S1A-480-A [480V] | 27.6 kW, 480 Vac Inverter with arc detector | 27.6 | 480 | 97.5 | Y | N |  | 0.61 |  |  | 520 | 715 | 800 | 2.76 | 5.52 | 8.28 | 13.8 | 20.7 | 27.6 | 94.8 | 96.4 | 97 | 97.4 | 97.4 | 97.3 | 97.2 | 95.4 | 97.1 | 97.6 | 97.8 | 97.9 | 97.8 | 97.7 | 96.1 | 97.6 | 98 | 98.2 | 98.2 | 98.2 | 98.1
Power-One | TRIO-27.6-TL-OUTD-S1A-US-480 [480V] | 27.6 kW, 480 Vac Inverter with arc detector | 27.6 | 480 | 97.5 | Y | N | Multiple Listing of ABB | 0.61 |  |  | 520 | 715 | 800 | 2.76 | 5.52 | 8.28 | 13.8 | 20.7 | 27.6 | 94.8 | 96.4 | 97 | 97.4 | 97.4 | 97.3 | 97.2 | 95.4 | 97.1 | 97.6 | 97.8 | 97.9 | 97.8 | 97.7 | 96.1 | 97.6 | 98 | 98.2 | 98.2 | 98.2 | 98.1
Power-One | TRIO-27.6-TL-OUTD-S1B-480-A [480V] | 27.6 kW, 480 Vac Inverter with arc detector | 27.6 | 480 | 97.5 | Y | N |  | 0.61 |  |  | 520 | 715 | 800 | 2.76 | 5.52 | 8.28 | 13.8 | 20.7 | 27.6 | 94.8 | 96.4 | 97 | 97.4 | 97.4 | 97.3 | 97.2 | 95.4 | 97.1 | 97.6 | 97.8 | 97.9 | 97.8 | 97.7 | 96.1 | 97.6 | 98 | 98.2 | 98.2 | 98.2 | 98.1
Power-One | TRIO-27.6-TL-OUTD-S1B-US-480 [480V] | 27.6 kW, 480 Vac Inverter with arc detector | 27.6 | 480 | 97.5 | Y | N | Multiple Listing of ABB | 0.61 |  |  | 520 | 715 | 800 | 2.76 | 5.52 | 8.28 | 13.8 | 20.7 | 27.6 | 94.8 | 96.4 | 97 | 97.4 | 97.4 | 97.3 | 97.2 | 95.4 | 97.1 | 97.6 | 97.8 | 97.9 | 97.8 | 97.7 | 96.1 | 97.6 | 98 | 98.2 | 98.2 | 98.2 | 98.1
Power-One | TRIO-27.6-TL-OUTD-S1-US-480 [480V] | 27.6 kW, 480 Vac Inverter with arc detector | 27.6 | 480 | 97.5 | Y | N | Multiple Listing of ABB | 0.61 |  |  | 520 | 715 | 800 | 2.76 | 5.52 | 8.28 | 13.8 | 20.7 | 27.6 | 94.8 | 96.4 | 97 | 97.4 | 97.4 | 97.3 | 97.2 | 95.4 | 97.1 | 97.6 | 97.8 | 97.9 | 97.8 | 97.7 | 96.1 | 97.6 | 98 | 98.2 | 98.2 | 98.2 | 98.1
Power-One | TRIO-27.6-TL-OUTD-S-480-A [480V] | 27.6 kW, 480 Vac Inverter with arc detector | 27.6 | 480 | 97.5 | Y | N |  | 0.61 |  |  | 520 | 715 | 800 | 2.76 | 5.52 | 8.28 | 13.8 | 20.7 | 27.6 | 94.8 | 96.4 | 97 | 97.4 | 97.4 | 97.3 | 97.2 | 95.4 | 97.1 | 97.6 | 97.8 | 97.9 | 97.8 | 97.7 | 96.1 | 97.6 | 98 | 98.2 | 98.2 | 98.2 | 98.1
Power-One | TRIO-27.6-TL-OUTD-S-US-480 [480V] | 27.6 kW, 480 Vac Inverter with arc detector | 27.6 | 480 | 97.5 | Y | N | Multiple Listing of ABB | 0.61 |  |  | 520 | 715 | 800 | 2.76 | 5.52 | 8.28 | 13.8 | 20.7 | 27.6 | 94.8 | 96.4 | 97 | 97.4 | 97.4 | 97.3 | 97.2 | 95.4 | 97.1 | 97.6 | 97.8 | 97.9 | 97.8 | 97.7 | 96.1 | 97.6 | 98 | 98.2 | 98.2 | 98.2 | 98.1
Power-One | PVI-CENTRAL-50-US [208V] | 50 kW, 208 Vac Utility Interactive Inverter | 50 | 208 | 95 | Y | N | Multiple Listing of ABB | 33 | 50 | 33 | 330 | 370 | 480 | 5 | 10 | 15 | 25 | 37.5 | 50 | 90.7 | 94.5 | 95.4 | 95.6 | 95.3 | 94.7 | 95.1 | 90.4 | 94.4 | 95.3 | 95.6 | 95.2 | 94.6 | 95 | 89.7 | 94 | 94.8 | 95.2 | 94.9 | 94.4 | 94.7
Power-One | PVI-CENTRAL-50-US [480V] | 50 kW, 480 Vac Utility Interactive Inverter | 50 | 480 | 95 | Y | N | Multiple Listing of ABB | 41 | 50 | 41 | 330 | 370 | 480 | 5 | 10 | 15 | 25 | 37.5 | 50 | 90.5 | 94.4 | 95.3 | 95.7 | 95.6 | 95.1 | 95.3 | 90.2 | 94.2 | 95.2 | 95.6 | 95.5 | 95 | 95.2 | 89.5 | 93.8 | 94.9 | 95.3 | 95.3 | 94.8 | 94.9
Power-One | PVI-CENTRAL-100-US [208V] | 100 kW, 208 Vac Utility Interactive Inverter | 100 | 208 | 95 | Y | N | Multiple Listing of ABB | 47 | 100 | 47 | 330 | 370 | 480 | 10 | 20 | 30 | 50 | 75 | 100 | 91.5 | 94.7 | 95.4 | 95.6 | 95.3 | 94.7 | 95.2 | 91.2 | 94.5 | 95.3 | 95.5 | 95.2 | 94.6 | 95.1 | 90.3 | 94.1 | 94.9 | 95.2 | 95 | 94.4 | 94.7
Power-One | PVI-CENTRAL-100-US [480V] | 100 kW, 480 Vac Utility Interactive Inverter | 100 | 480 | 95 | Y | N | Multiple Listing of ABB | 50 | 100 | 50 | 330 | 370 | 480 | 10 | 20 | 30 | 50 | 75 | 100 | 91.5 | 94.8 | 95.5 | 95.7 | 95.5 | 94.7 | 95.3 | 91.2 | 94.6 | 95.3 | 95.6 | 95.4 | 94.6 | 95.2 | 90.3 | 94.2 | 95 | 95.3 | 95.1 | 94.4 | 94.8
Power-One | PVI-CENTRAL-250-US [480V] | 250 kW, 480 Vac Utility Interactive Inverter | 250 | 480 | 97 | Y | N | Multiple Listing of ABB | 105.3 | 250 | 105.3 | 320 | 360 | 480 | 25 | 50 | 75 | 125 | 187.5 | 250 | 95.7 | 97.5 | 97.5 | 97.6 | 97 | 96.6 | 97.1 | 95.4 | 97.2 | 97.3 | 97.4 | 96.8 | 96.5 | 96.9 | 94.1 | 96 | 96.3 | 96.7 | 96.5 | 96 | 96.3
Power-One | PVI-CENTRAL-300-US [480V] | 300 kW, 480 Vac Utility Interactive Inverter | 300 | 480 | 97 | Y | N | Multiple Listing of ABB | 119 | 300 | 119 | 320 | 360 | 480 | 30 | 60 | 90 | 150 | 225 | 300 | 96.2 | 97.5 | 97.6 | 97.6 | 97.1 | 96.5 | 97.2 | 95.8 | 97.3 | 97.4 | 97.4 | 96.9 | 96.4 | 97 | 94.8 | 96.2 | 96.3 | 96.6 | 96.3 | 95.8 | 96.3
Power-One | ULTRA-750-TL-OUTD-2-US-690-x-y-z [690V] | 750 kW, 690 Vac Utility Interactive Inverter with Medium Voltage NEMA TP1 transformer | 750 | 690 | 96.5 | Y | N | Multiple Listing of ABB | 301.7 |  |  | 585 | 746 | 800 | 75 | 150 | 225 | 375 | 562.5 | 750 | 94.5 | 95.8 | 96.2 | 96.2 | 95.9 | 95.1 | 95.9 | 95 | 96.5 | 96.7 | 96.9 | 96.5 | 95.9 | 96.5 | 95.1 | 96.6 | 96.9 | 97 | 96.7 | 96.1 | 96.7
Power-One | ULTRA-750-TL-OUTD-4-US-690-x-y-z [690V] | 750 kW, 690 Vac Utility Interactive Inverter with Medium Voltage NEMA TP1 transformer | 750 | 690 | 96.5 | Y | N | Multiple Listing of ABB | 346.8 |  |  | 585 | 746 | 800 | 75 | 150 | 225 | 375 | 562.5 | 750 | 94.4 | 96 | 96.4 | 96.5 | 96.1 | 95.4 | 96.1 | 94.9 | 96.5 | 96.8 | 97.1 | 96.8 | 96.2 | 96.7 | 95 | 96.6 | 96.9 | 97.1 | 96.9 | 96.4 | 96.8
Power-One | ULTRA-750-TL-OUTD-1-US-690-x-y-z [690V] | 750 kW, 690 Vac Utility Interactive Inverter with Medium Voltage NEMA TP1 transformer | 780 | 690 | 96.5 | Y | N | Multiple Listing of ABB | 302 |  |  | 585 | 746 | 800 | 78 | 156 | 234 | 390 | 585 | 780 | 94.4 | 95.8 | 96.1 | 96.2 | 95.8 | 95.1 | 95.8 | 94.9 | 96.4 | 96.7 | 96.9 | 96.5 | 96 | 96.5 | 95.1 | 96.6 | 96.9 | 97 | 96.7 | 96.2 | 96.7
Power-One | ULTRA-750-TL-OUTD-3-US-690-x-y-z [690V] | 750 kW, 690 Vac Utility Interactive Inverter with Medium Voltage NEMA TP1 transformer | 780 | 690 | 96.5 | Y | N | Multiple Listing of ABB | 346.8 |  |  | 585 | 746 | 800 | 78 | 156 | 234 | 390 | 585 | 780 | 94.5 | 96 | 96.4 | 96.4 | 96 | 95.3 | 96.1 | 95 | 96.5 | 97 | 97.1 | 96.8 | 96.2 | 96.7 | 95.1 | 96.6 | 97.1 | 97.2 | 96.9 | 96.3 | 96.9
Power-One | ULTRA-1100-TL-OUTD-2-US-690-x-y-z [690V] | 1100 kW, 690 Vac Utility Interactive Inverter with Medium Voltage NEMA TP1 transformer | 1000 | 690 | 96.5 | Y | N | Multiple Listing of ABB | 328.8 |  |  | 585 | 746 | 800 | 100 | 200 | 300 | 500 | 750 | 1000 | 94.5 | 96.1 | 96.5 | 96.5 | 96.2 | 95.4 | 96.2 | 94.9 | 96.7 | 97.1 | 97.1 | 96.8 | 96.2 | 96.8 | 95.1 | 96.9 | 97.2 | 97.3 | 96.9 | 96.4 | 96.9
Power-One | ULTRA-1100-TL-OUTD-4-US-690-x-y-z [690V] | 1100 kW, 690 Vac Utility Interactive Inverter with Medium Voltage NEMA TP1 transformer | 1000 | 690 | 97 | Y | N | Multiple Listing of ABB | 381.6 |  |  | 585 | 746 | 800 | 100 | 200 | 300 | 500 | 750 | 1000 | 94.5 | 96.2 | 96.6 | 96.8 | 96.4 | 95.8 | 96.4 | 95 | 96.8 | 97.2 | 97.3 | 97 | 96.5 | 97 | 95.1 | 96.9 | 97.4 | 97.4 | 97.1 | 96.6 | 97.1
Power-One | ULTRA-1100-TL-OUTD-1-US-690-x-y-z [690V] | 1100 kW, 690 Vac Utility Interactive Inverter with Medium Voltage NEMA TP1 transformer | 1154 | 690 | 96.5 | Y | N | Multiple Listing of ABB | 329 |  |  | 585 | 746 | 800 | 117 | 234 | 351 | 585 | 877.5 | 1170 | 94.4 | 96 | 96.4 | 96.5 | 96.1 | 95.4 | 96.1 | 95 | 96.6 | 97 | 97.1 | 96.8 | 96.2 | 96.8 | 95.1 | 96.8 | 97.2 | 97.3 | 97 | 96.4 | 97
Power-One | ULTRA-1100-TL-OUTD-3-US-690-x-y-z [690V] | 1100 kW, 690 Vac Utility Interactive Inverter with Medium Voltage NEMA TP1 transformer | 1170 | 690 | 97 | Y | N | Multiple Listing of ABB | 381.6 |  |  | 585 | 746 | 800 | 117 | 234 | 351 | 585 | 877.5 | 1170 | 94.6 | 96.3 | 96.6 | 96.7 | 96.3 | 95.6 | 96.3 | 95.2 | 96.8 | 97.3 | 97.3 | 96.9 | 96.3 | 96.9 | 95.3 | 96.9 | 97.4 | 97.4 | 97 | 96.5 | 97
Power-One | ULTRA-1500-TL-OUTD-2-US-690-x-y-z [690V] | 1500 kW, 690 Vac Utility Interactive Inverter with Medium Voltage NEMA TP1 transformer | 1500 | 690 | 96.5 | Y | N | Multiple Listing of ABB | 373.9 |  |  | 585 | 746 | 800 | 150 | 300 | 450 | 750 | 1125 | 1500 | 94.9 | 96.3 | 96.5 | 96.7 | 96.3 | 95.6 | 96.3 | 95.3 | 96.8 | 97 | 97.2 | 96.9 | 96.3 | 96.9 | 95.4 | 96.9 | 97.2 | 97.4 | 97 | 96.5 | 97
Power-One | ULTRA-1500-TL-OUTD-4-US-690-x-y-z [690V] | 1500 kW, 690 Vac Utility Interactive Inverter with Medium Voltage NEMA TP1 transformer | 1500 | 690 | 97 | Y | N | Multiple Listing of ABB | 430.1 |  |  | 585 | 746 | 800 | 150 | 300 | 450 | 750 | 1125 | 1500 | 94.9 | 96.5 | 96.8 | 97 | 96.5 | 95.8 | 96.5 | 95.4 | 97 | 97.3 | 97.5 | 97.1 | 96.6 | 97.1 | 95.5 | 97.1 | 97.4 | 97.6 | 97.3 | 96.7 | 97.2
Power-One | ULTRA-1500-TL-OUTD-1-US-690-x-y-z [690V] | 1500 kW, 690 Vac Utility Interactive Inverter with Medium Voltage NEMA TP1 transformer | 1550 | 690 | 96.5 | Y | N | Multiple Listing of ABB | 374 |  |  | 585 | 746 | 800 | 156 | 312 | 468 | 780 | 1170 | 1560 | 94.9 | 96.3 | 96.5 | 96.8 | 96.2 | 95.4 | 96.2 | 95.3 | 96.8 | 97.1 | 97.2 | 96.9 | 96.3 | 96.9 | 95.5 | 97 | 97.2 | 97.4 | 97.1 | 96.5 | 97
Power-One | ULTRA-1500-TL-OUTD-3-US-690-x-y-z [690V] | 1500 kW, 690 Vac Utility Interactive Inverter with Medium Voltage NEMA TP1 transformer | 1560 | 690 | 97 | Y | N | Multiple Listing of ABB | 430.1 |  |  | 585 | 746 | 800 | 156 | 312 | 468 | 780 | 1170 | 1560 | 94.9 | 96.5 | 96.8 | 97 | 96.4 | 95.7 | 96.5 | 95.4 | 97 | 97.3 | 97.5 | 97.1 | 96.6 | 97.1 | 95.5 | 97.1 | 97.4 | 97.6 | 97.2 | 96.7 | 97.2
Princeton Power Systems, Inc. | GTIB-480-30-WZZZZZZ-G1.3 [480V] | 30 kVA, 480 Vac, 830Vdc, Non-isolated, Bi-directional, Grid Support Utility Interactive PV or Battery Inverter; where Z can be -ATS, -GA, -F, -GN-W-H, -H, -EMOS, or blank. Cannot accept PV and Battery DC input simultaneously. | 29.444 | 480 | 93.5 | N | N |  | 35.14 |  |  | 540 | 750 | 830 | 2.9444 | 5.8889 | 8.8333 | 14.7222 | 22.0832 | 29.4443 | 86.7633 | 92.621 | 93.1032 | 93.8163 | 93.2421 | 92.0854 | 92.998 | 87.6485 | 93.2657 | 93.53 | 94.1163 | 93.4041 | 92.9205 | 93.3074 | 88.6063 | 92.4924 | 94.6691 | 94.5469 | 93.6549 | 93.0472 | 93.6735 | 2019-06-17
Princeton Power Systems, Inc. | GTIB-480-30-ZZZZZZ-G1.3 [480V] | 30 kVA, 480 Vac, 830Vdc, Transformerless, Non-isolated, Bi-directional, Grid Support Utility Interactive PV or Battery Inverter; where Z can be -ATS, -GA, -F, -GN-W-H, -H, -EMOS, or blank (Z≠-W). Cannot accept PV and Battery DC input simultaneously. | 29.956 | 480 | 97 | N | N |  | 46.3 |  |  | 540 | 750 | 830 | 2.9956 | 5.9911 | 8.9867 | 14.9778 | 22.4667 | 29.9557 | 92.6541 | 95.1194 | 96.0767 | 96.8464 | 96.977 | 96.8538 | 96.5696 | 93.7759 | 95.2415 | 96.5013 | 97.1768 | 97.3758 | 97.3985 | 96.9795 | 92.7942 | 94.8855 | 96.3887 | 97.0579 | 97.1908 | 97.4251 | 96.7872 | 2019-06-17
Princeton Power Systems, Inc. | GTIB-208-30WYYYYYY [208V] | 30 kW, 208 Vac, 780 Vdc max, 3-phase Utility Interactive Inverter with transformer, where Y= -ATS, -GA, -F, - GN-H, -H, -EMOS, or (blank) W, – Integrated transformer that provides AC/DC isolation. | 30 | 208 | 93 | N | N |  | 98.9 |  |  | 280 | 650 | 780 | 3 | 6 | 9 | 15 | 22.5 | 30 | 83.2 | 89.7 | 91.7 | 92.5 | 92.1 | 91.3 | 91.6 | 88.4 | 91.9 | 93.2 | 93.6 | 93.1 | 93.3 | 93 | 89 | 92.3 | 93.6 | 94.2 | 93.9 | 93.3 | 93.6 | 2017-06 | 2019-06-17
Princeton Power Systems, Inc. | GTIB30-480BGNSC [480V] | 30 kW, 480 Vac, 3-phase Utility Interactive Inverter | 30 | 480 | 92.5 | Y | N |  | 64.2 |  |  | 280 | 443 | 580 | 3 | 6 | 9 | 15 | 22.5 | 30 | 80.1 | 88.6 | 91.3 | 92.5 | 92.4 | 91.7 | 91.6 | 80.1 | 88.7 | 91.6 | 93.4 | 93.6 | 93.3 | 92.5 | 83 | 90.7 | 93.6 | 94.1 | 94.2 | 94 | 93.5 |  | 2019-06-17
Princeton Power Systems, Inc. | GTIB-480-30-WZZZZZZ [480V] | 30 kW, 480 Vac, 780 Vdc max, 3-phase Utility Interactive Inverter without transformer, where Z = -W, -ATS, -GA, -F, -GN-W-H, -H, -EMOS, or (blank) | 30 | 480 | 92.5 | N | N |  | 98.9 |  |  | 280 | 650 | 780 | 3 | 6 | 9 | 15 | 22.5 | 30 | 82.4 | 89.1 | 91.3 | 92.2 | 91.7 | 90.9 | 91.2 | 88.2 | 91.6 | 92.7 | 93.6 | 93.3 | 92.9 | 93 | 88.6 | 92.6 | 93.6 | 94 | 93.7 | 93 | 93.5 | 2017-06 | 2019-06-17
Princeton Power Systems, Inc. | GTIB-480-30-ZZZZZZZ [480V] | 30 kW, 480 Vac, 780 V dc max, 3-phase Utility Interactive Inverter without transformer, where Z = -ATS, -GA, -F, -GN-H, -H, -EMOS, or (blank) | 30 | 480 | 95.5 | N | N |  | 98.9 |  |  | 280 | 650 | 780 | 3 | 6 | 9 | 15 | 22.5 | 30 | 86.1 | 90.9 | 93.6 | 94.7 | 95.3 | 95.3 | 94.4 | 91.3 | 94.2 | 95.3 | 96.2 | 96.6 | 96.6 | 96 | 91.4 | 94.6 | 95.6 | 96.6 | 97 | 97.1 | 96.4 | 2017-06 | 2019-06-17
Princeton Power Systems, Inc. | GTIB-480-100-xxxx [480V] [480Vdc] | 100 kW, 480 Vac, 480 Vdc max Utility Interactive Inverter | 100 | 480 | 94.5 | N | N |  | 170 |  |  | 330 | 400 | 480 | 10 | 20 | 30 | 50 | 75 | 100 | 87.42 | 92.23 | 93.54 | 94.53 | 94.49 | 93.87 | 93.96 | 87.74 | 92.55 | 93.79 | 94.76 | 94.76 | 94.43 | 94.24 | 88.37 | 93.27 | 94.56 | 95.46 | 95.59 | 95.07 | 95.01 |  | 2019-06-17
Princeton Power Systems, Inc. | GTIB-480-100-xxxx [480V] [600Vdc] | 100 kW, 480 Vac, 600 Vdc Utility Interactive Inverter | 100 | 480 | 95 | N | N |  | 170 |  |  | 330 | 480 | 600 | 10 | 20 | 30 | 50 | 75 | 100 | 87.42 | 92.23 | 93.54 | 94.53 | 94.49 | 93.87 | 93.96 | 88.37 | 93.27 | 94.56 | 95.46 | 95.59 | 95.07 | 95.01 | 89.35 | 93.63 | 94.97 | 95.74 | 95.84 | 95.4 | 95.32 |  | 2019-06-17
Princeton Power Systems, Inc. | GTIB-480-100X-YYYYYYYY-Z-G1.2 [480V] | 100 kW, 480 Vac, 800 Vdc, 3-phase, Utility Interactive Inverter with Princeton Power Systems transformer | 100 | 480 | 94.5 | Y | N |  | 69.52 |  |  | 280 | 670 | 800 | 10 | 20 | 30 | 50 | 75 | 100 | 86.9 | 91.9 | 93.3 | 93.9 | 93.5 | 93 | 93.2 | 88.2 | 92.8 | 94.4 | 95.3 | 95.3 | 94.9 | 94.7 | 89.5 | 94 | 95.1 | 95.7 | 95.6 | 95.3 | 95.2 |  | 2019-06-17
Princeton Power Systems, Inc. | GTIB-480-125XXXXXX-G1.5 [480V] | 125 kVA, 480 Vac, 830Vdc, Transformerless, Non-isolated, Grid Support Utility Interactive PV or Battery Inverter; where X can be -B, -D, -DH, -DA, -DD, -GN, -M, -OV, -V, or blank. Cannot accept PV and Battery DC input simultaneously. | 124.964 | 480 | 96 | N | N |  | 68 |  |  | 350 | 710 | 830 | 12.4964 | 24.9928 | 37.4892 | 62.482 | 93.723 | 124.964 | 87.1196 | 92.9413 | 94.9723 | 95.2179 | 95.6593 | 95.2115 | 94.9843 | 91.9189 | 95.3761 | 95.8979 | 96.6258 | 96.8865 | 96.649 | 96.427 | 91.5596 | 95.713 | 96.4245 | 96.9684 | 96.936 | 96.8929 | 96.6031 | 2019-06-17
Princeton Power Systems, Inc. | GTIB-480-125XXXXXX-W-G1.5 [480V] | 125 kVA, 480 Vac, 830Vdc, Non-isolated, Grid Support Utility Interactive PV or Battery Inverter; where X can be -B, -D, -DH, -DA, -DD, -GN, -M, -OV, -V, or blank. Cannot accept PV and Battery DC input simultaneously. | 124.964 | 480 | 94.5 | N | N | Weighted Efficiency includes efficiency of 125 kVA Jefferson Electric 423-D007-013 distribution transformer. | 68 |  |  | 350 | 710 | 830 | 12.4964 | 24.9928 | 37.4892 | 62.482 | 93.723 | 124.964 | 84.9387 | 91.6494 | 93.8422 | 94.0171 | 94.1574 | 93.2247 | 93.5493 | 89.6179 | 94.0504 | 94.7567 | 95.4072 | 95.3654 | 94.6322 | 94.9688 | 89.2675 | 94.3826 | 95.2771 | 95.7455 | 95.4141 | 94.8711 | 95.1427 | 2019-06-17
Princeton Power Systems, Inc. | GTIB-480-125-XXXXXX-W-G1.3 [480V] | 125 kW, 480 Vac, 800 Vdc max, 3-phase Utility Interactive Inverter with transformer, where X = B, D, DH, GN, M, OV, V or blank B=Battery Temperature sensor D=Microgrid Option (dark start option)-254-780 Vdc (cannot be used with DH option) DH= Microgrid Option (dark start option)-450-800 Vdc (cannot be used with D option) GN= Ground Fault Detector/interrupter module installed, negatively grounded (cannot be used when position Y is blank) M= Integrated Revenue Meter with Modbus over TCP/IP OV=DC port overvoltage relay V=Low voltage option DC36-800V (Cannot be used with D or DH option) Position Y=X,W, or blank | 125 | 480 | 94 | N | N |  | 99.7 |  |  | 280 | 670 | 800 | 12.5 | 25 | 37.5 | 62.5 | 93.8 | 125 | 85.8 | 91.3 | 92.8 | 93.8 | 94 | 93.8 | 93.3 | 86.5 | 92.2 | 93.6 | 94.8 | 94.9 | 94.8 | 94.2 | 86.7 | 92.5 | 94 | 97 | 95.2 | 95.2 | 94.6 | 2017-06 | 2019-06-17
Princeton Power Systems, Inc. | GTIB-480-125-XXXXXX-Y-G1.3 [480V] | 125 kW, 480 Vac, 800 Vdc max, 3-phase Utility Interactive Inverter without transformer, where X=B, D, DH, GN, M, OV, V or (blank) B=Battery Temperature sensor D=Microgrid Option (dark start option)-254-780 Vdc (cannot be used with DH option) DH= Microgrid Option (dark start option)-450-800 Vdc (cannot be used with D option) GN= Ground Fault Detector/interrupter module installed, negatively grounded (cannot be used when position Y is blank) M= Integrated Revenue Meter with Modbus over TCP/IP OV=DC port overvoltage relay V=Low voltage option DC36-800V (cannot be used with D or DH option) Y=X,W, or blank | 125 | 480 | 96 | N | N |  | 99.7 |  |  | 354 | 670 | 800 | 12.5 | 25 | 37.5 | 62.5 | 93.8 | 125 | 91 | 94.1 | 95.2 | 95.6 | 95.7 | 95.5 | 95.3 | 91.5 | 94.9 | 95.9 | 96.5 | 96.7 | 96.6 | 96.3 | 92.3 | 95.6 | 96.4 | 96.9 | 97 | 96.9 | 96.6 | 2017-06 | 2019-06-17
Princeton Power Systems, Inc. | BIGI-250-X48GNMNR [480V] | 250 kW, 2-input, 480V 3-phase Inverter | 250 | 480 | 94.5 | Y | N |  | 138 |  |  | 417 | 490 | 580 | 25 | 50 | 75 | 125 | 187.5 | 250 | 87.2 | 92.4 | 94 | 94.8 | 94.7 | 94.3 | 94.2 | 87.6 | 92.7 | 94.2 | 95 | 94.9 | 94.6 | 94.4 | 88 | 92.9 | 94.4 | 95.3 | 95.2 | 94.7 | 94.7 |  | 2019-06-17
Princeton Power Systems, Inc. | BIGI-250-X48GNNR [480V] | 250 kW, 2-input, 480V 3-phase Inverter | 250 | 480 | 94.5 | N | N |  | 138 |  |  | 417 | 490 | 580 | 25 | 50 | 75 | 125 | 187.5 | 250 | 87.2 | 92.4 | 94 | 94.8 | 94.7 | 94.3 | 94.2 | 87.6 | 92.7 | 94.2 | 95 | 94.9 | 94.6 | 94.4 | 88 | 92.9 | 94.4 | 95.3 | 95.2 | 94.7 | 94.7 |  | 2019-06-17
PV Powered | PVP1100 | 1100 W Utility Interactive Inverter | 1.1 |  | 91.5 | Y | N |  | 3.6 |  |  | 100 | 207.5 | 380 | 0.11 | 0.22 | 0.33 | 0.55 | 0.83 | 1.1 | 80.8 | 89 | 91.1 | 92.7 | 93.3 | 93.3 | 92.2 | 78.9 | 87.9 | 90.4 | 92.3 | 92.9 | 93.1 | 91.7 | 73.5 | 84.8 | 88.1 | 90.7 | 91.7 | 92 | 90
PV Powered | PVP1100EVR [120V] | 1100 W, 120 Vac Utility Interactive Inverter with extended voltage range | 1.1 | 120 | 90.5 | Y | N |  | 3.6 |  |  | 100 | 182 | 380 | 0.11 | 0.22 | 0.33 | 0.55 | 0.83 | 1.1 | 81.8 | 89 | 90.9 | 92.1 | 92.4 | 92.5 | 91.6 | 79.9 | 88 | 90.1 | 91.7 | 92.2 | 92.3 | 91.1 | 74.8 | 84.7 | 87.8 | 90 | 90.8 | 91.1 | 89.3
PV Powered | PVP2000 [120V] | 2000 W, 120 Vac Utility Interactive Inverter | 2 | 120 | 92.5 | Y | N |  | 3.6 |  |  | 100 | 207.5 | 380 | 0.2 | 0.4 | 0.6 | 1 | 1.5 | 2 | 85.7 | 91.4 | 92.8 | 93.7 | 93.9 | 93.7 | 93.3 | 84.5 | 90.8 | 92.4 | 93.5 | 93.6 | 93.5 | 92.9 | 81.1 | 88.8 | 90.9 | 92.3 | 92.7 | 92.6 | 91.7
PV Powered | PVP2000EVR [240V] | 2000 W, 240 Vac Utility Interactive Inverter with extended voltage range | 2 | 240 | 92 | Y | N |  | 3.6 |  |  | 100 | 199 | 380 | 0.2 | 0.4 | 0.6 | 1 | 1.5 | 2 | 87.3 | 91.7 | 92.6 | 93.5 | 93.2 | 93 | 92.9 | 85.7 | 90.8 | 92.1 | 92.9 | 92.9 | 92.6 | 92.4 | 82.4 | 88.8 | 90.5 | 91.6 | 91.8 | 91.6 | 91.1
PV Powered | PVP2500 [240V] | 2500 W, 240 Vac Utility Interactive Inverter | 2.5 | 240 | 94.5 | Y | N |  | 3.9 |  |  | 100 | 218 | 400 | 0.25 | 0.5 | 0.75 | 1.25 | 1.88 | 2.5 | 87.1 | 93.3 | 94.9 | 95.8 | 95.8 | 95.6 | 95.2 | 85.2 | 92.4 | 93.8 | 95.2 | 95.4 | 95.1 | 94.6 | 80.4 | 90 | 91.7 | 93.7 | 94.5 | 93.8 | 93.2
PV Powered | PVP2800-208 [208V] | 2800 W, 208 Vac Utility Interactive Inverter | 2.8 | 208 | 92 | Y | N |  | 3.85 |  |  | 100 | 230 | 380 | 0.28 | 0.56 | 0.84 | 1.4 | 2.1 | 2.8 | 81.5 | 89.7 | 91.6 | 92.9 | 93.1 | 93 | 92.2 | 80.8 | 89.3 | 91.3 | 92.7 | 92.9 | 92.8 | 92 | 78.3 | 87.9 | 90.2 | 91.9 | 92.2 | 92.1 | 91.1
PV Powered | PVP3000 [240V] | 3000 W, 240 Vac Utility Interactive Inverter | 3 | 240 | 93.5 | Y | N |  | 3.63 |  |  | 100 | 222.5 | 380 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 88.9 | 92.9 | 93.8 | 94.3 | 94.2 | 93.9 | 93.9 | 87.9 | 92.5 | 93.5 | 94.1 | 94 | 93.8 | 93.7 | 84.9 | 90.9 | 92.4 | 93.3 | 93.2 | 93 | 92.7
PV Powered | PVP3500 [240V] | 3500 W, 240 Vac Utility Interactive Inverter | 3.5 | 240 | 95.5 | Y | N |  | 3.86 |  |  | 100 | 263 | 400 | 0.35 | 0.7 | 1.05 | 1.75 | 2.63 | 3.5 | 87.2 | 93.1 | 95.4 | 96.5 | 96.7 | 96.6 | 95.9 | 85.7 | 92.2 | 94.9 | 96.2 | 96.4 | 96.3 | 95.5 | 82.1 | 90.2 | 93.6 | 95.4 | 95.7 | 95.6 | 94.5
PV Powered | PVP4600 [240V] | 4600 W, 240 Vac Utility Interactive Inverter | 4.6 | 240 | 95.5 | Y | N |  | 4 | 4.6 | 4 | 100 | 254 | 400 | 0.46 | 0.92 | 1.38 | 2.3 | 3.45 | 4.6 | 90.3 | 94.8 | 95.9 | 96.5 | 96.5 | 96.2 | 96.1 | 89.2 | 94.3 | 95.6 | 96.3 | 96.4 | 96.1 | 95.9 | 86.5 | 92.9 | 94.7 | 95.6 | 95.7 | 95.4 | 95
PV Powered | PVP4800 [240V] | 4800 W, 240 Vac Utility Interactive Inverter | 4.8 | 240 | 96 | Y | N |  | 4.1 |  |  | 100 | 263 | 400 | 0.48 | 0.96 | 1.44 | 2.4 | 3.6 | 4.8 | 86.8 | 93.5 | 95.5 | 97 | 97.2 | 97.1 | 96.4 | 85.5 | 92.9 | 95 | 96.7 | 96.9 | 96.8 | 96 | 84.5 | 91.5 | 93.9 | 95.9 | 96.2 | 96.1 | 95.1
PV Powered | PVP5200 [240V] | 5200 W, 240 Vac Utility Interactive Inverter | 5.2 | 240 | 96 | Y | N |  | 4 | 5.2 | 4 | 100 | 280 | 400 | 0.52 | 1.04 | 1.56 | 2.6 | 3.9 | 5.2 | 89.4 | 94.8 | 96 | 96.8 | 97 | 96.8 | 96.4 | 88.6 | 94.4 | 95.7 | 96.7 | 96.8 | 96.6 | 96.2 | 87.7 | 93.1 | 94.8 | 96.1 | 96.3 | 96.1 | 95.5
PV Powered | PVP30KW-208 [208V] | 30 kW, 208 Vac, 3-phase Utility Interactive Inverter with 330-600 Vdc input | 30 | 208 | 94 | Y | N |  | 17 | 30 | 17 | 330 | 368 | 480 | 3 | 6 | 9 | 15 | 22.5 | 30 | 89.8 | 93.6 | 94.5 | 94.7 | 94.6 | 94.1 | 94.4 | 89.4 | 93.2 | 94.3 | 94.5 | 94.4 | 94 | 94.2 | 87.6 | 92.4 | 93.5 | 94 | 93.9 | 93.5 | 93.5
PV Powered | PVP30KW-480 [480V] | 30 kW, 480 Vac, 3-phase Utility Interactive Inverter with 330-600 Vdc input | 30 | 480 | 94 | Y | N |  | 16 | 30 | 16 | 330 | 368 | 480 | 3 | 6 | 9 | 15 | 22.5 | 30 | 90.6 | 94 | 94.8 | 95.1 | 94.9 | 94.3 | 94.7 | 90 | 93.6 | 94.4 | 94.9 | 94.6 | 94.1 | 94.4 | 88.4 | 92.4 | 93.5 | 94.3 | 94 | 93.5 | 93.7
PV Powered | PVP30KW-LV-208 [208V] | 30 kW, 208 Vac, 3-phase Utility Interactive Inverter with 295-600 Vdc input | 30 | 208 | 93 | Y | N |  | 22 |  |  | 295 | 341 | 480 | 3 | 6 | 9 | 15 | 22.5 | 30 | 89.4 | 93 | 94.1 | 94.4 | 94.1 | 93.8 | 93.9 | 88.2 | 92.5 | 93.5 | 94.1 | 93.8 | 93.5 | 93.5 | 83.6 | 89.7 | 91.2 | 92.4 | 92.4 | 92.2 | 91.8
PV Powered | PVP30KW-LV-480 [480V] | 30 kW, 480 Vac, 3-phase Utility Interactive Inverter with 295-600 Vdc input | 30 | 480 | 93.5 | Y | N |  | 22 |  |  | 295 | 341 | 480 | 3 | 6 | 9 | 15 | 22.5 | 30 | 89.9 | 93.7 | 94.5 | 94.9 | 94.7 | 94.1 | 94.5 | 88.7 | 93 | 93.9 | 94.5 | 94.3 | 93.8 | 94 | 84.1 | 90.1 | 91.8 | 92.9 | 92.8 | 92.6 | 92.2
PV Powered | PVP35 kW-208 [208V] | 35 kW, 208 Vac, 3-phase Utility Interactive Inverter | 35 | 208 | 95.5 | Y | N |  | 38.63 |  |  | 295 | 341 | 480 | 3.5 | 7 | 10.5 | 17.5 | 26.25 | 35 | 93.3 | 95.6 | 96.2 | 96.2 | 95.8 | 95.3 | 95.8 | 92.6 | 95.3 | 95.9 | 95.9 | 95.6 | 95.1 | 95.5 | 90.5 | 94.1 | 94.9 | 95.1 | 94.9 | 94.5 | 94.7
PV Powered | PVP35 kW-480 [480V] | 35 kW, 480 Vac, 3-phase Utility Interactive Inverter | 35 | 480 | 96 | Y | N |  | 37.79 |  |  | 295 | 341 | 480 | 3.5 | 7 | 10.5 | 17.5 | 26.25 | 35 | 94.1 | 96.4 | 96.9 | 97 | 96.8 | 96.3 | 96.7 | 93.3 | 95.9 | 96.5 | 96.7 | 96.5 | 96 | 96.4 | 91.1 | 94.7 | 95.4 | 95.7 | 95.6 | 95.2 | 95.3
PV Powered | PVP35 kW-600 [600V] | 35 kW, 600 Vac, 3-phase Utility Interactive Inverter | 35 | 600 | 95.5 | Y | N |  | 37.27 |  |  | 295 | 341 | 480 | 3.5 | 7 | 10.5 | 17.5 | 26.25 | 35 | 93.6 | 95.9 | 96.3 | 96.4 | 96.1 | 95.7 | 96.1 | 93 | 95.5 | 96 | 96.1 | 96 | 95.6 | 95.8 | 91 | 94.5 | 95.1 | 95.4 | 95.3 | 95 | 95.1
PV Powered | PVP50KW-208 [208V] | 50 kW, 208 Vac, 3-phase Utility Interactive Inverter with 295-600 Vdc input | 50 | 208 | 96 | Y | N |  | 33 |  |  | 295 | 341 | 480 | 5 | 10 | 15 | 25 | 37.5 | 50 | 95 | 96.7 | 96.6 | 96.6 | 96 | 95.3 | 96.2 | 94.4 | 96.3 | 96.3 | 96.3 | 95.8 | 95.2 | 95.9 | 92.7 | 95.5 | 95.4 | 95.6 | 95.2 | 94.7 | 95.2
PV Powered | PVP50KW-480 [480V] | 50 kW, 480 Vac, 3-phase Utility Interactive Inverter with 295-600 Vdc input | 50 | 480 | 96 | Y | N |  | 33 |  |  | 295 | 341 | 480 | 5 | 10 | 15 | 25 | 37.5 | 50 | 95.7 | 96.8 | 97.2 | 97 | 96.4 | 95.9 | 96.6 | 95.2 | 96.5 | 97 | 96.8 | 96.2 | 95.8 | 96.4 | 93.8 | 95.6 | 96.3 | 96 | 95.6 | 95.3 | 95.7
PV Powered | PVP50KW-600 [600V] | 50 kW, 600 Vac, 3-phase Utility Interactive Inverter | 50 | 600 | 96 | Y | N |  | 43 |  |  | 295 | 341 | 480 | 5 | 10 | 15 | 25 | 37.5 | 50 | 94.2 | 96.2 | 96.6 | 96.6 | 96.2 | 95.7 | 96.2 | 93.6 | 95.9 | 96.3 | 96.3 | 96 | 95.6 | 95.9 | 91.6 | 94.8 | 95.4 | 95.5 | 95.3 | 95 | 95.1
PV Powered | PVP75KW-208 [208V] | 75 kW, 208 Vac, 3-phase Utility Interactive Inverter with 295-600 Vdc input | 75 | 208 | 95.5 | Y | N |  | 50 |  |  | 295 | 341 | 480 | 7.5 | 15 | 22.5 | 37.5 | 56.25 | 75 | 92.7 | 95.6 | 96.1 | 96 | 95.9 | 95.6 | 95.8 | 92 | 95.2 | 95.8 | 95.8 | 95.7 | 95.3 | 95.5 | 89.8 | 93.8 | 94.8 | 94.9 | 95 | 94.6 | 94.6
PV Powered | PVP75KW-480 [480V] | 75 kW, 480 Vac, 3-phase Utility Interactive Inverter with 295-600 Vdc input | 75 | 480 | 95.5 | Y | N |  | 50 |  |  | 295 | 341 | 480 | 7.5 | 15 | 22.5 | 37.5 | 56.25 | 75 | 92.7 | 95.6 | 96.2 | 96.6 | 96.4 | 96.1 | 96.2 | 91.9 | 95 | 95.6 | 96.3 | 96.1 | 95.8 | 95.9 | 89.2 | 93.3 | 94.1 | 95.2 | 95.1 | 95 | 94.6
PV Powered | PVP75KW-600 [600V] | 75 kW, 600 Vac, 3-phase Utility Interactive Inverter | 75 | 600 | 96 | Y | N |  | 105.8 |  |  | 295 | 341 | 480 | 7.5 | 15 | 22.5 | 37.5 | 56.25 | 75 | 92.3 | 95.5 | 96.2 | 96.5 | 96.5 | 96.2 | 96.24 | 91.5 | 95.1 | 95.9 | 96.3 | 96.3 | 96.1 | 96 | 89.4 | 93.9 | 95 | 95.5 | 95.7 | 95.6 | 95.26
PV Powered | PVP100 kW-208 [208V] | 100 kW, 208 Vac, 3-phase Utility Interactive Inverter with 295-600 Vdc input | 100 | 208 | 95.5 | Y | N |  | 42 |  |  | 295 | 341 | 480 | 10 | 20 | 30 | 50 | 75 | 100 | 94.2 | 96.4 | 96.3 | 96.3 | 95.8 | 95.2 | 95.9 | 93.6 | 96 | 96.1 | 96.1 | 95.7 | 95.1 | 95.7 | 91.7 | 95 | 95.2 | 95.3 | 95.1 | 94.6 | 95
PV Powered | PVP100 kW-480 [480V] | 100 kW, 480 Vac, 3-phase Utility Interactive Inverter with 295-600 Vdc input | 100 | 480 | 96 | Y | N |  | 36 |  |  | 295 | 341 | 480 | 10 | 20 | 30 | 50 | 75 | 100 | 94.4 | 96.6 | 97.1 | 97 | 96.2 | 95.8 | 96.4 | 93.7 | 96.2 | 96.8 | 96.7 | 96 | 95.6 | 96.1 | 91.9 | 95 | 95.9 | 96 | 95.2 | 94.9 | 95.3
PV Powered | PVP100KW-600 [600V] | 100 kW, 600 Vac, 3-phase Utility Interactive Inverter | 100 | 600 | 96 | Y | N |  | 99.56 |  |  | 295 | 341 | 480 | 10 | 20 | 30 | 50 | 75 | 100 | 93.8 | 96.1 | 96.5 | 96.6 | 96.3 | 95.9 | 96.3 | 93.2 | 95.8 | 96.3 | 96.4 | 96.1 | 95.8 | 96.1 | 91.5 | 94.8 | 95.5 | 95.8 | 95.6 | 95.2 | 95.4
PV Powered | PVP250KW-480 [480V] | 250 kW, 480 Vac, 3-phase Utility Interactive Inverter | 249.5 | 480 | 96.5 | Y | N |  | 54.14 |  |  | 295 | 341 | 480 | 24.95 | 49.9 | 74.85 | 124.8 | 187.1 | 249.5 | 96 | 97 | 96.9 | 96.9 | 96.6 | 96.1 | 96.7 | 95.6 | 96.6 | 96.7 | 96.8 | 96.4 | 96 | 96.5 | 94.7 | 95.8 | 96.2 | 96.2 | 95.9 | 95.4 | 95.9
PV Powered | PVP250KW-600 [600V] | 250 kW, 600 Vac, 3-phase Utility Interactive Inverter | 249.5 | 600 | 96.5 | Y | N |  | 101 |  |  | 295 | 341 | 480 | 24.95 | 49.9 | 74.85 | 124.8 | 187.1 | 249.5 | 95.2 | 96.8 | 97.1 | 97.1 | 96.8 | 96.4 | 96.8 | 94.8 | 96.5 | 96.8 | 96.9 | 96.6 | 96.3 | 96.6 | 93.4 | 95.6 | 96.1 | 96.2 | 96 | 95.7 | 95.9
PV Powered | PVP260KW [480V] | 260 kW, 480 Vac, 3-phase Utility Interactive Inverter with 295-600 Vdc input | 260 | 480 | 97 | Y | N |  | 67 |  |  | 295 | 341 | 480 | 26 | 52 | 78 | 130 | 195 | 260 | 96 | 97.5 | 97.7 | 97.6 | 97.1 | 96.4 | 97.2 | 95.6 | 97.3 | 97.5 | 97.4 | 97 | 96.4 | 97 | 94.4 | 96.5 | 96.9 | 97 | 96.6 | 96.1 | 96.6
PV Powered | PVP260KW-LV [480V] | 260 kW, 480 Vac, 3-phase Utility Interactive Inverter with 265-600 Vdc input | 260 | 480 | 96.5 | Y | N |  | 67 |  |  | 265 | 319 | 480 | 26 | 52 | 78 | 130 | 195 | 260 | 96.1 | 97.6 | 97.8 | 97.5 | 96.9 | 96 | 97.1 | 95.6 | 97.3 | 97.5 | 97.3 | 96.7 | 95.9 | 96.9 | 94 | 96.2 | 96.7 | 96.8 | 96.2 | 95.5 | 96.3
REFU Elektronik | REFUsol 24K-UL [480V] | 24 kW, 480 Vac, 1000 Vdc, 3-phase String Inverter | 24 | 480 | 98 | N | N |  | 0.3 |  |  | 570 | 730 | 890 | 2.34 | 4.67 | 7.01 | 11.69 | 17.53 | 23.37 | 97.4 | 97.9 | 98 | 97.9 | 97.7 | 97.6 | 97.8 | 97.5 | 98 | 98.1 | 98.2 | 98.2 | 98.1 | 98.1 | 96.9 | 97.6 | 97.8 | 98 | 97.9 | 97.9 | 97.8 | 2017-04 | 2017-05-31
REFU Elektronik | REFUsol 24K-UL-AFCI [480V] | 24 kW, 480 Vac, 1000 Vdc, 3-phase String Inverter | 24 | 480 | 98 | N | N |  | 0.3 |  |  | 570 | 730 | 890 | 2.34 | 4.67 | 7.01 | 11.69 | 17.53 | 23.37 | 97.3 | 97.8 | 97.9 | 97.9 | 97.7 | 97.6 | 97.8 | 97.4 | 98 | 98.1 | 98.2 | 98.2 | 98.1 | 98.1 | 96.8 | 97.5 | 97.7 | 98 | 97.8 | 97.8 | 97.8 | 2017-04 | 2017-05-31
REFU Elektronik | REFUsol 48K-UL [480V] | 48 kW, 480 Vac, 1000 Vdc, 3-phase String Inverter | 47.888 | 480 | 98 | N | N |  | 0.9 |  |  | 580 | 720 | 850 | 4.79 | 9.58 | 14.37 | 23.94 | 35.92 | 47.89 | 97.1 | 98.1 | 98.2 | 98.2 | 98.2 | 98 | 98.1 | 97.1 | 98.2 | 98.3 | 98.3 | 98.2 | 98.1 | 98.2 | 96.7 | 97.8 | 98 | 98.1 | 98 | 97.9 | 97.9 | 2017-04
REFU Elektronik | REFUsol 48K-UL-AFCI [480V] | 48 kW, 480 Vac, 1000 Vdc, 3-phase String Inverter | 47.888 | 480 | 98 | N | N |  | 0.9 |  |  | 580 | 720 | 850 | 4.79 | 9.58 | 14.37 | 23.94 | 35.92 | 47.89 | 96.7 | 98 | 98.1 | 98.1 | 98.1 | 97.9 | 98 | 96.9 | 98 | 98.2 | 98.3 | 98.3 | 98.1 | 98.2 | 96.9 | 97.9 | 98 | 98.1 | 97.9 | 97.6 | 97.9 | 2017-04
Refusol | 804R012 [480V] | 12 kW, 480 Vac, 3-phase Utility Interactive Inverter | 12.12 | 480 | 97.5 | Y | N |  | 0.87 |  |  | 450 | 720 | 900 | 1.212 | 2.424 | 3.636 | 6.06 | 9.09 | 12.12 | 94.93 | 96.05 | 96.86 | 97.37 | 97.46 | 97.3 | 97.19 | 95.96 | 96.52 | 97.44 | 97.9 | 98.05 | 98.07 | 97.79 | 95.21 | 95.89 | 96.76 | 97.44 | 97.63 | 97.74 | 97.31
Refusol | 804R016 [480V] | 16 kW, 480 Vac, 3-phase Utility Interactive Inverter | 16.1 | 480 | 97.5 | Y | N |  | 0.087 |  |  | 500 | 720 | 900 | 1.61 | 3.22 | 4.83 | 8.05 | 12.08 | 16.1 | 95.95 | 96.84 | 97.38 | 97.62 | 97.59 | 97.41 | 97.46 | 96.59 | 97.26 | 97.74 | 98.02 | 98.07 | 97.97 | 97.91 | 95.93 | 96.54 | 97.19 | 97.63 | 97.73 | 97.72 | 97.51
Refusol | 804R020 [480V] | 20 kW, 480 Vac, 3-phase Utility Interactive Inverter | 19.65 | 480 | 97.5 | Y | N |  | 0.09 |  |  | 550 | 720 | 900 | 1.97 | 3.93 | 5.9 | 9.83 | 14.74 | 19.65 | 96.5 | 97.3 | 97.7 | 97.8 | 97.7 | 97.5 | 97.6 | 96.7 | 97.5 | 97.9 | 98.1 | 98.1 | 98 | 98 | 96 | 96.6 | 97.2 | 97.6 | 97.6 | 97.5 | 97.4
Refusol | 804R024 [480V] | 22.2 kW, 480 Vac, 3-phase Utility Interactive Inverter | 22.23 | 480 | 98 | Y | N |  | 0.49 |  |  | 600 | 720 | 900 | 2.223 | 4.446 | 6.669 | 11.12 | 16.67 | 22.23 | 97.17 | 97.69 | 97.93 | 97.92 | 97.81 | 97.57 | 97.8 | 97.25 | 97.73 | 98.01 | 98.1 | 97.99 | 97.81 | 97.96 | 96.69 | 97.05 | 97.49 | 97.7 | 97.62 | 97.48 | 97.55
Renergy | RS-1500 [208V] | 1.5 kW, 208 Vac Utility Interactive Inverter | 1.55 | 208 | 94.5 | Y | N |  | 0.21 |  |  | 100 | 325 | 360 | 0.155 | 0.31 | 0.465 | 0.775 | 1.163 | 1.55 | 84.46 | 90.49 | 92.52 | 94.25 | 94.92 | 95.02 | 93.86 | 85.04 | 91.04 | 93.19 | 94.79 | 95.41 | 95.53 | 94.38 | 85.31 | 91.19 | 93.54 | 95.02 | 95.55 | 95.76 | 94.58
Renergy | RS-1500 [240V] | 2 kW, 240 Vac Utility Interactive Inverter | 1.55 | 240 | 94.5 | Y | N |  | 0.32 |  |  | 100 | 325 | 360 | 0.155 | 0.31 | 0.465 | 0.775 | 1.163 | 1.55 | 84.62 | 90.46 | 92.57 | 94.42 | 95.07 | 95.25 | 93.99 | 84.89 | 90.97 | 93.04 | 94.81 | 95.51 | 95.73 | 94.42 | 85.22 | 91.38 | 93.44 | 95.12 | 95.65 | 95.93 | 94.66
Renergy | RS-2000 [208V] | 2 kW, 208 Vac Utility Interactive Inverter | 2.06 | 208 | 95.5 | Y | N |  | 0.29 |  |  | 100 | 325 | 360 | 0.206 | 0.412 | 0.618 | 1.03 | 1.545 | 2.06 | 88.28 | 93.12 | 94.41 | 95.27 | 95.43 | 95.37 | 94.87 | 89.63 | 93.68 | 94.91 | 95.73 | 95.84 | 95.8 | 95.34 | 89.74 | 94.01 | 95.11 | 96.13 | 96.38 | 96.07 | 95.77
Renergy | RS-2000 [240V] | 2 kW, 240 Vac Utility Interactive Inverter | 2.06 | 240 | 95 | Y | N |  | 0.36 |  |  | 100 | 325 | 360 | 0.206 | 0.412 | 0.618 | 1.03 | 1.545 | 2.06 | 86.91 | 92.14 | 93.78 | 94.94 | 95.3 | 95.37 | 94.55 | 87.84 | 92.87 | 94.26 | 95.56 | 95.79 | 95.73 | 95.09 | 88.1 | 93.05 | 94.37 | 95.71 | 96 | 95.94 | 95.28
Renergy | RS-3000 [208V] | 3 kW, 208 Vac Utility Interactive Inverter | 3 | 208 | 95.5 | Y | N |  | 0.18 |  |  | 100 | 325 | 360 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 91.57 | 94.41 | 95.16 | 95.47 | 95.31 | 94.62 | 95.1 | 92.05 | 94.92 | 95.58 | 95.89 | 95.76 | 95.37 | 95.56 | 92.22 | 95.17 | 95.79 | 96.25 | 95.93 | 95.8 | 95.78
Renergy | RS-3000 [240V] | 3 kW, 240 Vac Utility Interactive Inverter | 3.01 | 240 | 95.5 | Y | N |  | 0.25 |  |  | 100 | 325 | 360 | 0.301 | 0.602 | 0.903 | 1.505 | 2.258 | 3.01 | 90 | 93.9 | 94.85 | 95.4 | 95.31 | 94.83 | 94.97 | 90.64 | 94.34 | 95.34 | 95.79 | 95.87 | 95.6 | 95.49 | 91 | 94.59 | 95.44 | 95.97 | 96.01 | 95.77 | 95.65
Renergy | RS-4000 [208V] | 4 kW, 208 Vac Utility Interactive Inverter | 3.98 | 208 | 95.5 | Y | N |  | 0.18 |  |  | 100 | 325 | 360 | 0.398 | 0.796 | 1.194 | 1.99 | 2.985 | 3.98 | 90.53 | 94.32 | 95.17 | 95.44 | 95.41 | 95.16 | 95.13 | 91.58 | 94.87 | 95.63 | 96.05 | 96 | 95.45 | 95.7 | 91.82 | 95.03 | 95.8 | 96.45 | 96.31 | 95.76 | 96.01
Renergy | RS-4000 [240V] | 4 kW, 240 Vac Utility Interactive Inverter | 3.99 | 240 | 96 | Y | N |  | 0.25 |  |  | 100 | 325 | 360 | 0.399 | 0.798 | 1.197 | 1.995 | 2.993 | 3.99 | 90.55 | 94.3 | 95.24 | 95.69 | 95.74 | 95.56 | 95.38 | 91.53 | 94.95 | 95.81 | 96.33 | 96.33 | 96.05 | 95.99 | 91.95 | 95.23 | 95.96 | 96.4 | 96.48 | 96.25 | 96.15
Renergy | RS-5000 [240V] | 5000 W, 240 Vac Utility Interactive Inverter | 5.24 | 240 | 95.5 | Y | N |  | 0.2 |  |  | 100 | 380 | 400 | 0.52 | 1.05 | 1.57 | 2.62 | 3.93 | 5.24 | 91.8 | 94.1 | 94.6 | 94.7 | 94.3 | 93.5 | 94.3 | 92.5 | 95.1 | 96.1 | 96.2 | 95.9 | 95.6 | 95.8 | 92.3 | 95.3 | 95.8 | 96.1 | 95.9 | 95.5 | 95.8
Renesola Zhejiang | Replus-250A [240V] | 225 W, 240 Vac Utility Interactive Inverter | 0.22 | 240 | 95 | N | Y |  | 0.17 |  |  | 22 | 28.5 | 44 | 0.02 | 0.04 | 0.07 | 0.11 | 0.16 | 0.22 | 89.6 | 95.5 | 95.3 | 95.7 | 95 | 94.1 | 94.9 | 90.8 | 95.2 | 94.8 | 95.5 | 95.4 | 95 | 95.2 | 85.8 | 91.5 | 93.5 | 94.4 | 95.1 | 95.5 | 94.2
Renesola Zhejiang | Replus-250B [208V] | 217 W, 208 Vac Utility Interactive Inverter | 0.23 | 208 | 95 | N | Y |  | 0.17 |  |  | 22 | 28.5 | 44 | 0.02 | 0.05 | 0.07 | 0.11 | 0.17 | 0.23 | 90.1 | 94.5 | 94.9 | 95.1 | 95.9 | 95.4 | 95.3 | 89.7 | 93.9 | 95.2 | 95.1 | 96.2 | 96.2 | 95.5 | 85.2 | 91.4 | 93.7 | 92.5 | 95.2 | 96.3 | 93.9
Renesola Zhejiang | Replus-300-208A | Utility Interactive Inverter | 0.251 |  | 95.5 | N | Y |  | 0.06 |  |  | 22 | 29 | 38 | 0.025 | 0.05 | 0.075 | 0.125 | 0.188 | 0.251 | 93.3 | 94.8 | 96.1 | 95.2 | 95.5 | 95.3 | 95.4 | 94.1 | 95.7 | 96.2 | 95.6 | 95.7 | 95.6 | 95.7 | 94.2 | 96.1 | 95.9 | 95.8 | 95.5 | 96 | 95.6
Renesola Zhejiang | Replus-300-240A | Utility Interactive Inverter | 0.251 |  | 95.5 | N | Y |  | 0.08 |  |  | 22 | 29 | 38 | 0.025 | 0.05 | 0.075 | 0.125 | 0.188 | 0.251 | 92.2 | 94.1 | 94.9 | 95.2 | 96.1 | 95.7 | 95.5 | 92.9 | 94.7 | 94.5 | 95.7 | 96.1 | 96.3 | 95.7 | 92.7 | 94.6 | 93.2 | 95.7 | 95.4 | 96.4 | 95.1
Renesola Zhejiang | MU300SAP3 [240V] | 289 W, 240 Vac Utility Interactive Inverter | 0.29 | 240 | 96 | N | Y |  | 0.1 |  |  | 26 | 31 | 43 | 0.03 | 0.06 | 0.09 | 0.14 | 0.22 | 0.29 | 92.1 | 94.4 | 95 | 95.7 | 96.3 | 95.9 | 95.7 | 91.6 | 95.1 | 94.8 | 96.5 | 96.5 | 96.5 | 96.1 | 89.9 | 94.3 | 95.3 | 96.3 | 96.2 | 96.2 | 95.8
Renesola Zhejiang | Replus 3600MTLB-US [208V] | 3600W, 208 Vac Utility Interactive Inverter | 3.6 | 208 | 97 | Y | N |  | 0.23 |  |  | 100 | 375 | 450 | 0.36 | 0.72 | 1.08 | 1.8 | 2.7 | 3.6 | 91.9 | 94.6 | 95.5 | 96.4 | 96.5 | 96.3 | 96.1 | 94.5 | 96.7 | 97.3 | 97.6 | 97.4 | 97.2 | 97.3 | 93 | 96 | 96.9 | 97.3 | 97.3 | 97.1 | 97
Renesola Zhejiang | Replus 3600MTLB-US [240V] | 3600W, 240 Vac Utility Interactive Inverter | 3.6 | 240 | 97 | Y | N |  | 0.31 |  |  | 100 | 375 | 450 | 0.36 | 0.72 | 1.08 | 1.8 | 2.7 | 3.6 | 92.4 | 94.6 | 95.5 | 96.5 | 96.7 | 96.7 | 96.2 | 95.3 | 97.1 | 97.5 | 97.8 | 97.7 | 97.5 | 97.6 | 94.2 | 96.5 | 97.1 | 97.5 | 97.6 | 97.4 | 97.3
Renesola Zhejiang | Replus 3600MTLB-US [277V] | 3600W, 277 Vac Utility Interactive Inverter | 3.6 | 277 | 97 | Y | N |  | 0.4 |  |  | 100 | 375 | 450 | 0.36 | 0.72 | 1.08 | 1.8 | 2.7 | 3.6 | 91.2 | 93.9 | 94.7 | 96.1 | 96.6 | 96.6 | 95.9 | 93.4 | 96 | 96.6 | 97.4 | 97.5 | 97.5 | 97.2 | 94.5 | 96.8 | 97.4 | 97.9 | 98 | 97.9 | 97.7
Renesola Zhejiang | Replus 4200MTLB-US [208V] | 4200W, 208 Vac Utility Interactive Inverter | 4.2 | 208 | 97 | Y | N |  | 0.25 |  |  | 100 | 375 | 450 | 0.42 | 0.84 | 1.26 | 2.1 | 3.15 | 4.2 | 91.6 | 94.4 | 95.5 | 96.6 | 96.8 | 96.7 | 96.3 | 94.1 | 96.5 | 97.1 | 97.3 | 97.1 | 96.7 | 97 | 93.6 | 96.2 | 96.8 | 97.2 | 97.5 | 97.1 | 97.1
Renesola Zhejiang | Replus 4200MTLB-US [240V] | 4200W, 240 Vac Utility Interactive Inverter | 4.2 | 240 | 97 | Y | N |  | 0.33 |  |  | 100 | 375 | 450 | 0.42 | 0.84 | 1.26 | 2.1 | 3.15 | 4.2 | 92.4 | 94.6 | 95.5 | 96.5 | 96.7 | 96.7 | 96.2 | 95.3 | 97.1 | 97.5 | 97.8 | 97.7 | 97.5 | 97.6 | 94.2 | 96.5 | 97.1 | 97.5 | 97.6 | 97.4 | 97.3
Renesola Zhejiang | Replus 4200MTLB-US [277V] | 4200 W, 277 Vac Utility Interactive Inverter | 4.2 | 277 | 97 | Y | N |  | 0.4 |  |  | 100 | 375 | 450 | 0.42 | 0.84 | 1.26 | 2.1 | 3.15 | 4.2 | 91.4 | 94.4 | 96 | 96.6 | 96.8 | 96.6 | 96.3 | 92.1 | 95.2 | 96.3 | 97.3 | 97.6 | 97.1 | 97 | 93.6 | 96.3 | 97.2 | 97.6 | 97.6 | 97.6 | 97.4
Renesola Zhejiang | Replus 5000MTLB-US [208V] | 4600 W, 208 Vac Utility Interactive Inverter | 4.6 | 208 | 97 | Y | N |  | 0.26 |  |  | 100 | 375 | 450 | 0.46 | 0.92 | 1.38 | 2.3 | 3.45 | 4.6 | 94.7 | 96.5 | 96.8 | 96.9 | 96.5 | 96 | 96.5 | 95.4 | 97 | 97.3 | 97.4 | 97 | 96.5 | 97 | 94.3 | 96.4 | 96.9 | 97.1 | 97 | 96.5 | 96.8
Renesola Zhejiang | Replus 5000MTLB-US [240V] | 4600 W, 240 Vac Utility Interactive Inverter | 4.6 | 240 | 97 | Y | N |  | 0.36 |  |  | 100 | 375 | 450 | 0.46 | 0.92 | 1.38 | 2.3 | 3.45 | 4.6 | 92.8 | 95.2 | 96 | 96.7 | 96.6 | 96.4 | 96.3 | 95.8 | 97.3 | 97.7 | 97.8 | 97.5 | 97.1 | 97.5 | 96.7 | 96.7 | 97.2 | 97.5 | 97.4 | 97.1 | 97.3
Renesola Zhejiang | Replus 5000MTLB-US [277V] | 4600 W, 277 Vac Utility Interactive Inverter | 4.6 | 277 | 97 | Y | N |  | 0.43 |  |  | 100 | 375 | 450 | 0.46 | 0.92 | 1.38 | 2.3 | 3.45 | 4.6 | 92.2 | 94.9 | 95.6 | 96.6 | 96.8 | 96.8 | 96.4 | 94.6 | 96.7 | 97.2 | 97.6 | 97.6 | 97.4 | 97.4 | 95.4 | 97.1 | 97.6 | 97.9 | 97.8 | 97.7 | 97.7
Renesola Zhejiang | Replus 8000TLB-US [208V] | 8000 W Utility Interactive Inverter | 8.07 | 208 | 96.5 | Y | N |  | 0.05 |  |  | 100 | 345 | 480 | 0.81 | 1.61 | 2.42 | 4.03 | 6.05 | 8.07 | 95.6 | 96.7 | 97.1 | 97.2 | 97.1 | 96.9 | 97.1 | 94.9 | 96.3 | 96.8 | 97 | 96.9 | 96.8 | 96.8 | 92.6 | 95 | 95.8 | 96.4 | 96.4 | 96.2 | 96.1
Renesola Zhejiang | Replus 8000TLB-US [240V] | 8000 W Utility Interactive Inverter | 8.08 | 240 | 97 | Y | N |  | 0.08 |  |  | 100 | 380 | 480 | 0.81 | 1.62 | 2.42 | 4.04 | 6.06 | 8.08 | 95.4 | 96.7 | 97.1 | 97.4 | 97.4 | 97.2 | 97.2 | 95.1 | 96.6 | 97 | 97.3 | 97.3 | 97.2 | 97.1 | 93.2 | 95.5 | 96.2 | 96.8 | 96.4 | 96.9 | 96.3
Renesola Zhejiang | Replus 9000TLB-US [208V] | 9000 W Utility Interactive Inverter | 9.08 | 208 | 96.5 | Y | N |  | 0.05 |  |  | 100 | 345 | 480 | 0.91 | 1.82 | 2.72 | 4.54 | 6.81 | 9.08 | 95.9 | 96.8 | 97.1 | 97.2 | 97 | 96.8 | 97 | 95.3 | 96.5 | 96.9 | 97 | 97 | 96.7 | 96.9 | 93.1 | 95.3 | 96 | 96.4 | 96.4 | 96.2 | 96.2
Renesola Zhejiang | Replus 9000TLB-US [240V] | 9000 W Utility Interactive Inverter | 9.08 | 240 | 96.5 | Y | N |  | 0.08 |  |  | 100 | 380 | 480 | 0.91 | 1.82 | 2.72 | 4.54 | 6.81 | 9.08 | 95.8 | 79.3 | 97.2 | 97.4 | 97.4 | 97.2 | 96.4 | 95.5 | 96.8 | 97.1 | 97.3 | 97.3 | 97.1 | 97.2 | 93.8 | 95.8 | 96.4 | 96.7 | 96.9 | 96.8 | 96.6
Renesola Zhejiang | Replus 10000TLB-US [208V] | 10000 W Utility Interactive Inverter | 10.09 | 208 | 96.5 | Y | N |  | 0.05 |  |  | 100 | 345 | 480 | 1.01 | 2.02 | 3.03 | 5.04 | 7.57 | 10.09 | 95.8 | 96.9 | 97.1 | 97.2 | 97 | 96.6 | 97 | 95.5 | 96.6 | 96.9 | 97 | 96.9 | 96.5 | 96.8 | 93.1 | 95.4 | 96.1 | 96.4 | 96.3 | 96 | 96.1
Renesola Zhejiang | Replus 10000TLB-US [240V] | 10000 W Utility Interactive Inverter | 10.09 | 240 | 97 | Y | N |  | 0.08 |  |  | 100 | 380 | 480 | 1.01 | 2.02 | 3.03 | 5.04 | 7.56 | 10.09 | 96 | 97 | 97.3 | 97.4 | 97.3 | 97.1 | 97.2 | 95.8 | 96.9 | 97.2 | 97.4 | 97.3 | 97 | 97.2 | 94.3 | 96 | 96.5 | 96.9 | 96.8 | 96.7 | 96.7
Renesola Zhejiang | Replus 10000TL3B-US [277V] | 10000 W, 277 Vac Utility Interactive Inverter | 10.1 | 277 | 95.5 | Y | N |  | 0.01 |  |  | 100 | 420 | 480 | 1.01 | 2.02 | 3.03 | 5.05 | 7.58 | 10.1 | 89.5 | 93.1 | 94.1 | 94.9 | 95 | 95 | 94.6 | 90.1 | 93.9 | 95.2 | 96 | 96.3 | 96.4 | 95.7 | 89.9 | 94.2 | 95.4 | 96.3 | 96.7 | 96.8 | 96
Renesola Zhejiang | Replus 12000TL3B-US [277V] | 11620W, 277 Vac Utility Interactive Inverter | 11.62 | 277 | 95.5 | Y | N |  | 0.01 |  |  | 250 | 420 | 480 | 1.16 | 2.32 | 3.49 | 5.81 | 8.72 | 11.62 | 89.8 | 93.4 | 94.4 | 95.2 | 94.9 | 95 | 94.6 | 90.2 | 94.2 | 95.3 | 96.2 | 96.4 | 96.5 | 95.9 | 91 | 94.6 | 95.6 | 96.4 | 96.6 | 96.7 | 96.1
Renesola Zhejiang | Replus 11000TLB-US [240V] | 11000 W Utility Interactive Inverter | 11.7 | 240 | 97 | Y | N |  | 0.08 |  |  | 356 | 380 | 480 | 1.17 | 2.34 | 3.51 | 5.85 | 8.78 | 11.7 | 96 | 97 | 97.3 | 97.3 | 97.2 | 97 | 97.2 | 95.8 | 96.9 | 97.2 | 97.3 | 97.2 | 96.9 | 97.1 | 94.3 | 96 | 96.5 | 97 | 96.8 | 96.5 | 96.6
Renesola Zhejiang | Replus 18000TL3B-US [277V] | 18306 W, 277 Vac Utility Interactive Inverter | 18.31 | 277 | 96 | Y | N |  | 0.01 |  |  | 250 | 420 | 480 | 1.83 | 3.66 | 5.49 | 9.15 | 13.73 | 18.31 | 92.3 | 94.9 | 95.4 | 95.2 | 95.5 | 95.4 | 95.3 | 92.5 | 95.8 | 96.4 | 96.8 | 96.9 | 96.6 | 96.6 | 92.9 | 95.8 | 96.5 | 96.9 | 97.1 | 96.8 | 96.7
Renesola Zhejiang | Replus 20000TL3B-US [277V] | 20415 W, 277 Vac Utility Interactive Inverter | 20.42 | 277 | 96.5 | Y | N |  | 0.2 |  |  | 250 | 420 | 480 | 2.04 | 4.08 | 6.12 | 10.21 | 15.31 | 20.42 | 92.7 | 95.1 | 95.5 | 95.6 | 95.7 | 95.7 | 95.5 | 93.1 | 96 | 96.5 | 96.8 | 96.8 | 96.8 | 96.6 | 93.5 | 96 | 96.6 | 97 | 97.1 | 97 | 96.8
Renovo Power Systems | RN3000US | 3 kW Digiwatts Grid-tie transformerless MPPT Inverter | 3 |  | 96.5 | Y | N |  | 0.05 |  |  | 100 | 380 | 440 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 93 | 95.5 | 96.2 | 96.3 | 95.9 | 95.1 | 95.8 | 94.4 | 96.5 | 97.1 | 97.2 | 97.2 | 96.9 | 97 | 93.5 | 96.1 | 96.9 | 97 | 97.1 | 96.9 | 96.8
Renovo Power Systems | RN5000US | 5 kW Digiwatts Grid-tie transformerless MPPT Inverter | 5 |  | 94.5 | Y | N |  | 1.3 |  |  | 100 | 345 | 440 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 89.9 | 92.8 | 94.1 | 94.5 | 94.3 | 93.9 | 94.1 | 91.1 | 92.8 | 94.3 | 94.9 | 94.8 | 94.4 | 94.5 | 89.9 | 93.9 | 94.7 | 95.2 | 95.1 | 94.7 | 94.8
Resonix | EVSK1750WG [208V] | 1.5 kW, 208 Vac Utility Interactive Inverter | 1.55 | 208 | 94.5 | Y | N |  | 0.21 |  |  | 100 | 325 | 360 | 0.155 | 0.31 | 0.465 | 0.775 | 1.163 | 1.55 | 84.46 | 90.49 | 92.52 | 94.25 | 94.92 | 95.02 | 93.86 | 85.04 | 91.04 | 93.19 | 94.79 | 95.41 | 95.53 | 94.38 | 85.31 | 91.19 | 93.54 | 95.02 | 95.55 | 95.76 | 94.58
Resonix | EVSK1750WG [240V] | 2 kW, 240 Vac Utility Interactive Inverter | 1.55 | 240 | 94.5 | Y | N |  | 0.32 |  |  | 100 | 325 | 360 | 0.155 | 0.31 | 0.465 | 0.775 | 1.163 | 1.55 | 84.62 | 90.46 | 92.57 | 94.42 | 95.07 | 95.25 | 93.99 | 84.89 | 90.97 | 93.04 | 94.81 | 95.51 | 95.73 | 94.42 | 85.22 | 91.38 | 93.44 | 95.12 | 95.65 | 95.93 | 94.66
Resonix | EVSK2340WG [208V] | 2 kW, 208 Vac Utility Interactive Inverter | 2.06 | 208 | 95.5 | Y | N |  | 0.29 |  |  | 100 | 325 | 360 | 0.206 | 0.412 | 0.618 | 1.03 | 1.545 | 2.06 | 88.28 | 93.12 | 94.41 | 95.27 | 95.43 | 95.37 | 94.87 | 89.63 | 93.68 | 94.91 | 95.73 | 95.84 | 95.8 | 95.34 | 89.74 | 94.01 | 95.11 | 96.13 | 96.38 | 96.07 | 95.77
Resonix | EVSK2340WG [240V] | 3 kW, 240 Vac Utility Interactive Inverter | 2.06 | 240 | 95 | Y | N |  | 0.36 |  |  | 100 | 325 | 360 | 0.206 | 0.412 | 0.618 | 1.03 | 1.545 | 2.06 | 86.91 | 92.14 | 93.78 | 94.94 | 95.3 | 95.37 | 94.55 | 87.84 | 92.87 | 94.26 | 95.56 | 95.79 | 95.73 | 95.09 | 88.1 | 93.05 | 94.37 | 95.71 | 96 | 95.94 | 95.28
Resonix | EVSK3510WG [208V] | 3 kW, 208 Vac Utility Interactive Inverter | 3 | 208 | 95.5 | Y | N |  | 0.18 |  |  | 100 | 325 | 360 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 91.57 | 94.41 | 95.16 | 95.47 | 95.31 | 94.62 | 95.1 | 92.05 | 94.92 | 95.58 | 95.89 | 95.76 | 95.37 | 95.56 | 92.22 | 95.17 | 95.79 | 96.25 | 95.93 | 95.8 | 95.78
Resonix | EVSK3510WG [240V] | 3 kW, 240 Vac Utility Interactive Inverter | 3.01 | 240 | 95.5 | Y | N |  | 0.25 |  |  | 100 | 325 | 360 | 0.301 | 0.602 | 0.903 | 1.505 | 2.258 | 3.01 | 90 | 93.9 | 94.85 | 95.4 | 95.31 | 94.83 | 94.97 | 90.64 | 94.34 | 95.34 | 95.79 | 95.87 | 95.6 | 95.49 | 91 | 94.59 | 95.44 | 95.97 | 96.01 | 95.77 | 95.65
Resonix | EVSK4700WG [208V] | 4 kW, 208 Vac Utility Interactive Inverter | 3.98 | 208 | 95.5 | Y | N |  | 0.18 |  |  | 100 | 325 | 360 | 0.398 | 0.796 | 1.194 | 1.99 | 2.985 | 3.98 | 90.53 | 94.32 | 95.17 | 95.44 | 95.41 | 95.16 | 95.13 | 91.58 | 94.87 | 95.63 | 96.05 | 96 | 95.45 | 95.7 | 91.82 | 95.03 | 95.8 | 96.45 | 96.31 | 95.76 | 96.01
Resonix | EVSK4700WG [240V] | 4 kW, 240 Vac Utility Interactive Inverter | 3.99 | 240 | 96 | Y | N |  | 0.25 |  |  | 100 | 325 | 360 | 0.399 | 0.798 | 1.197 | 1.995 | 2.993 | 3.99 | 90.55 | 94.3 | 95.24 | 95.69 | 95.74 | 95.56 | 95.38 | 91.53 | 94.95 | 95.81 | 96.33 | 96.33 | 96.05 | 95.99 | 91.95 | 95.23 | 95.96 | 96.4 | 96.48 | 96.25 | 96.15
Rhombus Energy Solutions | BESI-50kW-480 [480V] | 50kW, 480 Vac, transformer-less, 3-phase, Multi-Mode Utility Interactive Energy Storage Inverter | 49.35 | 480 | 94 | N | N |  | 103 |  |  | 550 | 636 | 840 | 4.935 | 9.87 | 14.805 | 24.675 | 37.0125 | 49.35 | 76.5714 | 88 | 92 | 95.1429 | 96 | 96 | 94.1629 | 79 | 89 | 92 | 95 | 96 | 96 | 94.28 | 79 | 88.8571 | 92 | 94 | 96 | 96 | 94.0629 | 2018-08-15 | 2018-10-15
Rhombus Energy Solutions | BESS-50kW-480 [480V] | 50kW, 480 Vac, transformer-less, 3-phase, Utility Interactive Energy Storage Inverter | 49.35 | 480 | 94 | N | N |  | 103 |  |  | 550 | 636 | 840 | 4.935 | 9.87 | 14.805 | 24.675 | 37.0125 | 49.35 | 76.5714 | 88 | 92 | 95.1429 | 96 | 96 | 94.1629 | 79 | 89 | 92 | 95 | 96 | 96 | 94.28 | 79 | 88.8571 | 92 | 94 | 96 | 96 | 94.0629 | 2018-08-15 | 2018-10-15
Ritek | RTMU300SAP2 [240V] | 289 W, 240 Vac Utility Interactive Inverter | 0.289 | 240 | 96 | N | Y |  | 0.1 |  |  | 26 | 31 | 43 | 0.03 | 0.06 | 0.09 | 0.14 | 0.22 | 0.29 | 92.1 | 94.4 | 95 | 95.7 | 96.3 | 95.9 | 95.7 | 91.6 | 95.1 | 94.8 | 96.5 | 96.5 | 96.5 | 96.1 | 89.9 | 94.3 | 95.3 | 96.3 | 96.2 | 96.2 | 95.8
Sainty Solar | SSI-2K2U [240V] | 2110 W, 240 Vac Utility Interactive Inverter | 2.11 | 240 | 94.5 | Y | N |  | 0.25 |  |  | 100 | 375 | 400 | 0.21 | 0.42 | 0.63 | 1.06 | 1.58 | 2.11 | 85.3 | 91.6 | 92.9 | 94.3 | 94.6 | 94.5 | 93.8 | 82.1 | 91.9 | 94.2 | 95.6 | 96.1 | 96.4 | 95 | 82.2 | 91.5 | 93.8 | 95.6 | 96.1 | 96.3 | 95
Sainty Solar | SSI-3K3U [240V] | 3180 W, 240 Vac Utility Interactive Inverter | 3.18 | 240 | 95 | Y | N |  | 0.25 |  |  | 100 | 375 | 400 | 0.32 | 0.64 | 0.95 | 1.59 | 2.39 | 3.18 | 88.8 | 92.9 | 94.1 | 94.6 | 94.3 | 94 | 94 | 88.8 | 94.4 | 95.3 | 96.2 | 96.3 | 95.9 | 95.7 | 89.5 | 93.7 | 95.3 | 96.2 | 96.3 | 96.1 | 95.7
Sainty Solar | SSI-4K4U [240V] | 4100W, 240 Vac Utility Interactive Inverter | 4.16 | 240 | 95.5 | Y | N |  | 0.2 |  |  | 100 | 380 | 400 | 0.42 | 0.83 | 1.25 | 2.08 | 3.12 | 4.16 | 90.6 | 93.8 | 94.5 | 94.8 | 94.6 | 94.2 | 94.4 | 91.4 | 95 | 95.7 | 96.1 | 96.2 | 95.9 | 95.9 | 90.7 | 94.7 | 95.5 | 96.1 | 96.1 | 95.9 | 95.7
Sainty Solar | SSI-5K5U [240V] | 5000 W, 240 Vac Utility Interactive Inverter | 5.24 | 240 | 95.5 | Y | N |  | 0.2 |  |  | 100 | 380 | 400 | 0.52 | 1.05 | 1.57 | 2.62 | 3.93 | 5.24 | 91.8 | 94.1 | 94.6 | 94.7 | 94.3 | 93.5 | 94.3 | 92.5 | 95.1 | 96.1 | 96.2 | 95.9 | 95.6 | 95.8 | 92.3 | 95.3 | 95.8 | 96.1 | 95.9 | 95.5 | 95.8
Samil Power | SolarPond 240HF-US [208V] | 235W, 208 Vac Utility Interactive Inverter | 0.235 | 208 | 95.5 | N | Y |  | 0.08 |  |  | 27 | 34 | 40 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 91.1 | 94.3 | 95.2 | 95.5 | 95.8 | 95.5 | 95.4 | 89.8 | 94.1 | 95 | 95.6 | 95.8 | 95.9 | 95.4 | 89.2 | 93.4 | 94.9 | 95.7 | 95.8 | 95.7 | 95.3
Samil Power | SolarPond 240HF-US [240V] | 237W, 240 Vac Utility Interactive Inverter | 0.238 | 240 | 95 | N | Y |  | 0.08 |  |  | 27 | 34 | 40 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.4 | 93.4 | 94.6 | 95.1 | 95.6 | 95.6 | 95 | 89 | 93 | 94.4 | 95.3 | 95.6 | 95.8 | 95 | 88.5 | 92.7 | 94.1 | 95.6 | 95.6 | 95.7 | 95
Samil Power | SolarRiver3000TL-US [208V] | 3 kW, 208 Vac Utility Interactive Inverter | 3 | 208 | 96.5 | Y | N |  | 0.22 | 3 | 0.22 | 100 | 400 | 500 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 93.8 | 96 | 96.6 | 96.6 | 96.2 | 95.7 | 96.19 | 94 | 96.3 | 96.8 | 97 | 97.1 | 96.8 | 96.89 | 93.3 | 96.1 | 96.8 | 96.9 | 97 | 96.9 | 96.74
Samil Power | SolarRiver3000TL-US [240V] | 3 kW, 240 Vac Utility Interactive Inverter | 3 | 240 | 97 | Y | N |  | 0.67 | 3 | 0.67 | 100 | 400 | 500 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 93.3 | 95.8 | 96.6 | 96.8 | 96.7 | 96.4 | 96.51 | 94.2 | 96.6 | 97.2 | 97.3 | 97.5 | 97.1 | 97.24 | 93.7 | 96.2 | 96.8 | 97.1 | 97.2 | 97.3 | 96.97
Samil Power | SolarRiver4000TL-US [208V] | 4 kW, 208 Vac Utility Interactive Inverter | 4 | 208 | 97 | Y | N |  | 0.21 | 4 | 0.21 | 100 | 400 | 500 | 0.4 | 0.8 | 1.2 | 2 | 3 | 4 | 94.4 | 96.2 | 96.5 | 97 | 96.4 | 96 | 96.44 | 95.1 | 96.7 | 97.2 | 97.3 | 97.2 | 96.9 | 97.1 | 94.7 | 96.2 | 96.7 | 97 | 96.9 | 96.7 | 96.79
Samil Power | SolarRiver4000TL-US [240V] | 4 kW, 240 Vac Utility Interactive Inverter | 4 | 240 | 97 | Y | N |  | 0.64 | 4 | 0.64 | 100 | 400 | 500 | 0.4 | 0.8 | 1.2 | 2 | 3 | 4 | 94.1 | 95.9 | 96.6 | 97 | 96.8 | 96.6 | 96.65 | 95.2 | 96.8 | 97.3 | 97.7 | 97.6 | 97.3 | 97.44 | 94.4 | 96.5 | 97.3 | 97.5 | 97.4 | 97.3 | 97.24
Samil Power | SolarRiver5000TL-US [208V] | 5 kW, 208 Vac Utility Interactive Inverter | 5 | 208 | 97 | Y | N |  | 0.31 | 5 | 0.31 | 100 | 400 | 500 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 94.5 | 96.5 | 96.9 | 97.1 | 96.9 | 96.4 | 96.82 | 94.9 | 96.8 | 97.5 | 97.4 | 97.4 | 97.2 | 97.29 | 95.4 | 97 | 97.8 | 97.8 | 97.7 | 97.2 | 97.57
Samil Power | SolarRiver5000TL-US [240V] | 5 kW, 240 Vac Utility Interactive Inverter | 5 | 240 | 97 | Y | N |  | 0.24 | 5 | 0.24 | 100 | 400 | 500 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 94.5 | 96.5 | 96.9 | 97.1 | 96.9 | 96.4 | 96.82 | 94.9 | 96.8 | 97.5 | 97.4 | 97.4 | 97.2 | 97.29 | 95.4 | 97 | 97.8 | 97.8 | 97.7 | 97.2 | 97.57
Samil Power | SolarRiver6000TL-US [208V] | 6 kW, 208 Vac Utility Interactive Inverter | 6 | 208 | 97 | Y | N |  | 0.32 | 6 | 0.32 | 100 | 400 | 500 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 94.5 | 96.5 | 96.9 | 97.1 | 96.9 | 96.4 | 96.82 | 94.9 | 96.8 | 97.5 | 97.4 | 97.4 | 97.2 | 97.29 | 95.4 | 97 | 97.8 | 97.8 | 97.7 | 97.2 | 97.57
Samil Power | SolarRiver6000TL-US [240V] | 6 kW, 240 Vac Utility Interactive Inverter | 6 | 240 | 97 | Y | N |  | 0.68 | 6 | 0.68 | 100 | 400 | 500 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 94.5 | 96.5 | 96.9 | 97.1 | 96.9 | 96.4 | 96.82 | 94.9 | 96.8 | 97.5 | 97.4 | 97.4 | 97.2 | 97.29 | 95.4 | 97 | 97.8 | 97.8 | 97.7 | 97.2 | 97.57
Samil Power | SolarRiver6000TL-US [277V] | 6 kW, 277 Vac Utility Interactive Inverter | 6 | 277 | 97 | Y | N |  | 0.85 | 6 | 0.85 | 100 | 400 | 500 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 94.5 | 96.5 | 96.9 | 97.1 | 96.9 | 96.4 | 96.82 | 94.9 | 96.8 | 97.5 | 97.4 | 97.4 | 97.2 | 97.29 | 95.4 | 97 | 97.8 | 97.8 | 97.7 | 97.2 | 97.57
Samil Power | SolarRiver7000TL-US [208V] | 7 kW, 208 Vac Utility Interactive Inverter | 7 | 208 | 97 | Y | N |  | 0.27 |  |  | 100 | 400 | 480 | 0.7 | 1.4 | 2.1 | 3.5 | 5.25 | 7 | 93.5 | 96 | 96.7 | 97 | 96.9 | 96.6 | 96.7 | 94.4 | 96.6 | 97.2 | 97.5 | 97.3 | 97 | 97.1 | 93.3 | 96 | 96.6 | 97.1 | 97.2 | 96.9 | 96.9
Samil Power | SolarRiver7000TL-US [240V] | 7 kW, 240 Vac Utility Interactive Inverter | 7 | 240 | 97.5 | Y | N |  | 0.39 |  |  | 100 | 400 | 480 | 0.7 | 1.4 | 2.1 | 3.5 | 5.25 | 7 | 92.7 | 95.8 | 96.6 | 97 | 97.1 | 96.8 | 96.8 | 95.3 | 97.3 | 97.8 | 98 | 97.9 | 97.7 | 97.7 | 94.6 | 96.9 | 97.5 | 97.8 | 97.8 | 97.6 | 97.6
Samil Power | SolarRiver7000TL-US [277V] | 7 kW, 277 Vac Utility Interactive Inverter | 7 | 277 | 97 | Y | N |  | 0.45 |  |  | 100 | 400 | 480 | 0.7 | 1.4 | 2.1 | 3.5 | 5.25 | 7 | 91.2 | 94.7 | 95.9 | 96.8 | 97 | 96.9 | 96.5 | 93.5 | 96.4 | 97.1 | 97.7 | 97.7 | 97.7 | 97.4 | 94.9 | 97.1 | 97.6 | 98.1 | 98.1 | 98 | 97.8
Samil Power | SolarRiver8000TL-US [208V] | 8kW, 208 Vac Utility Interactive Inverter | 8 | 208 | 97 | Y | N |  | 0.43 |  |  | 100 | 400 | 480 | 0.8 | 1.6 | 2.4 | 4 | 6 | 8 | 93.8 | 96.2 | 96.8 | 97 | 96.9 | 96.4 | 96.7 | 94.5 | 96.4 | 97.2 | 97.5 | 97.3 | 96.9 | 97.1 | 93.7 | 96.2 | 96.9 | 97.2 | 97.1 | 96.7 | 96.9
Samil Power | SolarRiver8000TL-US [240V] | 8kW, 240 Vac Utility Interactive Inverter | 8 | 240 | 97.5 | Y | N |  | 0.47 |  |  | 100 | 400 | 480 | 0.8 | 1.6 | 2.4 | 4 | 6 | 8 | 93 | 96 | 96.7 | 97.1 | 96.9 | 96.7 | 96.7 | 95.7 | 97.4 | 97.8 | 97.9 | 97.8 | 97.5 | 97.7 | 95 | 97.1 | 97.5 | 97.8 | 97.7 | 97.4 | 97.5
Samil Power | SolarRiver8000TL-US [277V] | 8kW, 277 Vac Utility Interactive Inverter | 8 | 277 | 97 | Y | N |  | 0.28 |  |  | 100 | 400 | 480 | 0.8 | 1.6 | 2.4 | 4 | 6 | 8 | 91 | 94.6 | 96 | 96.8 | 97 | 96.9 | 96.5 | 93.5 | 95.8 | 96.8 | 97.5 | 97.6 | 97.5 | 97.2 | 94.5 | 96.5 | 97.3 | 97.7 | 98 | 97.8 | 97.6
Samil Power | SolarRiver9000TL-US [208V] | 9 kW, 208 Vac Utility Interactive Inverter | 9 | 208 | 97 | Y | N |  | 0.43 |  |  | 100 | 400 | 480 | 0.9 | 1.8 | 2.7 | 4.5 | 6.75 | 9 | 95 | 96.8 | 97.2 | 97.2 | 96.9 | 96.4 | 96.9 | 95.4 | 97 | 97.3 | 97.3 | 97.2 | 96.8 | 97.1 | 94.7 | 96.5 | 97.1 | 97.3 | 97.1 | 96.7 | 97
Samil Power | SolarRiver9000TL-US [240V] | 9 kW, 240 Vac Utility Interactive Inverter | 9 | 240 | 97.5 | Y | N |  | 0.4 |  |  | 100 | 400 | 480 | 0.9 | 1.8 | 2.7 | 4.5 | 6.75 | 9 | 94.1 | 96.8 | 97.2 | 97.4 | 97.4 | 97 | 97.2 | 96 | 97.5 | 97.6 | 98.1 | 97.8 | 97.5 | 97.7 | 95.1 | 96.9 | 97.4 | 97.7 | 97.7 | 97.5 | 97.5
Samil Power | SolarRiver9000TL-US [277V] | 9 kW, 277 Vac Utility Interactive Inverter | 9 | 277 | 97.5 | Y | N |  | 0.52 |  |  | 100 | 400 | 480 | 0.9 | 1.8 | 2.7 | 4.5 | 6.75 | 9 | 92.5 | 95.5 | 96.6 | 97.2 | 97.2 | 97.1 | 96.9 | 93.9 | 96.6 | 97.2 | 97.6 | 97.6 | 97.5 | 97.4 | 95.1 | 97 | 97.7 | 97.9 | 97.8 | 97.7 | 97.7
Samil Power | SolarRiver10000TL-US [208V] | 10 kW, 208 Vac Utility Interactive Inverter | 10 | 208 | 97 | Y | N |  | 0.44 |  |  | 100 | 400 | 480 | 1 | 2 | 3 | 5 | 7.5 | 10 | 95.3 | 96.9 | 97.3 | 97.1 | 96.8 | 96.3 | 96.8 | 95 | 97 | 97.4 | 97.4 | 97.1 | 96.6 | 97.1 | 94.2 | 96.6 | 97.1 | 97.2 | 96.9 | 96.6 | 96.9
Samil Power | SolarRiver10000TL-US [240V] | 10 kW, 240 Vac Utility Interactive Inverter | 10 | 240 | 97.5 | Y | N |  | 0.38 |  |  | 100 | 400 | 480 | 1 | 2 | 3 | 5 | 7.5 | 10 | 94.7 | 96.9 | 97.3 | 97.6 | 97.3 | 97 | 97.2 | 95.8 | 97.5 | 98.1 | 98 | 97.8 | 97.5 | 97.8 | 95.4 | 97.1 | 97.4 | 97.7 | 97.6 | 97.4 | 97.5
Samil Power | SolarRiver10000TL-US [277V] | 10 kW, 277 Vac Utility Interactive Inverter | 10 | 277 | 97.5 | Y | N |  | 0.44 |  |  | 100 | 400 | 480 | 1 | 2 | 3 | 5 | 7.5 | 10 | 93.2 | 96 | 96.7 | 97.2 | 97.3 | 97.1 | 97 | 94.3 | 96.5 | 97.4 | 97.7 | 97.5 | 97.4 | 97.4 | 95.4 | 97.2 | 97.6 | 97.9 | 97.9 | 97.6 | 97.7
SanRex | PV-100K-48T-13 | 100 kW Utility Interactive Inverter | 99.68 |  | 94.5 | Y | N |  | 90.92 |  |  | 300 | 400 | 520 | 9.97 | 19.94 | 29.9 | 49.84 | 74.76 | 99.68 | 88.3 | 93.1 | 94.6 | 95.8 | 96.2 | 96.2 | 95.4 | 86.6 | 91.8 | 93.6 | 94.9 | 95.4 | 95.4 | 94.5 | 84.6 | 90.6 | 92.6 | 94.1 | 94.6 | 94.7 | 93.7
SanRex | PV-250K-48T-13 | 250 kW Utility Interactive Inverter | 251.4 |  | 95 | Y | N |  | 20.5 |  |  | 300 | 400 | 520 | 25.14 | 50.28 | 75.42 | 125.7 | 188.6 | 251.4 | 91.9 | 94.8 | 95.7 | 96.1 | 96 | 95.6 | 95.7 | 90 | 93.5 | 94.7 | 95.3 | 95.2 | 94.8 | 94.9 | 88 | 92.3 | 93.7 | 94.5 | 94.6 | 94.2 | 94.1
SanRex | PV-500K-48T-13 | 500 kW Utility Interactive Inverter | 501.4 |  | 95.5 | N | N |  | 46.27 |  |  | 300 | 400 | 520 | 50.14 | 100.3 | 150.4 | 250.7 | 376.1 | 501.4 | 92.1 | 95.2 | 96 | 96.5 | 96.4 | 96.2 | 96.1 | 90.6 | 94.2 | 95.2 | 95.8 | 95.7 | 95.3 | 95.4 | 88.2 | 93.3 | 94.3 | 95.1 | 95.2 | 94.8 | 94.7
SANYO ELECTRIC CO LTD OF PANASONIC GROUP | VBHN325SA17E [240V] | 325 W, 96 cell heterojunction monocrystalline ACPV module, white backsheet. DC Module: VBHN325SA17. Micro-inverter: IQ7X-96-x-ACM-US [240V]. | 0.315 | 240 | 97.5 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. |  |  |  | 53 | 60 | 64 | 0.0315 | 0.063 | 0.0945 | 0.1575 | 0.23625 | 0.315 | 95.7348 | 96.8402 | 96.9962 | 97.7627 | 97.7558 | 97.4686 | 97.5251 | 95.6103 | 96.6782 | 96.7549 | 97.6667 | 97.7392 | 97.5137 | 97.4564 | 95.4365 | 96.4979 | 96.6571 | 97.6038 | 97.7001 | 97.4825 | 97.3932 | 2019-04-02
SANYO ELECTRIC CO LTD OF PANASONIC GROUP | VBHN330SA17E [240V] | 330 W, 96 cell heterojunction monocrystalline ACPV module, white backsheet. DC Module: VBHN330SA17. Micro-inverter: IQ7X-96-x-ACM-US [240V]. | 0.315 | 240 | 97.5 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. |  |  |  | 53 | 60 | 64 | 0.0315 | 0.063 | 0.0945 | 0.1575 | 0.23625 | 0.315 | 95.7348 | 96.8402 | 96.9962 | 97.7627 | 97.7558 | 97.4686 | 97.5251 | 95.6103 | 96.6782 | 96.7549 | 97.6667 | 97.7392 | 97.5137 | 97.4564 | 95.4365 | 96.4979 | 96.6571 | 97.6038 | 97.7001 | 97.4825 | 97.3932 | 2019-04-02
Satcon Technology | AE-30-60-PV-A [480V] | 30 kW, 480 Vac, 3-phase Utility Interactive Inverter | 30 | 480 | 93 | Y | N |  | 59 |  |  | 330 | 410 | 480 | 3 | 6 | 9 | 15 | 22.5 | 30 | 82.9 | 89.8 | 92 | 93.5 | 94.2 | 94.3 | 93.1 | 83.5 | 89.7 | 91.9 | 93.5 | 93.9 | 93.8 | 93 | 81 | 88.6 | 91 | 93 | 93.5 | 93.6 | 92.3
Satcon Technology | AE-30-60-PV-D [208V] | 30 kW, 208 Vac, 3-phase Utility Interactive Inverter | 30 | 208 | 92.5 | Y | N |  | 54 |  |  | 330 | 410 | 480 | 3 | 6 | 9 | 15 | 22.5 | 30 | 82.1 | 89.2 | 91.4 | 93.1 | 93.4 | 93.2 | 92.5 | 81.5 | 88.7 | 91.2 | 92.8 | 93.2 | 93 | 92.1 | 85.2 | 90.5 | 92.5 | 93.5 | 93.8 | 93.5 | 93.1
Satcon Technology | AE-30-60-PV-E [240V] | 30 kW, 240 Vac, 1-phase Utility Interactive Inverter | 30 | 240 | 93 | Y | N |  | 68 |  |  | 330 | 410 | 480 | 3 | 6 | 9 | 15 | 22.5 | 30 | 85.1 | 90.7 | 92.6 | 93.7 | 93.8 | 93.5 | 93.1 | 84.7 | 90.3 | 92.2 | 93.4 | 93.4 | 92.9 | 92.8 | 83.6 | 89.8 | 91.7 | 93 | 93.1 | 92.8 | 92.4
Satcon Technology | AE-30-60-PV-F [240V] | 30 kW, 240 Vac, 3-phase Utility Interactive Inverter | 30 | 240 | 94.5 | Y | N |  | 59 |  |  | 340 | 375 | 480 | 3 | 6 | 9 | 15 | 22.5 | 30 | 91.6 | 92.5 | 93.9 | 95.2 | 95.5 | 95.6 | 94.9 | 91.8 | 91.9 | 93.6 | 95 | 95.3 | 95.4 | 94.7 | 89.9 | 91.2 | 92.9 | 94.5 | 94.9 | 95 | 94.2
Satcon Technology | PVS-30 [208V] | 30 kW, 208 Vac, 3-phase Utility Interactive Inverter | 30 | 208 | 95 | Y | N |  | 75.62 |  |  | 305 | 350 | 480 | 3 | 6 | 9 | 15 | 22.5 | 30 | 88.8 | 93.5 | 94.8 | 95.7 | 95.6 | 95.4 | 95.1 | 88 | 93.1 | 94.7 | 95.4 | 95.5 | 95.3 | 95 | 87 | 92.4 | 94.2 | 95 | 95.1 | 95.1 | 94.5
Satcon Technology | PVS-30 [240V] | 30 kW, 240 Vac, 3-phase Utility Interactive Inverter | 30 | 240 | 95 | Y | N |  | 64.58 |  |  | 305 | 355 | 480 | 3 | 6 | 9 | 15 | 22.5 | 30 | 88.2 | 93.8 | 95 | 96 | 95.8 | 95.6 | 95.3 | 88.2 | 93.3 | 94.8 | 95.7 | 95.7 | 95.6 | 95.1 | 86.1 | 92.5 | 94.4 | 95.3 | 95.5 | 95.2 | 94.8
Satcon Technology | PVS-30 [480V] | 30 kW, 480 Vac, 3-phase Utility Interactive Inverter | 30 | 480 | 95 | Y | N |  | 72.3 |  |  | 305 | 350 | 480 | 3 | 6 | 9 | 15 | 22.5 | 30 | 88.4 | 93.5 | 94.6 | 95.6 | 95.6 | 95.3 | 95.1 | 87.7 | 93.1 | 94.6 | 95.4 | 95.5 | 95.3 | 95 | 86.3 | 92.1 | 93.9 | 94.9 | 95 | 94.8 | 94.3
Satcon Technology | AE-50-60-PV-D [208V] | 50 kW, 208 Vac, 3-phase Utility Interactive Inverter | 50 | 208 | 94.5 | Y | N |  | 90 |  |  | 327.2 | 410.9 | 474.9 | 5 | 10 | 15 | 25 | 37.5 | 50 | 88.2 | 93 | 94.4 | 95.4 | 95.2 | 95.2 | 94.7 | 86.7 | 92 | 93.8 | 94.9 | 94.8 | 94.8 | 94.2 | 85.8 | 91.2 | 93.2 | 94.6 | 94.5 | 94.6 | 93.8
Satcon Technology | AE-50-60-PV-F [240V] | 50 kW, 240 Vac, 3-phase Utility Interactive Inverter | 50 | 240 | 93 | Y | N |  | 68 |  |  | 340 | 430 | 480 | 5 | 10 | 15 | 25 | 37.5 | 50 | 84.3 | 90.6 | 92.7 | 94.4 | 94.4 | 94.5 | 93.6 | 81.8 | 89.1 | 91.8 | 93.6 | 93.8 | 94 | 92.8 | 80.2 | 88.2 | 91 | 93.2 | 93.5 | 93.8 | 92.3
Satcon Technology | PVS-50 [208V] | 50 kW, 208 Vac, 3-phase Utility Interactive Inverter | 50 | 208 | 95.5 | Y | N |  | 76.5 |  |  | 305 | 350 | 480 | 5 | 10 | 15 | 25 | 37.5 | 50 | 90.4 | 93.8 | 95.4 | 95.9 | 95.9 | 95.7 | 95.5 | 89.7 | 94.1 | 95.2 | 95.8 | 95.8 | 95.6 | 95.4 | 88.7 | 93 | 94.5 | 95.3 | 95.4 | 95.3 | 94.9
Satcon Technology | PVS-50 [240V] | 50 kW, 240 Vac, 3-phase Utility Interactive Inverter | 50 | 240 | 95.5 | Y | N |  | 93.97 |  |  | 310 | 365 | 480 | 5 | 10 | 15 | 25 | 37.5 | 50 | 90.8 | 95 | 95.9 | 96.2 | 96 | 95.5 | 95.7 | 90.4 | 94.8 | 95.3 | 96 | 95.7 | 95.5 | 95.5 | 89.6 | 93.3 | 95.2 | 95.5 | 95.4 | 95 | 95.1
Satcon Technology | PVS-50 [480V] | 50 kW, 480 Vac, 3-phase Utility Interactive Inverter | 50 | 480 | 95.5 | Y | N |  | 76.5 |  |  | 305 | 350 | 480 | 5 | 10 | 15 | 25 | 37.5 | 50 | 90.5 | 95 | 95.9 | 96.3 | 96.4 | 96 | 96 | 89.4 | 94.7 | 95.6 | 96.1 | 96.1 | 95.9 | 95.7 | 89.5 | 94.2 | 95.1 | 95.8 | 95.6 | 95.4 | 95.3
Satcon Technology | PVS-50-S-MT [208V] | 50 kW, 208 Vac, 3-phase Utility Interactive Inverter | 50 | 208 | 95.5 | Y | N |  | 81 | 50 | 81 | 265 | 320 | 480 | 5 | 10 | 15 | 25 | 37.5 | 50 | 91.6 | 95.4 | 96.1 | 96.3 | 96.1 | 95.7 | 95.9 | 91.3 | 95.3 | 96 | 96.2 | 96 | 95.6 | 95.8 | 89 | 94.8 | 95.4 | 95.5 | 95.5 | 95.1 | 95.2
Satcon Technology | PVS-50-S-MT [240V] | 50 kW, 240 Vac, 3-phase Utility Interactive Inverter | 50 | 240 | 95.5 | Y | N |  | 78 | 50 | 78 | 265 | 320 | 480 | 5 | 10 | 15 | 25 | 37.5 | 50 | 91.6 | 95.3 | 96.1 | 96.2 | 95.9 | 95.6 | 95.8 | 91 | 95.1 | 95.8 | 96.2 | 95.8 | 95.5 | 95.7 | 87.8 | 94.7 | 95.3 | 95.7 | 95.4 | 95.2 | 95.1
Satcon Technology | PVS-50-S-MT [480V] | 50 kW, 480 Vac, 3-phase Utility Interactive Inverter | 50 | 480 | 95.5 | Y | N |  | 78 | 50 | 78 | 265 | 320 | 480 | 5 | 10 | 15 | 25 | 37.5 | 50 | 92.1 | 95.3 | 96 | 96.2 | 96 | 95.7 | 95.9 | 91.5 | 95 | 95.7 | 96.1 | 95.9 | 95.6 | 95.7 | 88.7 | 94.3 | 95.3 | 95.6 | 95.4 | 95.2 | 95.1
Satcon Technology | AE-50-60-PV-A [480V] | 50 kW, 480 Vac, 3-phase Utility Interactive Inverter | 50.25 | 480 | 93 | Y | N |  | 100.8 |  |  | 330 | 420 | 480 | 5.03 | 10.05 | 15.08 | 25.13 | 37.69 | 50.25 | 81.1 | 88.9 | 91.7 | 93.7 | 94.6 | 94.7 | 93.2 | 79.9 | 88.2 | 91.1 | 93.3 | 94.3 | 94.7 | 92.8 | 79.3 | 87.7 | 90.6 | 93 | 93.9 | 94.2 | 92.5
Satcon Technology | AE-75-60-PV-A [480V] | 75 kW, 480 Vac, 3-phase Utility Interactive Inverter | 75 | 480 | 95.5 | Y | N |  | 99 |  |  | 318.9 | 405.6 | 479.5 | 7.5 | 15 | 22.5 | 37.5 | 56.25 | 75 | 91.1 | 94.4 | 95.5 | 96.1 | 96 | 95.9 | 95.7 | 90.3 | 93.9 | 95.1 | 95.8 | 95.6 | 95.5 | 95.3 | 89.5 | 93.4 | 94.6 | 95.5 | 95.4 | 95.3 | 95
Satcon Technology | AE-75-60-PV-D [208V] | 75 kW, 208 Vac, 3-phase Utility Interactive Inverter | 75 | 208 | 95.5 | Y | N |  | 99 |  |  | 330 | 415 | 480 | 7.5 | 15 | 22.5 | 37.5 | 56.25 | 75 | 90.9 | 94.4 | 95.5 | 96.1 | 96 | 95.9 | 95.7 | 90.5 | 94 | 95.1 | 95.9 | 95.7 | 95.6 | 95.4 | 89.6 | 93.6 | 94.9 | 95.6 | 95.5 | 95.4 | 95.1
Satcon Technology | PVS-75 [208V] | 75 kW, 208 Vac, 3-phase Utility Interactive Inverter | 75 | 208 | 96 | Y | N |  | 65.36 |  |  | 315 | 365 | 480 | 7.5 | 15 | 22.5 | 37.5 | 56.25 | 75 | 91 | 95.5 | 96.1 | 96.6 | 96.4 | 96.1 | 96.1 | 90.9 | 95.3 | 95.9 | 96.4 | 96.3 | 96 | 96 | 89.7 | 94.6 | 95.4 | 96.1 | 95.9 | 95.7 | 95.5
Satcon Technology | PVS-75 [240V] | 75 kW, 240 Vac, 3-phase Utility Interactive Inverter | 75 | 240 | 96 | Y | N |  | 71.84 |  |  | 315 | 365 | 480 | 7.5 | 15 | 22.5 | 37.5 | 56.25 | 75 | 92.3 | 95.5 | 96.3 | 96.6 | 96.6 | 96.3 | 96.3 | 91.2 | 95.5 | 96 | 96.5 | 96.5 | 96.2 | 96.1 | 90.6 | 94.8 | 95.4 | 96.1 | 96 | 96 | 95.7
Satcon Technology | PVS-75 [480V] | 75 kW, 480 Vac, 3-phase Utility Interactive Inverter | 75 | 480 | 96 | Y | N |  | 69.5 |  |  | 315 | 365 | 480 | 7.5 | 15 | 22.5 | 37.5 | 56.25 | 75 | 92.6 | 95.6 | 96.3 | 96.7 | 96.6 | 96.3 | 96.3 | 92.1 | 95.3 | 96 | 96.5 | 96.4 | 96.2 | 96.2 | 91.3 | 94.9 | 95.7 | 96.1 | 96.1 | 96 | 95.8
Satcon Technology | AE-100-60-PV-A [480V] | 100 kW, 480 Vac, 3-phase Utility Interactive Inverter | 100 | 480 | 94.5 | Y | N |  | 97.7 |  |  | 330 | 410 | 470 | 10 | 20 | 30 | 50 | 75 | 100 | 88.7 | 93.1 | 94.6 | 95.6 | 95.8 | 95.7 | 95.2 | 87.3 | 92.3 | 93.9 | 95 | 95.3 | 95.2 | 94.6 | 86.6 | 91.8 | 93.6 | 94.8 | 95.1 | 95.1 | 94.4
Satcon Technology | AE-100-60-PV-A-HE [480V] | 100 kW, 480 Vac, 3-phase Utility Interactive Inverter | 100 | 480 | 95.5 | Y | N |  | 97.7 |  |  | 330 | 400 | 480 | 10 | 20 | 30 | 50 | 75 | 100 | 93.2 | 95.5 | 96 | 96.1 | 95.6 | 95.3 | 95.7 | 93.3 | 95.3 | 95.8 | 95.9 | 95.9 | 95.2 | 95.7 | 92.9 | 94.7 | 95.5 | 95.4 | 95.2 | 94.8 | 95.2
Satcon Technology | AE-100-60-PV-D [208V] | 100 kW, 208 Vac, 3-phase Utility Interactive Inverter | 100 | 208 | 94.5 | Y | N |  | 91.5 |  |  | 330 | 402 | 470 | 10 | 20 | 30 | 50 | 75 | 100 | 89.3 | 94.1 | 94.5 | 95.6 | 95.3 | 95.1 | 95 | 88.6 | 92.9 | 94.2 | 95 | 95.1 | 94.9 | 94.6 | 89.7 | 92.8 | 94.2 | 94.7 | 94.7 | 94.5 | 94.4
Satcon Technology | AE-100-60-PV-F [240V] | 100 kW, 240 Vac, 3-phase Utility Interactive Inverter | 100 | 240 | 95 | Y | N |  | 97.7 |  |  | 330 | 408 | 480 | 10 | 20 | 30 | 50 | 75 | 100 | 90.2 | 93.9 | 94.9 | 95.8 | 95.7 | 95.5 | 95.3 | 89.3 | 93.2 | 94.7 | 95.3 | 95.4 | 95.2 | 94.9 | 88.8 | 93.2 | 94.2 | 95 | 95.3 | 94.9 | 94.7
Satcon Technology | PVS-100 [208V] | 100 kW, 208 Vac, 3-phase Utility Interactive Inverter | 100 | 208 | 96 | Y | N |  | 62.34 |  |  | 315 | 365 | 480 | 10 | 20 | 30 | 50 | 75 | 100 | 92.6 | 95.7 | 96.4 | 96.6 | 96.5 | 96.2 | 96.3 | 92.4 | 95.5 | 96.2 | 96.5 | 96.4 | 96.1 | 96.2 | 91.3 | 94.9 | 95.7 | 96.1 | 96.1 | 95.8 | 95.8
Satcon Technology | PVS-100 [240V] | 100 kW, 240 Vac, 3-phase Utility Interactive Inverter | 100 | 240 | 96 | Y | N |  | 61.57 |  |  | 315 | 365 | 480 | 10 | 20 | 30 | 50 | 75 | 100 | 91.1 | 95.3 | 96.1 | 96.5 | 96.5 | 96.2 | 96.1 | 90.6 | 94.9 | 95.9 | 96.4 | 96.3 | 96.1 | 96 | 89.4 | 94.3 | 95.4 | 96 | 96 | 95.8 | 95.6
Satcon Technology | PVS-100 [480V] | 100 kW, 480 Vac, 3-phase Utility Interactive Inverter | 100 | 480 | 96 | Y | N |  | 66.13 |  |  | 315 | 365 | 480 | 10 | 20 | 30 | 50 | 75 | 100 | 93.2 | 96.1 | 96.5 | 96.7 | 96.5 | 96.1 | 96.4 | 93.6 | 95.9 | 96.4 | 96.5 | 96.4 | 96 | 96.3 | 93 | 95.6 | 96.2 | 96.3 | 96.1 | 95.8 | 96
Satcon Technology | SDMS0100208LNIU [208V] | 100 kW, 208 Vac, 3-phase Inverter with combiner | 100 | 208 | 95 | Y | N |  | 60.38 |  |  | 300 | 430 | 480 | 10 | 20 | 30 | 50 | 75 | 100 | 91.5 | 94.2 | 95.2 | 95.5 | 95.2 | 94.8 | 95 | 89.5 | 92.3 | 95 | 95.8 | 95.6 | 95.3 | 95.1 | 90.1 | 93.5 | 94.7 | 95.9 | 95.8 | 95.5 | 95.3
Satcon Technology | SDMS0100240LNIU [240V] | 100 kW, 240 Vac, 3-phase Inverter with combiner | 100 | 240 | 95 | Y | N |  | 61.79 |  |  | 300 | 430 | 480 | 10 | 20 | 30 | 50 | 75 | 100 | 90.1 | 93.5 | 94.6 | 95.1 | 95.1 | 94.7 | 94.7 | 88.1 | 91.6 | 94.4 | 95.4 | 95.5 | 95.2 | 94.8 | 88.7 | 92.8 | 94.2 | 95.5 | 95.7 | 95.3 | 95
Satcon Technology | SDMS0100480LNIU [480V] | 100 kW, 480 Vac, 3-phase Inverter with combiner | 100 | 480 | 95 | Y | N |  | 63.88 |  |  | 300 | 430 | 480 | 10 | 20 | 30 | 50 | 75 | 100 | 89.5 | 93.4 | 94.4 | 95.1 | 95 | 94.7 | 94.6 | 87.6 | 91.5 | 94.3 | 95.3 | 95.4 | 95.2 | 94.7 | 88.1 | 92.7 | 94 | 95.4 | 95.6 | 95.4 | 94.9
Satcon Technology | PVS-110-S-MT [208V] | 110 kW, 208 Vac, 3-phase Utility Interactive Inverter | 110 | 208 | 95 | Y | N |  | 72.5 |  |  | 265 | 320 | 480 | 11 | 22 | 33 | 55 | 82.5 | 110 | 92.6 | 95.4 | 95.8 | 95.9 | 95.6 | 94.8 | 95.5 | 91.9 | 95 | 95.5 | 95.7 | 95.4 | 94.7 | 95.3 | 89.8 | 93.7 | 94.6 | 95 | 94.8 | 94.1 | 94.5
Satcon Technology | PVS-110-S-MT [240V] | 110 kW, 240 Vac, 3-phase Utility Interactive Inverter | 110 | 240 | 95.5 | Y | N |  | 70.6 |  |  | 265 | 320 | 480 | 11 | 22 | 33 | 55 | 82.5 | 110 | 93 | 95.6 | 96.1 | 96.1 | 95.8 | 95.2 | 95.8 | 92.3 | 95.2 | 95.8 | 95.8 | 95.6 | 95 | 95.5 | 90.4 | 94.1 | 94.9 | 95.2 | 95 | 94.5 | 94.8
Satcon Technology | PVS-110-S-MT [480V] | 110 kW, 480 Vac, 3-phase Utility Interactive Inverter | 110 | 480 | 95.5 | Y | N |  | 74.3 |  |  | 265 | 320 | 480 | 11 | 22 | 33 | 55 | 82.5 | 110 | 93.2 | 95.8 | 96.1 | 96.3 | 96 | 95.5 | 95.9 | 92.6 | 95.4 | 95.8 | 96 | 95.8 | 95.3 | 95.7 | 90.9 | 94.3 | 95 | 95.3 | 95.3 | 94.8 | 95
Satcon Technology | AE-135-60-PV-A [480V] | 135 kW, 480 Vac, 3-phase Utility Interactive Inverter | 135 | 480 | 95.5 | Y | N |  | 98 |  |  | 330 | 415 | 470 | 13.5 | 27 | 40.5 | 67.5 | 101.3 | 135 | 90.7 | 94.2 | 95.4 | 96.1 | 96.1 | 95.9 | 95.7 | 90 | 93.8 | 95 | 95.6 | 95.7 | 95.5 | 95.3 | 89.4 | 93.4 | 94.7 | 95.4 | 95.5 | 95.4 | 95
Satcon Technology | AE-135-60-PV-D [208V] | 135 kW, 208 Vac, 3-phase Utility Interactive Inverter | 135 | 208 | 95 | Y | N |  | 96 |  |  | 330 | 415 | 470 | 13.5 | 27 | 40.5 | 67.5 | 101.3 | 135 | 91.6 | 94.9 | 95.6 | 96 | 95.9 | 95.5 | 95.7 | 91.1 | 94.5 | 95.4 | 95.9 | 95.7 | 95.3 | 95.4 | 88.7 | 92.7 | 94.2 | 95 | 95.1 | 94.9 | 94.6
Satcon Technology | PVS-135 [208V] | 135 kW, 208 Vac, 3-phase Utility Interactive Inverter | 135 | 208 | 96 | Y | N |  | 63.12 |  |  | 310 | 355 | 480 | 13.5 | 27 | 40.5 | 67.5 | 101.3 | 135 | 92.9 | 95.6 | 95.8 | 96.5 | 96.4 | 96.1 | 96.1 | 92.5 | 95.4 | 96.1 | 96.4 | 96.2 | 95.9 | 96 | 91 | 94 | 95 | 95.7 | 95.8 | 95.7 | 95.4
Satcon Technology | PVS-135 [240V] | 135 kW, 240 Vac, 3-phase Utility Interactive Inverter | 135 | 240 | 96 | Y | N |  | 63.7 |  |  | 320 | 360 | 480 | 13.5 | 27 | 40.5 | 67.5 | 101.3 | 135 | 92.4 | 95.6 | 95.8 | 96.6 | 96.6 | 96.3 | 96.3 | 92 | 95.3 | 96 | 96.4 | 96.4 | 96.2 | 96.1 | 91 | 94 | 95 | 95.7 | 95.8 | 95.7 | 95.4
Satcon Technology | PVS-135 [480V] | 135 kW, 480 Vac, 3-phase Utility Interactive Inverter | 135 | 480 | 96 | Y | N |  | 63.67 |  |  | 310 | 355 | 480 | 13.5 | 27 | 40.5 | 67.5 | 101.3 | 135 | 92.9 | 95.8 | 96.5 | 96.7 | 96.5 | 96.2 | 96.4 | 92.4 | 95.5 | 96.2 | 96.4 | 96.4 | 96.1 | 96.1 | 90.8 | 94.7 | 95.6 | 96 | 95.9 | 95.7 | 95.6
Satcon Technology | PVS-210-S [208V] | 210 kW, 208 Vac, 3-phase Utility Interactive Inverter | 210 | 208 | 95.5 | Y | N |  | 160.8 |  |  | 265 | 318 | 480 | 21 | 42 | 63 | 105 | 157.5 | 210 | 93.5 | 95.7 | 96.2 | 96.2 | 96.1 | 95.5 | 96 | 93.1 | 95.5 | 96 | 96 | 95.6 | 95.2 | 95.6 | 91.9 | 94.6 | 95.2 | 95.3 | 95 | 94.6 | 94.9
Satcon Technology | PVS-210-S [240V] | 210 kW, 240 Vac, 3-phase Utility Interactive Inverter | 210 | 240 | 95.5 | Y | N |  | 112.9 |  |  | 265 | 318 | 480 | 21 | 42 | 63 | 105 | 157.5 | 210 | 93.2 | 95.7 | 96.2 | 96.3 | 96.1 | 95.6 | 96 | 92.7 | 95.5 | 95.9 | 96 | 95.7 | 95.3 | 95.7 | 91.6 | 94.4 | 95.2 | 95.2 | 95.1 | 94.6 | 95
Satcon Technology | PVS-210-S [480V] | 210 kW, 480 Vac, 3-phase Utility Interactive Inverter | 210 | 480 | 95.5 | Y | N |  | 189.8 |  |  | 265 | 318 | 480 | 21 | 42 | 63 | 105 | 157.5 | 210 | 92 | 95.2 | 95.8 | 96.2 | 96 | 95.7 | 95.8 | 91.7 | 94.9 | 95.7 | 95.9 | 95.5 | 95.4 | 95.4 | 90.8 | 94.1 | 95 | 95.3 | 95.1 | 94.8 | 94.9
Satcon Technology | AE-225-60-PV-A [480V] | 225 kW, 480 Vac, 3-phase Utility Interactive Inverter | 225 | 480 | 94.5 | Y | N |  | 114 |  |  | 330 | 430 | 480 | 22.5 | 45 | 67.5 | 112.5 | 168.8 | 225 | 90.2 | 93.5 | 94.8 | 95.5 | 95.5 | 95.4 | 95.1 | 89 | 93 | 94.3 | 95 | 95.1 | 94.8 | 94.6 | 88.5 | 92.7 | 94 | 94.8 | 95 | 94.6 | 94.4
Satcon Technology | AE-225-60-PV-D [208V] | 225 kW, 208 Vac, 3-phase Utility Interactive Inverter | 225 | 208 | 95.5 | Y | N |  | 180 |  |  | 330 | 415 | 470 | 22.5 | 45 | 67.5 | 112.5 | 168.8 | 225 | 92.2 | 95 | 95.7 | 96.1 | 95.9 | 95.5 | 95.7 | 93.2 | 94.7 | 95.5 | 95.8 | 95.7 | 95.3 | 95.5 | 91.8 | 94.4 | 95.2 | 95.6 | 95.5 | 95.2 | 95.2
Satcon Technology | PVS-250 | 250 kW, 3-phase Inverter for Medium Voltage Transformer | 250 |  | 95.5 | Y | N |  | 151.8 |  |  | 330 | 368 | 480 | 25 | 50 | 75 | 125 | 187.5 | 250 | 93.8 | 95.4 | 96 | 96.2 | 96 | 95.4 | 95.9 | 93.3 | 95.2 | 95.8 | 96 | 95.8 | 95.2 | 95.7 | 92.1 | 94.6 | 95.3 | 95.6 | 95.2 | 94.7 | 95.1
Satcon Technology | PVS-250 [208V] | 250 kW, 208 Vac, 3-phase Utility Interactive Inverter | 250 | 208 | 96 | Y | N |  | 105.1 | 250 | 105.1 | 320 | 365 | 480 | 25 | 50 | 75 | 125 | 187.5 | 250 | 95.1 | 96.3 | 96.5 | 96.4 | 96.5 | 96 | 96.4 | 94.4 | 95.9 | 96.4 | 96.3 | 96.3 | 95.8 | 96.2 | 93.7 | 95.9 | 96.2 | 95.9 | 95.8 | 95.3 | 95.8
Satcon Technology | PVS-250 [240V] | 250 kW, 240 Vac, 3-phase Utility Interactive Inverter | 250 | 240 | 96 | Y | N |  | 100 | 250 | 100 | 322 | 365 | 480 | 25 | 50 | 75 | 125 | 187.5 | 250 | 92.5 | 95.8 | 96.4 | 96.6 | 96.5 | 96.2 | 96.3 | 92.3 | 95.6 | 96.2 | 96.4 | 96.3 | 96 | 96.1 | 91.9 | 95.1 | 95.9 | 96 | 95.9 | 95.6 | 95.7
Satcon Technology | PVS-250 [480V] | 250 kW, 480 Vac, 3-phase Utility Interactive Inverter | 250 | 480 | 96 | Y | N |  | 119.7 | 250 | 119.7 | 320 | 365 | 480 | 25 | 50 | 75 | 125 | 187.5 | 250 | 93.4 | 96 | 96.4 | 96.6 | 96.5 | 96 | 96.3 | 93.1 | 95.7 | 96.2 | 96.3 | 96.2 | 95.7 | 96 | 92.3 | 94.9 | 95.8 | 95.9 | 95.7 | 95.2 | 95.5
Satcon Technology | PVS-375 [480V] | 375 kW, 480 Vac, 3-phase Utility Interactive Inverter | 375 | 480 | 95.5 | Y | N |  | 123.5 |  |  | 320 | 365 | 480 | 37.5 | 75 | 112.5 | 187.5 | 281.3 | 375 | 92.6 | 95.4 | 96 | 96.3 | 96.2 | 95.8 | 96 | 92.1 | 95.1 | 95.7 | 96 | 95.8 | 95.6 | 95.7 | 90.9 | 94.6 | 95 | 95.5 | 95.3 | 95.1 | 95.1
Satcon Technology | AE-500-60-PV-A [480V] | 500 kW, 480 Vac, 3-phase Utility Interactive Inverter | 500 | 480 | 95 | Y | N |  | 208 |  |  | 330 | 405 | 480 | 50 | 100 | 150 | 250 | 375 | 500 | 93.2 | 94.9 | 95.7 | 95.8 | 95.6 | 95.2 | 95.5 | 91.8 | 94.5 | 95.4 | 95.5 | 95.4 | 94.9 | 95.2 | 91.3 | 93.7 | 94.6 | 95.1 | 95 | 94.8 | 94.8
Satcon Technology | EQX0500US200X-N | 500 kW, 3-phase Inverter, N for ground type | 500 |  | 96 | Y | N |  | 171.5 |  |  | 320 | 360 | 480 | 50 | 100 | 150 | 250 | 375 | 500 | 93.9 | 96.1 | 96.5 | 96.6 | 96.1 | 95.6 | 96.2 | 93.6 | 96 | 96.5 | 96.5 | 96.1 | 95.6 | 96.1 | 92.7 | 95.5 | 96.1 | 96.2 | 95.9 | 95.5 | 95.8
Satcon Technology | EQX0500US200X-P | 500 kW, 3-phase Inverter, P for ground type | 500 |  | 96 | Y | N |  | 171.5 |  |  | 320 | 360 | 480 | 50 | 100 | 150 | 250 | 375 | 500 | 93.9 | 96.1 | 96.5 | 96.6 | 96.1 | 95.6 | 96.2 | 93.6 | 96 | 96.5 | 96.5 | 96.1 | 95.6 | 96.1 | 92.7 | 95.5 | 96.1 | 96.2 | 95.9 | 95.5 | 95.8
Satcon Technology | EQX0500US480T-N | 500 kW, 3-phase Inverter, N for ground type | 500 |  | 96 | Y | N |  | 116.5 |  |  | 320 | 360 | 480 | 50 | 100 | 150 | 250 | 375 | 500 | 92 | 95.4 | 96.2 | 96.7 | 96.6 | 96.4 | 96.3 | 91.7 | 95.3 | 96.1 | 96.6 | 96.6 | 96.5 | 96.3 | 90.8 | 94.8 | 95.8 | 96.4 | 96.4 | 96.3 | 96
Satcon Technology | EQX0500US480T-P | 500 kW, 3-phase Inverter, P for ground type | 500 |  | 96 | Y | N |  | 116.5 |  |  | 320 | 360 | 480 | 50 | 100 | 150 | 250 | 375 | 500 | 92 | 95.4 | 96.2 | 96.7 | 96.6 | 96.4 | 96.3 | 91.7 | 95.3 | 96.1 | 96.6 | 96.6 | 96.5 | 96.3 | 90.8 | 94.8 | 95.8 | 96.4 | 96.4 | 96.3 | 96
Satcon Technology | PVS-500 | 500 kW, 3-phase Inverter for Medium Voltage Transformer | 500 |  | 95.5 | Y | N |  | 2630 |  |  | 320 | 365 | 480 | 50 | 100 | 150 | 250 | 375 | 500 | 93.9 | 95.7 | 96.1 | 96 | 95.4 | 94.6 | 95.5 | 93.3 | 95.4 | 95.8 | 95.8 | 95.2 | 94.5 | 95.3 | 92.9 | 94.9 | 95.4 | 95.5 | 94.9 | 94.2 | 95
Satcon Technology | PVS-500 [480V] | 500 kW, 480 Vac, 3-phase Utility Interactive Inverter | 500 | 480 | 96 | Y | N |  | 131.1 |  |  | 315 | 365 | 480 | 50 | 100 | 150 | 250 | 375 | 500 | 92.9 | 95.7 | 96.2 | 96.5 | 96.4 | 96 | 96.2 | 92.4 | 95.4 | 96.1 | 96.3 | 96.2 | 95.8 | 96 | 91.8 | 95 | 95.7 | 96 | 95.8 | 95.3 | 95.6
Satcon Technology | SDMS0500UL320XN [320V] | 500 kW, 320 Vac, 3-phase Inverter with combiner, N for ground type | 500 | 320 | 95.5 | Y | N |  | 98 |  |  | 300 | 430 | 480 | 50 | 100 | 150 | 250 | 375 | 500 | 90.51 | 94.95 | 95.18 | 95.47 | 95.31 | 94.7 | 95.09 | 91.29 | 93.9 | 95.72 | 95.96 | 95.59 | 95.09 | 95.4 | 90.71 | 93.8 | 95.8 | 95.9 | 95.76 | 95.19 | 95.46
Satcon Technology | SDMS0500UL320XP [320V] | 501 kW, 320 Vac, 3-phase Inverter with combiner, P for ground type | 500 | 320 | 95.5 | Y | N |  | 98 |  |  | 300 | 430 | 480 | 50 | 100 | 150 | 250 | 375 | 500 | 90.51 | 94.95 | 95.18 | 95.47 | 95.31 | 94.7 | 95.09 | 91.29 | 93.9 | 95.72 | 95.96 | 95.59 | 95.09 | 95.4 | 90.71 | 93.8 | 95.8 | 95.9 | 95.76 | 95.19 | 95.46
Satcon Technology | SDMS0500UL480TN [480V] | 500 kW, 480 Vac, 3-phase Inverter with combiner, N for ground type | 500 | 480 | 96 | Y | N |  | 101 |  |  | 300 | 430 | 480 | 50 | 100 | 150 | 250 | 375 | 500 | 90.2 | 95.09 | 95.37 | 95.88 | 95.89 | 95.51 | 95.54 | 90.99 | 94.04 | 95.92 | 96.36 | 96.17 | 95.9 | 95.85 | 90.4 | 93.94 | 95.99 | 96.31 | 96.34 | 96 | 95.92
Satcon Technology | SDMS0500UL480TP [480V] | 501 kW, 480 Vac, 3-phase Inverter with combiner, P for ground type | 500 | 480 | 96 | Y | N |  | 101 |  |  | 300 | 430 | 480 | 50 | 100 | 150 | 250 | 375 | 500 | 90.2 | 95.09 | 95.37 | 95.88 | 95.89 | 95.51 | 95.54 | 90.99 | 94.04 | 95.92 | 96.36 | 96.17 | 95.9 | 95.85 | 90.4 | 93.94 | 95.99 | 96.31 | 96.34 | 96 | 95.92
Satcon Technology | EPP-1000-0600-32060-200X-U-N | 1000 kW, 3-phase Inverter, N for ground type | 1000 |  | 96.5 | Y | N |  | 325.5 |  |  | 320 | 360 | 480 | 100 | 200 | 300 | 500 | 750 | 1000 | 94.53 | 96.46 | 96.79 | 96.78 | 96.35 | 95.71 | 96.4 | 94.29 | 96.32 | 96.66 | 96.68 | 96.31 | 95.7 | 96.32 | 93.53 | 95.84 | 96.32 | 96.43 | 96.12 | 95.58 | 96.07
Satcon Technology | EPP-1000-0600-32060-200X-U-P | 1000 kW, 3-phase Inverter, P for ground type | 1000 |  | 96.5 | Y | N |  | 325.5 |  |  | 320 | 360 | 480 | 100 | 200 | 300 | 500 | 750 | 1000 | 94.53 | 96.46 | 96.79 | 96.78 | 96.35 | 95.71 | 96.4 | 94.29 | 96.32 | 96.66 | 96.68 | 96.31 | 95.7 | 96.32 | 93.53 | 95.84 | 96.32 | 96.43 | 96.12 | 95.58 | 96.07
Satcon Technology | PVS-1000 | 1000 kW, 3-phase Inverter for Medium Voltage Transformer | 1000 |  | 96 | Y | N |  | 396.4 |  |  | 420 | 486 | 670 | 100 | 200 | 300 | 500 | 750 | 1000 | 93.7 | 96.1 | 96.7 | 96.9 | 96.6 | 96.1 | 96.5 | 93.2 | 95.8 | 96.4 | 96.7 | 96.5 | 96 | 96.3 | 91.7 | 94.9 | 95.7 | 96.1 | 95.9 | 95.5 | 95.7
Satcon Technology | EPP-1250-1000-52085-320X-U-N | 1250 kW, 3-phase Inverter, N for ground type | 1250 |  | 97 | Y | N |  | 320.4 |  |  | 525 | 595 | 800 | 125 | 250 | 375 | 625 | 937.5 | 1250 | 94.6 | 96.7 | 97.3 | 97.4 | 97.1 | 96.7 | 97 | 94.1 | 96.5 | 97.1 | 97.2 | 97 | 96.5 | 96.9 | 93 | 95.9 | 96.6 | 96.8 | 96.7 | 96.2 | 96.5
Satcon Technology | EPP-1250-1000-52085-320X-U-P | 1250 kW, 3-phase Inverter, P for ground type | 1250 |  | 97 | Y | N |  | 320.4 |  |  | 525 | 595 | 800 | 125 | 250 | 375 | 625 | 937.5 | 1250 | 94.6 | 96.7 | 97.3 | 97.4 | 97.1 | 96.7 | 97 | 94.1 | 96.5 | 97.1 | 97.2 | 97 | 96.5 | 96.9 | 93 | 95.9 | 96.6 | 96.8 | 96.7 | 96.2 | 96.5
Schneider Electric Solar Inverters USA, Inc. | Conext TX 2800 NA [208V] | 2.65 kW, 208 Vac, Grid Tie Inverter | 2.65 | 208 | 94.5 | Y | N |  | 1.23 | 2.65 | 1.23 | 100 | 300 | 480 | 0.27 | 0.53 | 0.8 | 1.33 | 1.99 | 2.65 | 88.5 | 93.2 | 94.5 | 95.2 | 95.2 | 94.8 | 94.7 | 87.9 | 92.9 | 94.2 | 95 | 95 | 94.8 | 94.5 | 85.9 | 91.8 | 93.5 | 94.4 | 94.5 | 94.4 | 93.9 |  | 2018-05-01
Schneider Electric Solar Inverters USA, Inc. | Conext TX 2800 NA [240V] | 2.8 kW, 240 Vac, Grid Tie Inverter | 2.8 | 240 | 94.5 | Y | N |  | 1.22 | 2.8 | 1.22 | 100 | 300 | 480 | 0.28 | 0.56 | 0.84 | 1.4 | 2.1 | 2.8 | 88.9 | 93.4 | 94.5 | 95.2 | 95.2 | 94.8 | 94.8 | 88.4 | 93.1 | 94.3 | 95 | 95.1 | 94.7 | 94.6 | 86.4 | 92.2 | 93.7 | 94.6 | 94.7 | 94.3 | 94 |  | 2018-05-01
Schneider Electric Solar Inverters USA, Inc. | Conext TX 3300 NA [208V] | 3.1 kW, 208 Vac, Grid Tie Inverter | 3.1 | 208 | 94.5 | Y | N |  | 0.96 | 3.1 | 96 | 100 | 300 | 480 | 0.31 | 0.62 | 0.93 | 1.55 | 2.33 | 3.1 | 89.3 | 93.4 | 94.6 | 95.3 | 95.2 | 94.7 | 94.8 | 88.9 | 93.1 | 94.5 | 95.1 | 95.1 | 94.6 | 94.6 | 86.7 | 92.3 | 93.8 | 94.6 | 94.7 | 94.2 | 94.1 |  | 2018-05-01
Schneider Electric Solar Inverters USA, Inc. | Conext TX 3300 NA [240V] | 3.3 kW, 240 Vac, Grid Tie Inverter | 3.3 | 240 | 95 | Y | N |  | 1.22 | 3.3 | 1.22 | 100 | 300 | 480 | 0.33 | 0.66 | 0.99 | 1.65 | 2.48 | 3.3 | 89.8 | 93.9 | 94.9 | 95.6 | 95.5 | 95.1 | 95.1 | 89.4 | 93.6 | 94.7 | 95.4 | 95.4 | 95 | 95 | 87.8 | 92.8 | 94.2 | 95 | 95 | 94.7 | 94.5 |  | 2018-05-01
Schneider Electric Solar Inverters USA, Inc. | Conext TX 3800 NA [208V] | 3.5 kW, 208 Vac, Grid Tie Inverter | 3.5 | 208 | 95.5 | Y | N |  | 0.96 | 3.5 | 0.96 | 100 | 300 | 480 | 0.35 | 0.7 | 1.05 | 1.75 | 2.63 | 3.5 | 91.3 | 95 | 95.8 | 96 | 95.8 | 95.3 | 95.6 | 90.9 | 94.6 | 95.6 | 95.8 | 95.6 | 95.1 | 95.4 | 89.2 | 93.8 | 94.9 | 95.3 | 95.2 | 94.7 | 94.8 |  | 2018-05-01
Schneider Electric Solar Inverters USA, Inc. | Conext TX 3800 NA [240V] | 3.8 kW, 240 Vac, Grid Tie Inverter | 3.8 | 240 | 95.5 | Y | N |  | 1.21 | 3.8 | 1.21 | 100 | 300 | 480 | 0.38 | 0.76 | 1.14 | 1.9 | 2.85 | 3.8 | 92.3 | 95.4 | 96.2 | 96.3 | 96.1 | 95.5 | 95.9 | 91.8 | 95.1 | 95.9 | 96.1 | 95.8 | 95.4 | 95.7 | 90.1 | 94.2 | 95.2 | 95.6 | 95.4 | 95 | 95.1 |  | 2018-05-01
Schneider Electric Solar Inverters USA, Inc. | XW4024-120/240-60 [120V] | 4 kVA, 24 Vdc, 120/240 Vac, battery backup, Utility Interactive Inverter | 4 | 120 | 91.5 | Y | N |  | 29.65 | 4 | 29.65 | 100 | 26 | 29 | 0.4 | 0.8 | 1.2 | 2 | 3 | 4 | 87.9 | 92.9 | 93.5 | 93 | 91.3 | 89.4 | 91.8 | 87.8 | 92.8 | 93.4 | 92.9 | 91.2 | 89.2 | 91.7 | 87.8 | 92.6 | 93.2 | 92.5 | 91 | 89.1 | 91.5 |  | 2018-05-01
Schneider Electric Solar Inverters USA, Inc. | XW4024-120/240-60 | 4 kVA, 24 Vdc, 120/240 Vac, battery backup, Utility Interactive Inverter | 4.09 |  | 91 | Y | N |  | 24 |  |  | 100 | 26 | 29 | 0.41 | 0.82 | 1.2 | 2 | 3.1 | 4.1 | 88.8 | 92.9 | 93.3 | 92.5 | 90.5 | 88.4 | 91.2 | 88.6 | 92.7 | 93.1 | 92 | 90.1 | 88.1 | 90.8 | 89 | 92.9 | 93.3 | 92.4 | 90.3 | 88.1 | 91.1 |  | 2018-05-01
Schneider Electric Solar Inverters USA, Inc. | XW4548-120/240-60 | 4.5 kVA, 48Vdc, 120/240 Vac, battery backup, Utility Interactive Inverter | 4.4 |  | 93 | Y | N |  | 26 |  |  | 100 | 53 | 58 | 0.44 | 0.88 | 1.32 | 2.2 | 3.3 | 4.4 | 89.7 | 93.5 | 94.4 | 94.1 | 93 | 91.7 | 93.2 | 88.7 | 93.3 | 94.2 | 94 | 92.9 | 91.5 | 93.1 | 88.6 | 93.2 | 94 | 93.8 | 92.6 | 91.5 | 92.9 |  | 2018-05-01
Schneider Electric Solar Inverters USA, Inc. | Conext TX 5000 NA [208V] | 4.5 kW, 208 Vac, Grid Tie Inverter | 4.5 | 208 | 95.5 | Y | N |  | 0.98 | 4.5 | 0.98 | 100 | 300 | 480 | 0.45 | 0.9 | 1.35 | 2.25 | 3.38 | 4.5 | 93.1 | 95.8 | 96.4 | 96.4 | 95.9 | 95.2 | 95.9 | 92.5 | 95.6 | 96.2 | 96.2 | 95.8 | 95.1 | 95.7 | 91.2 | 94.7 | 95.5 | 95.7 | 95.4 | 94.8 | 95.2 |  | 2018-05-01
Schneider Electric Solar Inverters USA, Inc. | XW+5548-NA | 4491 W, 120/240 Vac, 48 Vdc Utility Interactive Inverter with battery backup | 4.5 |  | 93.5 | Y | N |  | 17 |  |  | 100 | 52 | 58 | 0.45 | 0.9 | 1.35 | 2.25 | 3.37 | 4.49 | 92.6 | 94.6 | 94.8 | 94.4 | 93 | 91.7 | 93.5 | 91.6 | 94.6 | 94.9 | 94.4 | 93 | 91.5 | 93.4 | 92.3 | 94.3 | 94.7 | 94.2 | 92.9 | 91.6 | 93.4 |  | 2018-05-01
Schneider Electric Solar Inverters USA, Inc. | XW+5548-NA [120V] | 4492 W, 120 Vac, 48 Vdc Utility Interactive Inverter with battery backup | 4.5 | 120 | 93 | Y | N |  | 8 |  |  | 100 | 52 | 58 | 0.45 | 0.89 | 1.34 | 2.23 | 3.34 | 4.45 | 92.2 | 94.5 | 94.5 | 94 | 92.6 | 91.3 | 93.1 | 92.2 | 94.2 | 94.4 | 93.9 | 92.6 | 91.2 | 93.1 | 92.5 | 94.1 | 94.7 | 93.7 | 92.6 | 91.1 | 93.1 |  | 2018-05-01
Schneider Electric Solar Inverters USA, Inc. | Conext TX 5000 NA [240V] | 5.0 kW, 240 Vac, Grid Tie Inverter | 5 | 240 | 96 | Y | N |  | 1.25 | 5 | 1.25 | 100 | 300 | 480 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 94.1 | 96.2 | 96.7 | 96.7 | 96.2 | 95.4 | 96.3 | 93.7 | 96 | 96.5 | 96.5 | 96.1 | 95.3 | 96.1 | 92.4 | 95.2 | 95.9 | 96 | 95.7 | 95 | 95.6 |  | 2018-05-01
Schneider Electric Solar Inverters USA, Inc. | XW6048-120-60 [120V] | 6 kVA, 120Vac, 48 Vdc Utility Interactive Inverter with battery backup | 5.76 | 120 | 92.5 | Y | N |  | 45 |  |  | 100 | 52 | 58 | 0.58 | 1.15 | 1.73 | 2.88 | 4.32 | 5.76 | 90 | 93.9 | 94.1 | 93.6 | 92 | 90.4 | 92.5 | 89.8 | 93.7 | 94 | 93.5 | 91.8 | 90.3 | 92.4 | 89.5 | 93.5 | 93.8 | 93.3 | 91.8 | 90.2 | 92.2 |  | 2018-05-01
Schneider Electric Solar Inverters USA, Inc. | XW+6848-NA | 6000 W, 120Vac/240 Vac, 48 Vdc Utility Interactive Inverter with battery backup | 5.8 |  | 92.5 | Y | N |  | 6 |  |  | 100 | 52 | 58 | 0.58 | 1.15 | 1.73 | 2.88 | 4.31 | 5.75 | 90.6 | 93.7 | 94.1 | 93.3 | 92 | 90.5 | 92.5 | 90 | 93.5 | 93.9 | 93.3 | 91.9 | 90.3 | 92.3 | 89.8 | 93.5 | 93.7 | 93.2 | 91.7 | 90.1 | 92.2 |  | 2018-05-01
Schneider Electric Solar Inverters USA, Inc. | XW+6848-NA [120V] | 5751 W, 120 Vac, 48 Vdc Utility Interactive Inverter with battery backup | 6 | 120 | 92.5 | Y | N |  | 1 |  |  | 100 | 52 | 58 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 91.5 | 94 | 94.3 | 93.6 | 92.1 | 90 | 92.7 | 91.3 | 93.9 | 94.2 | 93.5 | 91.9 | 89.8 | 92.5 | 91.3 | 93.8 | 93.9 | 93.3 | 91.7 | 89.7 | 92.3 |  | 2018-05-01
Schneider Electric Solar Inverters USA, Inc. | XW6048-120/240 | 6 kVA, 120/240 Vac, 48 Vdc Utility Interactive Inverter with battery backup | 6 |  | 92.5 | Y | N |  | 26 |  |  | 100 | 52 | 58 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 91.4 | 94.1 | 94.2 | 93.5 | 91.6 | 89.8 | 92.3 | 90.8 | 94 | 94.2 | 93.5 | 91.9 | 89.7 | 92.5 | 90.7 | 93.9 | 94 | 93.4 | 91.8 | 89.6 | 92.3 |  | 2018-05-01
Schneider Electric Solar Inverters USA, Inc. | Conext CL 18000NA | 18 kW, 422-528 Vac, 3-phase Utility Interactive Inverter | 18.2 | 422-528 | 97 | Y | N |  | 1.2 |  |  | 300 | 670 | 800 | 1.82 | 3.64 | 5.46 | 9.1 | 13.65 | 18.2 | 92.5 | 95.1 | 95.8 | 95.9 | 96.2 | 96.2 | 95.9 | 95.3 | 97.1 | 97.6 | 97.7 | 97.8 | 97.8 | 97.6 | 95.8 | 97.4 | 97.9 | 98.2 | 98.2 | 98.2 | 98 |  | 2018-05-01
Schneider Electric Solar Inverters USA, Inc. | Conext CL 25000NA | 25 kW, 422-528 Vac, 3-phase Utility Interactive Inverter | 25 | 422-528 | 98 | Y | N |  | 1.2 |  |  | 500 | 720 | 800 | 2.5 | 5 | 7.5 | 12.5 | 18.75 | 25 | 94.8 | 96.5 | 96.8 | 97 | 97.1 | 97.1 | 96.9 | 97.9 | 98.1 | 98.3 | 98.4 | 98.3 | 98.1 | 98.3 | 96.7 | 97.8 | 98.6 | 98.2 | 98.2 | 98 | 98.1 |  | 2018-05-01
Schneider Electric Solar Inverters USA, Inc. | GT30-208 [208V] | 30 kW, 208 Vac, 3-phase Utility Interactive Inverter | 28.8 | 208 | 96 | Y | N |  | 14.4 |  |  | 180 | 221 | 344 | 2.88 | 5.76 | 8.64 | 14.4 | 21.6 | 28.8 | 96 | 96.9 | 96.9 | 96.8 | 96.3 | 95.7 | 96.5 | 95 | 96.3 | 96.5 | 96.4 | 95.9 | 95.3 | 96 | 91.3 | 94.3 | 95.1 | 95.3 | 95.1 | 94.5 | 94.9 |  | 2018-05-01
Schneider Electric Solar Inverters USA, Inc. | Conext CL-60A | 60 kW Utility Interactive Inverter | 60.391 |  | 98 | Y | N |  | 1.55 |  |  | 550 | 612.5 | 800 | 6.04 | 12.08 | 18.12 | 30.2 | 45.29 | 60.39 | 98.1 | 98.6 | 98.6 | 98.6 | 98.4 | 98.2 | 98.4 | 97.6 | 98.2 | 98.6 | 98.4 | 98.2 | 97.9 | 98.2 | 96.7 | 97.6 | 97.9 | 98 | 97.8 | 97.4 | 97.8 | 2017-05 | 2018-05-01
Schneider Electric Solar Inverters USA, Inc. | GT100-208 [208V] | 100 kW, 208 Vac 3-phase Utility Interactive Inverter | 100 | 208 | 95 | Y | N |  | 95 | 100 | 95 | 300 | 345 | 480 | 10 | 20 | 30 | 50 | 75 | 100 | 90.8 | 94.6 | 95.5 | 96.2 | 96.2 | 95.9 | 95.8 | 89.7 | 93.9 | 94.9 | 95.7 | 95.7 | 95.5 | 95.3 | 86.8 | 92.2 | 93.6 | 94.7 | 94.9 | 94.9 | 94.3 |  | 2018-05-01
Schneider Electric Solar Inverters USA, Inc. | GT100-208-PG [208V] | 100 kW, 208 Vac, 3-phase Utility Interactive Inverter, positive ground | 100 | 208 | 95 | Y | N |  | 95 | 100 | 95 | 300 | 345 | 480 | 10 | 20 | 30 | 50 | 75 | 100 | 90.8 | 94.6 | 95.5 | 96.2 | 96.2 | 95.9 | 95.8 | 89.7 | 93.9 | 94.9 | 95.7 | 95.7 | 95.5 | 95.3 | 86.8 | 92.2 | 93.6 | 94.7 | 94.9 | 94.9 | 94.3 |  | 2018-05-01
Schneider Electric Solar Inverters USA, Inc. | GT100-480 [480V] | 100 kW, 480 Vac, 3-phase Utility Interactive Inverter | 100 | 480 | 96 | Y | N |  | 92 | 100 | 92 | 300 | 345 | 480 | 10 | 20 | 30 | 50 | 75 | 100 | 92.4 | 95.4 | 96.3 | 96.7 | 96.7 | 96.4 | 96.4 | 91.5 | 94.8 | 95.8 | 96.3 | 96.3 | 95.9 | 96 | 88.8 | 93.4 | 94.7 | 95.5 | 95.7 | 95.2 | 95.1 |  | 2018-05-01
Schneider Electric Solar Inverters USA, Inc. | GT100-480-PG [480V] | 100 kW, 480 Vac, 3-phase Utility Interactive Inverter, positive ground | 100 | 480 | 96 | Y | N |  | 92 | 100 | 92 | 300 | 345 | 480 | 10 | 20 | 30 | 50 | 75 | 100 | 92.4 | 95.4 | 96.3 | 96.7 | 96.7 | 96.4 | 96.4 | 91.5 | 94.8 | 95.8 | 96.3 | 96.3 | 95.9 | 96 | 88.8 | 93.4 | 94.7 | 95.5 | 95.7 | 95.2 | 95.1 |  | 2018-05-01
Schneider Electric Solar Inverters USA, Inc. | GT250-480 [480V] | 250 kW, 480 Vac, 3-phase Utility Interactive Inverter | 250 | 480 | 96 | Y | N |  | 34 | 250 | 34 | 300 | 345 | 480 | 25 | 50 | 75 | 125 | 187.5 | 250 | 94 | 96.2 | 96.8 | 96.8 | 96.5 | 95.9 | 96.5 | 93.4 | 95.6 | 96.3 | 96.4 | 96.1 | 95.5 | 96 | 91.6 | 94.6 | 95.4 | 95.7 | 95.5 | 94.9 | 95.3 |  | 2018-05-01
Schneider Electric Solar Inverters USA, Inc. | GT250-480-PG [480V] | 250 kW, 480 Vac, 3-phase Utility Interactive Inverter, positive ground | 250 | 480 | 96 | Y | N |  | 34 | 250 | 34 | 300 | 345 | 480 | 25 | 50 | 75 | 125 | 187.5 | 250 | 94 | 96.2 | 96.8 | 96.8 | 96.5 | 95.9 | 96.5 | 93.4 | 95.6 | 96.3 | 96.4 | 96.1 | 95.5 | 96 | 91.6 | 94.6 | 95.4 | 95.7 | 95.5 | 94.9 | 95.3 |  | 2018-05-01
Schneider Electric Solar Inverters USA, Inc. | GT500-480 [480V] | 500 kW, 480 Vac, 3-phase Utility Interactive Inverter | 500 | 480 | 96 | Y | N |  | 335.8 | 500 | 335.8 | 310 | 353 | 480 | 50 | 100 | 150 | 250 | 375 | 500 | 93.8 | 96.5 | 96.9 | 96.9 | 96.7 | 96.2 | 96.6 | 92.9 | 95.9 | 96.5 | 96.6 | 96.3 | 95.9 | 96.2 | 90 | 94.5 | 95.5 | 95.9 | 95.8 | 95.4 | 95.5 |  | 2018-05-01
Schneider Electric Solar Inverters USA, Inc. | GT500-480-PG [480V] | 500 kW, 480 Vac, 3-phase Utility Interactive Inverter, positive ground | 500 | 480 | 96 | Y | N |  | 335.8 | 500 | 335.8 | 310 | 353 | 480 | 50 | 100 | 150 | 250 | 375 | 500 | 93.8 | 96.5 | 96.9 | 96.9 | 96.7 | 96.2 | 96.6 | 92.9 | 95.9 | 96.5 | 96.6 | 96.3 | 95.9 | 96.2 | 90 | 94.5 | 95.5 | 95.9 | 95.8 | 95.4 | 95.5 |  | 2018-05-01
Schneider Electric Solar Inverters USA, Inc. | GT500-MVX | 500 kW, 3-phase Inverter for medium voltage applications | 500 |  | 95.5 | Y | N | Weighted Efficiency includes MV TP1 Transformer efficiency. | 161 |  |  | 310 | 354 | 480 | 50 | 100 | 150 | 250 | 375 | 500 | 93.7 | 96.3 | 96.7 | 96.7 | 96.1 | 94.9 | 96.2 | 93 | 95.8 | 96.3 | 96.4 | 95.9 | 94.6 | 95.8 | 90 | 94.5 | 95.4 | 95.7 | 95.3 | 94.1 | 95.1 |  | 2018-06-01
Schneider Electric Solar Inverters USA, Inc. | GT500-MVX-PG | 500 kW, 3-phase Inverter for medium voltage applications, positive ground | 500 |  | 95.5 | Y | N | Weighted Efficiency includes MV TP1 Transformer efficiency. | 161 |  |  | 310 | 354 | 480 | 50 | 100 | 150 | 250 | 375 | 500 | 93.7 | 96.3 | 96.7 | 96.7 | 96.1 | 94.9 | 96.2 | 93 | 95.8 | 96.3 | 96.4 | 95.9 | 94.6 | 95.8 | 90 | 94.5 | 95.4 | 95.7 | 95.3 | 94.1 | 95.1 |  | 2018-06-01
Schneider Electric Solar Inverters USA, Inc. | Conext Core XC540-NA | Utility Interactive Photovoltaic Inverter to be used with ABB EcoDry Ultra Transformer | 540 |  | 97 | N | N |  | 196 |  |  | 439 | 529 | 800 | 54 | 108 | 162 | 270 | 405 | 540 | 95.4828 | 97.3332 | 97.7081 | 97.7999 | 97.6167 | 96.8773 | 97.5296 | 95.4218 | 97.0344 | 97.4169 | 97.4748 | 97.285 | 96.6512 | 97.2219 | 93.463 | 96.0098 | 96.6481 | 96.8949 | 96.7092 | 96.0827 | 96.5447 |  | 2018-05-01
Schneider Electric Solar Inverters USA, Inc. | Conext Core XC630-NA | Utility Interactive Photovoltaic Inverter to be used with ABB EcoDry Ultra Transformer | 630 |  | 97.5 | N | N |  | 200 |  |  | 510 | 582 | 800 | 63 | 126 | 189 | 315 | 472.5 | 630 | 95.5924 | 97.6798 | 97.9802 | 97.9365 | 97.8207 | 97.1378 | 97.7339 | 95.944 | 97.5335 | 97.7412 | 97.738 | 97.4997 | 96.8007 | 97.4832 | 94.3888 | 96.6615 | 97.1405 | 97.2963 | 97.0892 | 96.412 | 96.9756 |  | 2018-05-01
Schneider Electric Solar Inverters USA, Inc. | Conext Core XC680-NA | Utility Interactive Photovoltaic Inverter to be used with ABB EcoDry Ultra Transformer | 680 |  | 97.5 | N | N |  | 203 |  |  | 552 | 614 | 800 | 68 | 136 | 204 | 340 | 510 | 680 | 96.7326 | 97.5927 | 98.0772 | 98.1669 | 97.8751 | 97.5268 | 97.8834 | 96.2312 | 97.4394 | 97.7416 | 97.8243 | 97.6143 | 97.1701 | 97.5874 | 94.9986 | 96.6345 | 97.1536 | 97.4238 | 97.2347 | 96.8261 | 97.1248 |  | 2018-05-01
Schneider Electric Solar Inverters USA, Inc. | Conext Core XC733-NA | Utility Interactive Photovoltaic Inverter to be used with ABB EcoDry Ultra Transformer | 730.9 |  | 97.5 | N | N |  | 203 |  |  | 591 | 644 | 800 | 73.09 | 146.18 | 219.27 | 365.45 | 548.175 | 730.9 | 96.0765 | 97.8522 | 98.1843 | 98.2455 | 98.0218 | 97.5302 | 97.9774 | 95.721 | 97.5881 | 97.9165 | 97.997 | 97.7627 | 97.2498 | 97.7143 | 94.9928 | 97.1688 | 97.6099 | 97.7279 | 97.5155 | 97.0024 | 97.4276 |  | 2018-05-01
Schneider Electric Solar Inverters USA, Inc. | CS1666-1-NA [575V] | 1.66 MW, 1500 Vdc, 575 Vac, 3-phase, Special Purpose Utility Interactive PV Inverter with 1666 kVA Maximum Output Continuous Apparent Power | 1666 | 575 | 98 | N | N | Weighted Efficiency includes efficiency of 2.0 MVA Square D 3PH distribution transformer, liquid-filled type. | 295 |  |  | 856 | 1024 | 1200 | 167 | 333 | 500 | 833 | 1250 | 1666 | 96.79 | 97.94 | 98.09 | 98.15 | 97.94 | 97.66 | 97.9 | 96.33 | 97.56 | 97.92 | 98.08 | 97.88 | 97.52 | 97.8 | 95.68 | 97.45 | 97.7 | 97.9 | 97.74 | 97.44 | 97.7 | 2018-08-15 | 2018-10-15
Schneider Electric Solar Inverters USA, Inc. | CS1666-2-NA [575V] | 1.66 MW, 1500 Vdc, 575 Vac, 3-phase, Special Purpose Utility Interactive PV Inverter with 1831 kVA Maximum Output Continuous Apparent Power | 1666 | 575 | 98 | N | N | Weighted Efficiency includes efficiency of 2.0 MVA Square D 3PH distribution transformer, liquid-filled type. | 295 |  |  | 856 | 1024 | 1200 | 167 | 333 | 500 | 833 | 1250 | 1666 | 96.79 | 97.94 | 98.09 | 98.15 | 97.94 | 97.66 | 97.9 | 96.33 | 97.56 | 97.92 | 98.08 | 97.88 | 97.52 | 97.8 | 95.68 | 97.45 | 97.7 | 97.9 | 97.74 | 97.44 | 97.7 | 2018-08-15 | 2018-10-15
Schneider Electric Solar Inverters USA, Inc. | CS1666-3-NA [575V] | 1.66 MW, 1500 Vdc, 575 Vac, 3-phase, Special Purpose Utility Interactive PV Inverter with 1851 kVA Maximum Output Continuous Apparent Power | 1666 | 575 | 98 | N | N | Weighted Efficiency includes efficiency of 2.0 MVA Square D 3PH distribution transformer, liquid-filled type. | 295 |  |  | 856 | 1024 | 1200 | 167 | 333 | 500 | 833 | 1250 | 1666 | 96.79 | 97.94 | 98.09 | 98.15 | 97.94 | 97.66 | 97.9 | 96.33 | 97.56 | 97.92 | 98.08 | 97.88 | 97.52 | 97.8 | 95.68 | 97.45 | 97.7 | 97.9 | 97.74 | 97.44 | 97.7 | 2018-08-15 | 2018-10-15
Schneider Electric Solar Inverters USA, Inc. | CS1800-NA [575V] | 1.8 MW, 1500 Vdc, 575 Vac, 3-phase, Special Purpose Utility Interactive PV Inverter | 1800 | 575 | 98 | N | N | Weighted Efficiency includes efficiency of 2.0 MVA Square D 3PH distribution transformer, liquid-filled type. | 295 |  |  | 856 | 1024 | 1200 | 180 | 360 | 540 | 900 | 1350 | 1800 | 96.89 | 97.93 | 98.08 | 98.11 | 97.92 | 97.47 | 97.9 | 96.67 | 97.74 | 98 | 97.99 | 97.8 | 97.45 | 97.8 | 95.89 | 97.43 | 97.67 | 97.87 | 97.7 | 97.34 | 97.6 | 2018-08-15 | 2018-10-15
Schneider Electric Solar Inverters USA, Inc. | CS2000-NA [575V] | 2 MW, 1500 Vdc, 575 Vac, 3-phase, Special Purpose Utility Interactive PV Inverter | 2000 | 575 | 97.5 | N | N | Formerly Schneider Electric Solar Inverters USA, Inc. Conext SmartGen CS2000-NA. Weighted Efficiency includes efficiency of 2000 KVA Square D 3PH distribution transformer, liquid-filled type (40425642-006-S09-01). | 295 |  |  | 865 | 1042 | 1195 | 200 | 400 | 600 | 1000 | 1500 | 2000 | 96.76 | 97.71 | 97.98 | 97.96 | 97.66 | 97.21 | 97.71 | 96.32 | 97.58 | 97.87 | 97.83 | 97.56 | 97.15 | 97.58 | 95.92 | 97.38 | 97.69 | 97.72 | 97.5 | 97.06 | 97.48 | 2018-08-15 | 2018-10-15
Schneider Electric Solar Inverters USA, Inc. | CS2200-NA [600V] | 2.2 MW, 1500 Vdc, 600 Vac, 3-phase, Special Purpose Utility Interactive PV Inverter | 2200 | 600 | 98 | N | N | Weighted Efficiency includes efficiency of 2.5 MVA Square D 3PH distribution transformer, liquid-filled type. | 295 |  |  | 905 | 1054 | 1200 | 220 | 440 | 660 | 1100 | 1650 | 2200 | 97.9 | 98.28 | 98.33 | 98.2 | 97.82 | 97.24 | 98 | 97.6 | 98.1 | 98.19 | 98.09 | 97.72 | 97.17 | 97.8 | 97.21 | 97.9 | 98.05 | 97.99 | 97.65 | 97.1 | 97.7 | 2018-08-15 | 2018-10-15
Schneider Electric Solar Inverters USA, Inc. | CS2400-NA [600V] | 2.2 MW, 2.4 MVA, 1500Vdc, 600Vac, 3-ph Special Purpose Utility Interactive PV Inverter | 2200 | 600 | 98 | N | N | Weighted Efficiency includes efficiency of 2.5 MVA Square D 3PH distribution transformer, liquid-filled type. | 295 |  |  | 900 | 1054 | 1200 | 220 | 440 | 660 | 1100 | 1650 | 2200 | 97.4147 | 98.1198 | 98.251 | 98.2091 | 97.9143 | 97.4561 | 97.984 | 97.4181 | 98.0355 | 98.1755 | 98.1244 | 97.8109 | 97.3036 | 97.8907 | 97.0277 | 97.8316 | 98.0273 | 98.0302 | 97.7384 | 97.2377 | 97.7855 | 2018-11-01
Schuco USA | SB700U [120V] | 700W, 120Vac Sunny Boy String Inverter | 0.7 | 120 | 91.5 | Y | N |  | 0.0357 |  |  | 100 | 145 | 200 | 0.07 | 0.14 | 0.21 | 0.35 | 0.53 | 0.7 | 87.17 | 91.46 | 92.68 | 92.98 | 92.42 | 91.45 | 92.26 | 86.53 | 91.26 | 92.47 | 92.32 | 91.44 | 90.36 | 91.49 | 84.83 | 90.18 | 91.07 | 91.63 | 91.03 | 90.2 | 90.83
Schuco USA | SB700U-SBD [120V] | 700W, 120Vac Sunny Boy String Inverter with display | 0.7 | 120 | 91.5 | Y | N |  | 0.0357 |  |  | 100 | 145 | 200 | 0.07 | 0.14 | 0.21 | 0.35 | 0.53 | 0.7 | 87.17 | 91.46 | 92.68 | 92.98 | 92.42 | 91.45 | 92.26 | 86.53 | 91.26 | 92.47 | 92.32 | 91.44 | 90.36 | 91.49 | 84.83 | 90.18 | 91.07 | 91.63 | 91.03 | 90.2 | 90.83
Schuco USA | SWR1800U [120V] | 1.8kW, 120Vac Sunny Boy String Inverter | 1.8 | 120 | 91.5 | Y | N |  | 0.2659 |  |  | 100 | 200 | 400 | 0.18 | 0.36 | 0.54 | 0.9 | 1.35 | 1.8 | 89.82 | 92.39 | 93.01 | 92.83 | 91.99 | 91 | 92.17 | 89.56 | 92.12 | 92.82 | 92.7 | 91.72 | 90.8 | 91.95 | 86.79 | 90.45 | 91.44 | 91.78 | 91.18 | 90.3 | 91.08
Schuco USA | SWR1800U-SBD [120V] | 1.8kW, 120Vac Sunny Boy String Inverter with display | 1.8 | 120 | 91.5 | Y | N |  | 0.2659 |  |  | 100 | 200 | 400 | 0.18 | 0.36 | 0.54 | 0.9 | 1.35 | 1.8 | 89.82 | 92.39 | 93.01 | 92.83 | 91.99 | 91 | 92.17 | 89.56 | 92.12 | 92.82 | 92.7 | 91.72 | 90.8 | 91.95 | 86.79 | 90.45 | 91.44 | 91.78 | 91.18 | 90.3 | 91.08
Schuco USA | SWR2100U [240V] | 2.1kW, 240 Vac Sunny Boy String Inverter | 2.1 | 240 | 93 | Y | N |  | 0.32 |  |  | 100 | 300 | 480 | 0.21 | 0.42 | 0.63 | 1.05 | 1.575 | 2.1 | 91.2 | 93.6 | 94.3 | 94.3 | 93.9 | 93.3 | 93.9 | 90.2 | 92.7 | 93.5 | 94.5 | 93.7 | 93.1 | 93.6 | 86 | 89.9 | 91.3 | 92.1 | 92.3 | 91.8 | 91.8
Schuco USA | SWR2500U [208V] | 2.1kW, 208 Vac Sunny Boy String Inverter, with display | 2.1 | 208 | 92.5 | Y | N |  | 0.236 |  |  | 100 | 300 | 480 | 0.21 | 0.42 | 0.63 | 1.05 | 1.58 | 2.1 | 90.86 | 93.44 | 94.02 | 93.86 | 93.06 | 92.06 | 93.22 | 89.33 | 92.49 | 93.07 | 93.3 | 92.57 | 91.52 | 92.6 | 85.59 | 89.83 | 91.11 | 91.75 | 91.25 | 90.64 | 91.01
Schuco USA | SWR2500U-SBD [208V] | 2.1kW, 208 Vac Sunny Boy String Inverter with display | 2.1 | 208 | 92.5 | Y | N |  | 0.236 |  |  | 100 | 300 | 480 | 0.21 | 0.42 | 0.63 | 1.05 | 1.58 | 2.1 | 90.86 | 93.44 | 94.02 | 93.86 | 93.06 | 92.06 | 93.22 | 89.33 | 92.49 | 93.07 | 93.3 | 92.57 | 91.52 | 92.6 | 85.59 | 89.83 | 91.11 | 91.75 | 91.25 | 90.64 | 91.01
Schuco USA | SWR2500U [240V] | 2.5 kW, 240 Vac Sunny Boy String Inverter | 2.5 | 240 | 93 | Y | N |  | 0.318 |  |  | 100 | 300 | 480 | 0.25 | 0.5 | 0.75 | 1.25 | 1.88 | 2.5 | 91.03 | 93.93 | 94.57 | 94.53 | 93.9 | 93.26 | 93.97 | 89.79 | 93.21 | 93.89 | 94.15 | 93.66 | 92.89 | 93.57 | 86.28 | 90.48 | 91.91 | 92.59 | 92.33 | 91.84 | 91.98
Schuco USA | SWR2500U-SBD [240V] | 2.5 kW, 240 Vac Sunny Boy String Inverter with display | 2.5 | 240 | 93 | Y | N |  | 0.318 |  |  | 100 | 300 | 480 | 0.25 | 0.5 | 0.75 | 1.25 | 1.88 | 2.5 | 91.03 | 93.93 | 94.57 | 94.53 | 93.9 | 93.26 | 93.97 | 89.79 | 93.21 | 93.89 | 94.15 | 93.66 | 92.89 | 93.57 | 86.28 | 90.48 | 91.91 | 92.59 | 92.33 | 91.84 | 91.98
Schuco USA | SB3000US [208V] | 3 kW, 208 Vac Sunny Boy Utility Interactive Inverter with display | 3 | 208 | 95 | Y | N |  | 0.08 |  |  | 100 | 250 | 400 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 94 | 95.8 | 96 | 95.8 | 95.1 | 94.3 | 95.3 | 93.1 | 95.9 | 95.7 | 95.6 | 94.9 | 94 | 95.1 | 91.6 | 94.8 | 95.2 | 94.7 | 94.2 | 93.5 | 94.3
Schuco USA | SB3000US [240V] | 3 kW, 240 Vac Sunny Boy Utility Interactive Inverter with display | 3 | 240 | 95.5 | Y | N |  | 0.07 |  |  | 100 | 250 | 400 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 93.4 | 95.9 | 96.3 | 96.5 | 96.1 | 95.6 | 96 | 92.5 | 95.8 | 96 | 96.1 | 95.8 | 95.1 | 95.7 | 90.5 | 94.6 | 95.4 | 95.3 | 95.2 | 94.6 | 95
Schuco USA | SB3300U [240V] | 3.3 kW, 240 Vac Sunny Boy Utility Interactive Inverter with display | 3.3 | 240 | 94.5 | Y | N |  | 0.16 |  |  | 100 | 250 | 400 | 0.33 | 0.66 | 0.99 | 1.65 | 2.48 | 3.3 | 92.6 | 94.6 | 95.2 | 95.4 | 95.2 | 94.6 | 95.1 | 91.8 | 94.1 | 94.8 | 95.1 | 94.9 | 94.5 | 94.7 | 89.2 | 92.4 | 93.6 | 94 | 93.9 | 93.5 | 93.6
Schuco USA | SB3800U [208V] | 3.5 kW, 208 Vac Sunny Boy Utility Interactive Inverter with display | 3.5 | 208 | 94 | Y | N |  | 0.16 |  |  | 100 | 235 | 400 | 0.35 | 0.7 | 1.05 | 1.75 | 2.63 | 3.5 | 93.6 | 94.9 | 95.2 | 94.9 | 94.1 | 93.3 | 94.4 | 92.8 | 94.5 | 94.8 | 94.6 | 94 | 93 | 94.1 | 90.3 | 92.7 | 93.4 | 93.5 | 93.1 | 92.2 | 93
Schuco USA | SB4000US [208V] | 4 kW, 208 Vac Sunny Boy Utility Interactive Inverter with display | 3.5 | 208 | 95.5 | Y | N |  | 0.14 |  |  | 100 | 310 | 480 | 0.35 | 0.7 | 1.05 | 1.75 | 2.63 | 3.5 | 94.3 | 96.3 | 96.5 | 96.4 | 95.8 | 94.9 | 95.9 | 93.5 | 96.2 | 96.1 | 96.1 | 95.5 | 94.8 | 95.6 | 91.5 | 94.9 | 95.4 | 95.1 | 94.8 | 94 | 94.7
Schuco USA | SB3800U [240V] | 3.8kW, 240 Vac Sunny Boy Utility Interactive Inverter with display | 3.8 | 240 | 94.5 | Y | N |  | 0.16 |  |  | 100 | 250 | 400 | 0.38 | 0.76 | 1.14 | 1.9 | 2.85 | 3.8 | 93.3 | 95 | 95.5 | 95.4 | 95 | 94.3 | 95 | 92.8 | 94.6 | 95.1 | 95.1 | 94.7 | 93.8 | 94.7 | 90.2 | 93 | 93.9 | 94.1 | 93.8 | 93.2 | 93.7
Schuco USA | SB4000US [240V] | 4 kW, 240 Vac Sunny Boy Utility Interactive Inverter with display | 4 | 240 | 96 | Y | N |  | 0.17 |  |  | 100 | 310 | 480 | 0.4 | 0.8 | 1.2 | 2 | 3 | 4 | 92.5 | 96.4 | 96.8 | 96.7 | 96.4 | 96 | 96.3 | 91.9 | 96.2 | 96.3 | 96.5 | 96 | 95.5 | 96 | 89.1 | 94.7 | 95.6 | 95.5 | 95.3 | 94.9 | 95.1
Schuco USA | SB5000US [208V] | 5 kW, 208 Vac Sunny Boy Utility Interactive Inverter with display | 5 | 208 | 95.5 | Y | N |  | 0.46 |  |  | 100 | 310 | 480 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 91.5 | 95.7 | 96.2 | 96.7 | 96.7 | 96.3 | 96.4 | 89.9 | 95 | 95.7 | 96.2 | 96.4 | 96 | 95.9 | 86.3 | 92.5 | 94.3 | 95 | 95.1 | 95 | 94.5
Schuco USA | SB5000US [240V] | 5 kW, 240 Vac Sunny Boy Utility Interactive Inverter with display | 5 | 240 | 95.5 | Y | N |  | 0.72 |  |  | 100 | 310 | 480 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 91 | 95.7 | 96.2 | 96.8 | 96.8 | 96.5 | 96.4 | 89.7 | 94.9 | 95.7 | 96.2 | 96.4 | 96.2 | 95.9 | 86.2 | 92.5 | 94.3 | 95.2 | 95.2 | 95.1 | 94.6
Schuco USA | SB5000US [277V] | 5 kW, 277 Vac Sunny Boy Utility Interactive Inverter with display | 5 | 277 | 95.5 | Y | N |  | 1.41 |  |  | 100 | 310 | 480 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 91.5 | 95.8 | 96.5 | 96.8 | 96.5 | 96.6 | 96.3 | 90 | 95 | 95.8 | 96.2 | 96.5 | 96.2 | 96 | 86.3 | 92.3 | 94.4 | 95.2 | 95.2 | 95.2 | 94.6
Schuco USA | SB6000U [208V] | Sunny Boy 6000 Watt (208V) Utility Interactive Inverter with Meter | 5.2 | 208 | 94.5 | Y | N |  | 0.2 |  |  | 100 | 334 | 480 | 0.57 | 1.11 | 1.63 | 2.7 | 4.01 | 5.32 | 93.1 | 95.2 | 95.6 | 95.6 | 94.8 | 94.2 | 95 | 91.6 | 94.7 | 95.2 | 95.3 | 94.6 | 93.8 | 94.7 | 88.6 | 92.3 | 93.5 | 93.9 | 93.7 | 93.1 | 93.4
Schuco USA | SB6000U [240V] | Sunny Boy 6000 Watt (240V) Utility Interactive Inverter with Meter | 6 | 240 | 94.5 | Y | N |  | 0.2 |  |  | 100 | 310 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 93.2 | 95.5 | 95.8 | 95.5 | 94.9 | 94.2 | 95 | 92.3 | 94.9 | 95.2 | 95.2 | 94.6 | 93.8 | 94.7 | 90.1 | 93.3 | 94.1 | 94.3 | 93.9 | 93.2 | 93.8
Schuco USA | SB6000U [277V] | Sunny Boy 6000 Watt (277V) Utility Interactive Inverter with Meter | 6 | 277 | 94.5 | Y | N |  | 0.23 |  |  | 100 | 310 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 93.1 | 95.2 | 95.9 | 95.6 | 95.2 | 94.5 | 95.2 | 91.9 | 94.8 | 95.4 | 95.2 | 94.8 | 94.2 | 94.8 | 89.8 | 93.2 | 94.1 | 94.4 | 94 | 93.4 | 93.9
Schuco USA | SB6000US [208V] | 6 kW, 208 Vac Sunny Boy Utility Interactive Inverter with display | 6 | 208 | 95.5 | Y | N |  | 0.46 |  |  | 100 | 310 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 92.5 | 95.8 | 96.5 | 96.9 | 96.5 | 95.9 | 96.3 | 91.2 | 95.6 | 95.9 | 96.3 | 96.1 | 95.6 | 95.9 | 88 | 93.5 | 94.8 | 94.6 | 94.9 | 94.6 | 94.5
Schuco USA | SB6000US [240V] | 6 kW, 240 Vac Sunny Boy Utility Interactive Inverter with display | 6 | 240 | 95.5 | Y | N |  | 0.72 |  |  | 100 | 310 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 92.6 | 96.1 | 96.5 | 96.8 | 96.7 | 96 | 96.4 | 91.3 | 95.6 | 96 | 96.3 | 96.3 | 95.9 | 96 | 87.9 | 93.6 | 94.8 | 95.1 | 95 | 94.8 | 94.7
Schuco USA | SB6000US [277V] | 6 kW, 277 Vac Sunny Boy Utility Interactive Inverter with display | 6 | 277 | 96 | Y | N |  | 1.41 |  |  | 100 | 310 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 92.3 | 96 | 96.7 | 97 | 96.7 | 96.5 | 96.5 | 91.3 | 95.6 | 96.2 | 96.4 | 96.4 | 96 | 96.1 | 87.8 | 93.6 | 94.9 | 95.2 | 95.1 | 94.9 | 94.7
Schuco USA | SB7000US [208V] | 7 kW, 208 Vac Sunny Boy Utility Interactive Inverter with display | 7 | 208 | 95.5 | Y | N |  | 0.46 |  |  | 100 | 310 | 480 | 0.7 | 1.4 | 2.1 | 3.5 | 5.25 | 7 | 94 | 96.3 | 97.1 | 96.7 | 96.2 | 95.4 | 96.3 | 92.7 | 96.1 | 96.1 | 96.2 | 95.9 | 95.3 | 95.9 | 89.7 | 94.2 | 95 | 94.9 | 94.8 | 94.1 | 94.6
Schuco USA | SB7000US [240V] | 7 kW, 240 Vac Sunny Boy Utility Interactive Inverter with display | 7 | 240 | 96 | Y | N |  | 0.72 |  |  | 100 | 310 | 480 | 0.7 | 1.4 | 2.1 | 3.5 | 5.25 | 7 | 93.7 | 96.2 | 96.8 | 96.9 | 96.5 | 95.8 | 96.5 | 92.3 | 96.1 | 96.1 | 96.4 | 96.1 | 95.6 | 96 | 89.3 | 94.3 | 95.1 | 95.6 | 95 | 94.7 | 94.8
Schuco USA | SB7000US [277V] | 7 kW, 277 Vac Sunny Boy Utility Interactive Inverter with display | 7 | 277 | 96 | Y | N |  | 1.41 |  |  | 100 | 310 | 480 | 0.7 | 1.4 | 2.1 | 3.5 | 5.25 | 7 | 93.7 | 96.3 | 96.8 | 97 | 96.5 | 95.9 | 96.5 | 92.5 | 96.1 | 96.3 | 96.5 | 96.2 | 95.6 | 96.1 | 89.3 | 94.2 | 95.2 | 95 | 95.1 | 94.6 | 94.8
Schuco USA | SB8000US [240V] | 8kW, 240 Vac Sunny Boy Utility Interactive Inverter with display | 7.6 | 240 | 96 | Y | N |  | 0.17 |  |  | 100 | 345 | 480 | 0.76 | 1.52 | 2.28 | 3.8 | 5.7 | 7.6 | 95.04 | 96.48 | 96.84 | 96.82 | 96.5 | 96.01 | 96.53 | 94.59 | 96.19 | 96.61 | 96.63 | 96.3 | 96.29 | 96.33 | 93.13 | 95.28 | 95.83 | 95.98 | 95.72 | 95.94 | 95.67
Schuco USA | SB8000US [277V] | 8kW, 277 Vac Sunny Boy Utility Interactive Inverter with display | 8 | 277 | 96 | Y | N |  | 0.15 |  |  | 100 | 345 | 480 | 0.8 | 1.6 | 2.4 | 4 | 6 | 8 | 95.12 | 96.22 | 96.48 | 96.46 | 96.17 | 95.56 | 96.2 | 94.85 | 95.86 | 96.28 | 96.25 | 95.89 | 95.28 | 95.93 | 93.45 | 95.01 | 95.41 | 95.51 | 95.24 | 94.7 | 95.21
Schuco USA | ST42 [208V] | 42 kW, 208 Vac Sunny Tower Utility Interactive Inverter with display | 42 | 208 | 95.5 | Y | N |  | 0.46 |  |  | 250 | 310 | 480 | 4.2 | 8.4 | 12.6 | 21 | 31.5 | 42 | 94 | 96.3 | 97.1 | 96.7 | 96.2 | 95.4 | 96.3 | 92.7 | 96.1 | 96.1 | 96.2 | 95.9 | 95.3 | 95.9 | 89.7 | 94.2 | 95 | 94.9 | 94.8 | 94.1 | 94.6
Schuco USA | ST42 [277V] | 42 kW, 277 Vac Sunny Tower Utility Interactive Inverter with display | 42 | 277 | 96 | Y | N |  | 1.41 |  |  | 250 | 310 | 480 | 4.2 | 8.4 | 12.6 | 21 | 31.5 | 42 | 93.7 | 96.3 | 96.8 | 97 | 96.5 | 95.9 | 96.5 | 92.5 | 96.1 | 96.3 | 96.5 | 96.2 | 95.6 | 96.1 | 89.3 | 94.2 | 95.2 | 95 | 95.1 | 94.6 | 94.8
Sharp | JH-3500U [240V] | Utility Interactive Inverter 240 Vac L-L, 3.5 kW | 3.5 | 240 | 91 | Y | N |  | 0.65 |  |  | 100 | 276 | 304 | 0.35 | 0.7 | 1.05 | 1.75 | 2.63 | 3.5 | 75 | 83.1 | 87.1 | 90.3 | 91.5 | 92 | 89.7 | 80.9 | 87.8 | 90.6 | 91.7 | 92.6 | 92.4 | 91.5 | 83.3 | 87.8 | 90.7 | 92.2 | 92.7 | 92.7 | 91.7
Shenzhen BYD | BSG5000-U [240V] | 4.9 kW 240 Vac Utility Interactive Inverter | 4.88 | 240 | 92.5 | N | N |  | 1.75 |  |  | 100 | 400 | 550 | 0.49 | 0.98 | 1.46 | 2.44 | 3.66 | 4.88 | 89.8 | 93.4 | 94 | 93.9 | 93.2 | 92.1 | 93.2 | 87.7 | 92.1 | 93.3 | 93.5 | 92.9 | 91.8 | 92.8 | 85.8 | 90.7 | 92.3 | 93 | 92.2 | 91.9 | 92.1
Shenzhen BYD | BSG5000-U [208V] | 4.9 kW 208 Vac Utility Interactive Inverter | 4.91 | 208 | 92.5 | N | N |  | 1.32 |  |  | 100 | 400 | 550 | 0.49 | 0.98 | 1.47 | 2.46 | 3.69 | 4.91 | 89.8 | 93.1 | 93.9 | 93.6 | 92.8 | 91.6 | 92.9 | 87 | 91.8 | 93 | 93.3 | 92.6 | 91.5 | 92.4 | 84.4 | 91 | 92 | 92.6 | 92.1 | 91 | 91.8
Shenzhen BYD | BSG250K-U | 250 kW Utility Interactive Inverter | 250.4 |  | 95 | N | N |  | 151 |  |  | 330 | 370 | 480 | 25.04 | 50.07 | 75.11 | 125.2 | 187.8 | 250.4 | 90.1 | 94.4 | 95.5 | 96.4 | 95.7 | 95.3 | 95.5 | 89.1 | 93.9 | 95.1 | 95.6 | 95.9 | 95.7 | 95.4 | 87.1 | 92.6 | 94.2 | 94.8 | 95.3 | 95 | 94.6
Shenzhen BYD | BSG250K-U/N | 250 kW Utility Interactive Inverter | 250.4 |  | 95 | N | N |  | 151 |  |  | 330 | 370 | 480 | 25.04 | 50.07 | 75.11 | 125.2 | 187.8 | 250.4 | 90.1 | 94.4 | 95.5 | 96.4 | 95.7 | 95.3 | 95.5 | 89.1 | 93.9 | 95.1 | 95.6 | 95.9 | 95.7 | 95.4 | 87.1 | 92.6 | 94.2 | 94.8 | 95.3 | 95 | 94.6
Shenzhen Growatt New Energy Technology Co., Ltd | Growatt 1500-US [208V] | 1500 W 208 Vac Utility Interactive Inverter | 1.5 | 208 | 96 | Y | N |  | 0.07 |  |  | 100 | 330 | 360 | 0.15 | 0.3 | 0.45 | 0.75 | 1.13 | 1.5 | 91.1 | 94.9 | 96 | 96.4 | 96.2 | 96 | 95.9 | 91.7 | 95.5 | 96.5 | 96.8 | 96.7 | 96.5 | 96.4 | 91.5 | 95.2 | 96.2 | 96.7 | 96.7 | 96.5 | 96.3
Shenzhen Growatt New Energy Technology Co., Ltd | Growatt 1500-US [240V] | 1650 W 240 Vac Utility Interactive Inverter | 1.65 | 240 | 96 | Y | N |  | 0.11 |  |  | 100 | 330 | 360 | 0.17 | 0.33 | 0.5 | 0.83 | 1.24 | 1.65 | 89.5 | 94.2 | 95.5 | 96.3 | 96.3 | 96 | 95.8 | 90.2 | 94.7 | 95.9 | 96.6 | 96.6 | 96.5 | 96.2 | 91.3 | 95.4 | 96.5 | 97 | 97 | 96.8 | 96.6
Shenzhen Growatt New Energy Technology Co., Ltd | Growatt 1500-US [277V] | 1650 W 277 Vac Utility Interactive Inverter | 1.65 | 277 | 96 | Y | N |  | 0.13 |  |  | 100 | 330 | 360 | 0.17 | 0.33 | 0.5 | 0.83 | 1.24 | 1.65 | 89.2 | 93.5 | 95 | 96.1 | 96.2 | 96.1 | 95.6 | 89.3 | 94 | 95.6 | 96.4 | 96.6 | 96.7 | 96 | 89.3 | 94.3 | 95.7 | 96.6 | 96.8 | 96.8 | 96.2
Shenzhen Growatt New Energy Technology Co., Ltd | Growatt 2000-US [208V] | 1800 W 208 Vac Utility Interactive Inverter | 1.8 | 208 | 96.5 | Y | N |  | 0.09 |  |  | 100 | 360 | 400 | 0.18 | 0.36 | 0.54 | 0.9 | 1.35 | 1.8 | 92.3 | 95.4 | 96 | 96.4 | 96.3 | 96 | 96.1 | 92.8 | 96 | 96.6 | 96.8 | 96.6 | 96.4 | 96.5 | 92.7 | 95.7 | 96.3 | 96.6 | 96.5 | 96.3 | 96.3
Shenzhen Growatt New Energy Technology Co., Ltd | Growatt 2000HF-US [208V] | 2000 W 208 Vac Utility Interactive Inverter | 2 | 208 | 95.5 | Y | N |  | 0.1 |  |  | 100 | 360 | 450 | 0.2 | 0.4 | 0.6 | 1 | 1.5 | 2 | 90.8 | 93 | 94.9 | 95.6 | 95.3 | 95 | 95 | 91.4 | 94.4 | 95.6 | 96.4 | 96.2 | 95.7 | 95.8 | 90.2 | 93.5 | 95 | 95.8 | 95.7 | 95.3 | 95.3
Shenzhen Growatt New Energy Technology Co., Ltd | Growatt 2000HF-US [240V] | 2000 W 240 Vac Utility Interactive Inverter | 2 | 240 | 95.5 | Y | N |  | 0.12 |  |  | 100 | 360 | 450 | 0.2 | 0.4 | 0.6 | 1 | 1.5 | 2 | 90.1 | 92.5 | 94.5 | 95.9 | 95.8 | 95.3 | 95.2 | 91.3 | 94 | 95.7 | 96.6 | 96.4 | 95.8 | 96 | 89.4 | 92.4 | 95 | 96.1 | 96 | 95.4 | 95.4
Shenzhen Growatt New Energy Technology Co., Ltd | Growatt 2000-US [240V] | 2000 W 240 Vac Utility Interactive Inverter | 2 | 240 | 96.5 | Y | N |  | 0.1 |  |  | 100 | 360 | 400 | 0.2 | 0.4 | 0.6 | 1 | 1.5 | 2 | 91.4 | 94.6 | 95.7 | 96.3 | 96.4 | 96.1 | 96 | 92.9 | 96.1 | 96.8 | 97.1 | 97.1 | 96.9 | 96.9 | 92.3 | 95.8 | 96.6 | 96.9 | 97 | 96.8 | 96.7
Shenzhen Growatt New Energy Technology Co., Ltd | Growatt 2000-US [277V] | 2000 W 277 Vac Utility Interactive Inverter | 2 | 277 | 96.5 | Y | N |  | 0.14 |  |  | 100 | 360 | 400 | 0.2 | 0.4 | 0.6 | 1 | 1.5 | 2 | 89.3 | 93.7 | 95.1 | 96 | 96.3 | 96.1 | 95.7 | 91.1 | 94.8 | 95.9 | 96.5 | 96.8 | 96.8 | 96.3 | 92.9 | 96.1 | 96.9 | 97.3 | 97.4 | 97.3 | 97.1
Shenzhen Growatt New Energy Technology Co., Ltd | Growatt 2500HF-US [208V] | 2500 W 208 Vac Utility Interactive Inverter | 2.5 | 208 | 95.5 | Y | N |  | 0.1 |  |  | 100 | 360 | 450 | 0.25 | 0.5 | 0.75 | 1.25 | 1.88 | 2.5 | 90.2 | 93.3 | 94.6 | 95.4 | 95.4 | 95 | 95 | 91.8 | 94.3 | 95.6 | 96.2 | 96 | 95.6 | 95.7 | 90.7 | 93.7 | 94.9 | 95.8 | 95.6 | 95.2 | 95.3
Shenzhen Growatt New Energy Technology Co., Ltd | Growatt 2500HF-US [240V] | 2500 W 240 Vac Utility Interactive Inverter | 2.5 | 240 | 95.5 | Y | N |  | 0.13 |  |  | 100 | 360 | 450 | 0.25 | 0.5 | 0.75 | 1.25 | 1.88 | 2.5 | 90.2 | 93 | 94.5 | 95.6 | 95.4 | 95 | 95 | 91.4 | 94.1 | 95.7 | 96.3 | 96 | 95.7 | 95.8 | 90.8 | 93.2 | 95 | 95.8 | 95.7 | 95.5 | 95.3
Shenzhen Growatt New Energy Technology Co., Ltd | Growatt 3000-US [208V] | 2500 W 208 Vac Utility Interactive Inverter | 2.5 | 208 | 96.5 | Y | N |  | 0.1 |  |  | 100 | 360 | 400 | 0.25 | 0.5 | 0.75 | 1.25 | 1.88 | 2.5 | 92.3 | 95.4 | 96.2 | 96.5 | 96.2 | 95.8 | 96 | 93.9 | 96.2 | 96.8 | 97 | 96.8 | 96.4 | 96.7 | 92.7 | 95.8 | 96.5 | 96.8 | 96.6 | 96.3 | 96.4
Shenzhen Growatt New Energy Technology Co., Ltd | Growatt 3000-US [240V] | 3000 W 240 Vac Utility Interactive Inverter | 2.8 | 240 | 96.5 | Y | N |  | 0.15 |  |  | 100 | 360 | 400 | 0.28 | 0.56 | 0.84 | 1.4 | 2.1 | 2.8 | 91 | 94.4 | 95.6 | 96.4 | 96.4 | 96.1 | 96 | 94 | 96.6 | 97.1 | 97.5 | 97.4 | 97 | 97.2 | 93.3 | 96.1 | 96.8 | 97.4 | 97.3 | 97 | 97
Shenzhen Growatt New Energy Technology Co., Ltd | Growatt 3000-US [277V] | 3000 W 277 Vac Utility Interactive Inverter | 2.8 | 277 | 96.5 | Y | N |  | 0.19 |  |  | 100 | 360 | 400 | 0.28 | 0.56 | 0.84 | 1.4 | 2.1 | 2.8 | 89.4 | 93.4 | 94.8 | 95.9 | 96.2 | 96 | 95.5 | 91.6 | 95.2 | 96.3 | 96.9 | 97 | 96.8 | 96.6 | 94.1 | 96.6 | 97.3 | 97.7 | 97.6 | 97.4 | 97.4
Shenzhen Growatt New Energy Technology Co., Ltd | Growatt 3000HF-US [208V] | 3000 W 208 Vac Utility Interactive Inverter | 3 | 208 | 95.5 | Y | N |  | 0.1 |  |  | 100 | 360 | 450 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 90.5 | 93.5 | 95.1 | 95.5 | 95.2 | 95.1 | 95 | 91.2 | 94.2 | 95.5 | 96.2 | 95.9 | 95.6 | 95.6 | 90.2 | 93.5 | 95 | 95.9 | 95.7 | 95.4 | 95.3
Shenzhen Growatt New Energy Technology Co., Ltd | Growatt 3000HF-US [240V] | 3000 W 240 Vac Utility Interactive Inverter | 3 | 240 | 95.5 | Y | N |  | 0.14 |  |  | 100 | 360 | 450 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 89.4 | 93.1 | 94.8 | 95.6 | 95.4 | 94.9 | 95 | 91.1 | 94.2 | 95.7 | 96.4 | 96 | 95.5 | 95.8 | 90.4 | 93.6 | 95.2 | 96.1 | 95.7 | 95.4 | 95.4
Shenzhen Growatt New Energy Technology Co., Ltd | Growatt 3600 MTL-US [208V] | 3600W 208 Vac Utility Interactive Inverter | 3.6 | 208 | 97 | Y | N |  | 2.3 |  |  | 100 | 375 | 450 | 0.36 | 0.72 | 1.08 | 1.8 | 2.7 | 3.6 | 91.9 | 94.6 | 95.5 | 96.4 | 96.5 | 96.3 | 96.1 | 94.5 | 96.7 | 97.3 | 97.6 | 97.4 | 97.2 | 97.3 | 93 | 96 | 96.9 | 97.3 | 97.3 | 97.1 | 97
Shenzhen Growatt New Energy Technology Co., Ltd | Growatt 3600 MTL-US [240V] | 3600W 240 Vac Utility Interactive Inverter | 3.6 | 240 | 97 | Y | N |  | 0.31 |  |  | 100 | 375 | 450 | 0.36 | 0.72 | 1.08 | 1.8 | 2.7 | 3.6 | 92.4 | 94.6 | 95.5 | 96.5 | 96.7 | 96.7 | 96.2 | 95.3 | 97.1 | 97.5 | 97.8 | 97.7 | 97.5 | 97.6 | 94.2 | 96.5 | 97.1 | 97.5 | 97.6 | 97.4 | 97.3
Shenzhen Growatt New Energy Technology Co., Ltd | Growatt 3600 MTL-US [277V] | 3600W 277 Vac Utility Interactive Inverter | 3.6 | 277 | 97 | Y | N |  | 0.4 |  |  | 100 | 375 | 450 | 0.36 | 0.72 | 1.08 | 1.8 | 2.7 | 3.6 | 91.2 | 93.9 | 94.7 | 96.1 | 96.6 | 96.6 | 95.9 | 93.4 | 96 | 96.6 | 97.4 | 97.5 | 97.5 | 97.2 | 94.5 | 96.8 | 97.4 | 97.9 | 98 | 97.9 | 97.7
Shenzhen Growatt New Energy Technology Co., Ltd | Growatt 4000MTLP-US [208V] | 4 kW, 208 Vac Utility Interactive Inverter | 3.62 | 208 | 95.5 | Y | N |  | 0.05 |  |  | 100 | 482 | 550 | 0.36 | 0.72 | 1.08 | 1.81 | 2.71 | 3.62 | 88.8 | 91.7 | 93.1 | 94.6 | 95.2 | 95.2 | 94.4 | 92.2 | 95.7 | 95.7 | 96.5 | 96.7 | 96.7 | 96.3 | 91.4 | 94.3 | 95.3 | 96.2 | 96.5 | 96.6 | 96 |  | 2017-10-16
Shenzhen Growatt New Energy Technology Co., Ltd | Growatt 4000MTLP-US [240V] | 4 kW, 240 Vac Utility Interactive Inverter | 4.05 | 240 | 96 | Y | N |  | 0.05 |  |  | 100 | 482 | 550 | 0.4 | 0.81 | 1.21 | 2.02 | 3.04 | 4.05 | 89.5 | 92.1 | 93.7 | 95 | 95.5 | 95.6 | 94.8 | 93.1 | 95.4 | 96.2 | 96.9 | 97.1 | 97.1 | 96.7 | 92.3 | 94.8 | 95.9 | 96.6 | 96.9 | 97 | 96.4 |  | 2017-10-16
Shenzhen Growatt New Energy Technology Co., Ltd | Growatt 4000MTLP-US [277V] | 4 kW, 277 Vac Utility Interactive Inverter | 4.06 | 277 | 96 | Y | N |  | 0.05 |  |  | 100 | 482 | 550 | 0.41 | 0.81 | 1.22 | 2.03 | 3.04 | 4.06 | 88.3 | 91.5 | 93.1 | 94.6 | 95.3 | 95.5 | 94.4 | 93.6 | 95.7 | 96.6 | 95.3 | 97.4 | 97.4 | 96.6 | 92.7 | 95.1 | 96.3 | 96.9 | 97.2 | 97.3 | 96.8 |  | 2017-10-16
Shenzhen Growatt New Energy Technology Co., Ltd | Growatt 4200 MTL-US [208V] | 4200W 208 Vac Utility Interactive Inverter | 4.2 | 208 | 97 | Y | N |  | 0.25 |  |  | 100 | 375 | 450 | 0.42 | 0.84 | 1.26 | 2.1 | 3.15 | 4.2 | 91.6 | 94.4 | 95.5 | 96.6 | 96.8 | 96.7 | 96.3 | 94.1 | 96.5 | 97.1 | 97.3 | 97.1 | 96.7 | 97 | 93.6 | 96.2 | 96.8 | 97.2 | 97.5 | 97.1 | 97.1
Shenzhen Growatt New Energy Technology Co., Ltd | Growatt 4200 MTL-US [240V] | 4200W 240 Vac Utility Interactive Inverter | 4.2 | 240 | 97 | Y | N |  | 0.33 |  |  | 100 | 375 | 450 | 0.42 | 0.84 | 1.26 | 2.1 | 3.15 | 4.2 | 92.4 | 94.6 | 95.5 | 96.5 | 96.7 | 96.7 | 96.2 | 95.3 | 97.1 | 97.5 | 97.8 | 97.7 | 97.5 | 97.6 | 94.2 | 96.5 | 97.1 | 97.5 | 97.6 | 97.4 | 97.3
Shenzhen Growatt New Energy Technology Co., Ltd | Growatt 4200 MTL-US [277V] | 4200W 277 Vac Utility Interactive Inverter | 4.2 | 277 | 97 | Y | N |  | 0.4 |  |  | 100 | 375 | 450 | 0.42 | 0.84 | 1.26 | 2.1 | 3.15 | 4.2 | 91.4 | 94.4 | 96 | 96.6 | 96.8 | 96.6 | 96.3 | 92.1 | 95.2 | 96.3 | 97.3 | 97.6 | 97.1 | 97 | 93.6 | 96.3 | 97.2 | 97.6 | 97.6 | 97.6 | 97.4
Shenzhen Growatt New Energy Technology Co., Ltd | Growatt 5000MTLP-US [208V] | 5 kW, 208 Vac Utility Interactive Inverter | 4.59 | 208 | 95.5 | Y | N |  | 0.05 |  |  | 100 | 482 | 550 | 0.46 | 0.92 | 1.38 | 2.3 | 3.44 | 4.59 | 89.9 | 92.5 | 93.8 | 94.9 | 95.1 | 95.1 | 94.6 | 93.2 | 95.3 | 96 | 96.6 | 96.7 | 96.6 | 96.4 | 92.5 | 94.8 | 95.7 | 96.4 | 96.6 | 96.5 | 96.2 |  | 2017-10-16
Shenzhen Growatt New Energy Technology Co., Ltd | Growatt 5000 MTL-US [208V] | 4600 W 208 Vac Utility Interactive Inverter | 4.6 | 208 | 97 | Y | N |  | 0.26 |  |  | 100 | 375 | 450 | 0.46 | 0.92 | 1.38 | 2.3 | 3.45 | 4.6 | 94.7 | 96.5 | 96.8 | 96.9 | 96.5 | 96 | 96.5 | 95.4 | 97 | 97.3 | 97.4 | 97 | 96.5 | 97 | 94.3 | 96.4 | 96.9 | 97.1 | 97 | 96.5 | 96.8
Shenzhen Growatt New Energy Technology Co., Ltd | Growatt 5000 MTL-US [240V] | 4600 W 240 Vac Utility Interactive Inverter | 4.6 | 240 | 97 | Y | N |  | 0.36 |  |  | 100 | 375 | 450 | 0.46 | 0.92 | 1.38 | 2.3 | 3.45 | 4.6 | 92.8 | 95.2 | 96 | 96.7 | 96.6 | 96.4 | 96.3 | 95.8 | 97.3 | 97.7 | 97.8 | 97.5 | 97.1 | 97.5 | 96.7 | 96.7 | 97.2 | 97.5 | 97.4 | 97.1 | 97.3
Shenzhen Growatt New Energy Technology Co., Ltd | Growatt 5000 MTL-US [277V] | 4600 W 277 Vac Utility Interactive Inverter | 4.6 | 277 | 97 | Y | N |  | 0.43 |  |  | 100 | 375 | 450 | 0.46 | 0.92 | 1.38 | 2.3 | 3.45 | 4.6 | 92.2 | 94.9 | 95.6 | 96.6 | 96.8 | 96.8 | 96.4 | 94.6 | 96.7 | 97.2 | 97.6 | 97.6 | 97.4 | 97.4 | 95.4 | 97.1 | 97.6 | 97.9 | 97.8 | 97.7 | 97.7
Shenzhen Growatt New Energy Technology Co., Ltd | Growatt 5000MTLP-US [277V] | 5 kW, 277 Vac Utility Interactive Inverter | 5.06 | 277 | 96.5 | Y | N |  | 0.05 |  |  | 100 | 482 | 550 | 0.51 | 1.01 | 1.52 | 2.53 | 3.8 | 5.06 | 89.5 | 92.3 | 93.8 | 95 | 95.5 | 95.5 | 94.8 | 94.3 | 96.1 | 96.8 | 97.3 | 97.4 | 97.3 | 97.1 | 93.5 | 95.6 | 96.4 | 97 | 97.2 | 97.2 | 96.9 |  | 2017-10-16
Shenzhen Growatt New Energy Technology Co., Ltd | Growatt 5000MTLP-US [240V] | 5 kW, 240 Vac Utility Interactive Inverter | 5.07 | 240 | 96 | Y | N |  | 0.05 |  |  | 100 | 482 | 550 | 0.51 | 1.01 | 1.52 | 2.53 | 3.8 | 5.07 | 90.5 | 93 | 94.3 | 95.2 | 95.4 | 95.3 | 94.9 | 93.9 | 95.8 | 96.5 | 97 | 97.1 | 96.9 | 96.8 | 93.1 | 95.3 | 96.1 | 96.8 | 96.9 | 96.9 | 96.6 |  | 2017-10-16
Shenzhen Growatt New Energy Technology Co., Ltd | Growatt 6000MTLP-US [208V] | 6 kW, 208 Vac Utility Interactive Inverter | 5.34 | 208 | 96 | Y | N |  | 0.05 |  |  | 100 | 482 | 550 | 0.53 | 1.07 | 1.6 | 2.67 | 4.01 | 5.34 | 90.7 | 93.2 | 94.3 | 95 | 95 | 94.9 | 94.7 | 93.9 | 95.7 | 96.3 | 96.7 | 96.6 | 96.4 | 96.4 | 93.3 | 95.3 | 95.9 | 96.5 | 96.5 | 96.3 | 96.2 |  | 2017-10-16
Shenzhen Growatt New Energy Technology Co., Ltd | Growatt 6000MTLP-US [240V] | 6 kW, 240 Vac Utility Interactive Inverter | 6.08 | 240 | 96 | Y | N |  | 0.05 |  |  | 100 | 482 | 550 | 0.61 | 1.22 | 1.82 | 3.04 | 4.56 | 6.08 | 91.3 | 93.6 | 94.7 | 95.4 | 95.5 | 95.6 | 95.1 | 94.6 | 96.1 | 96.7 | 97 | 97 | 96.8 | 96.8 | 93.9 | 95.6 | 96.3 | 96.8 | 96.8 | 96.7 | 96.6 |  | 2017-10-16
Shenzhen Growatt New Energy Technology Co., Ltd | Growatt 6000MTLP-US [277V] | 6 kW, 277 Vac Utility Interactive Inverter | 6.08 | 277 | 96.5 | Y | N |  | 0.05 |  |  | 100 | 482 | 550 | 0.61 | 1.22 | 1.82 | 3.04 | 4.56 | 6.08 | 90.4 | 93 | 94.4 | 95.3 | 95.4 | 95.3 | 94.9 | 94.9 | 96.4 | 96.9 | 97.3 | 97.4 | 97.2 | 97.2 | 94.1 | 95.9 | 96.6 | 97.1 | 97.2 | 97.1 | 96.9 |  | 2017-10-16
Shenzhen Growatt New Energy Technology Co., Ltd | Growatt 7000MTLP-US [208V] | 7 kW, 208 Vac Utility Interactive Inverter | 6.093 | 208 | 96 | Y | N |  | 0.05 |  |  | 280 | 385 | 485 | 609.3 | 1218.6 | 1827.9 | 3046.5 | 4569.75 | 6093 | 93.9 | 95.4 | 95.8 | 95.9 | 95.5 | 95.3 | 95.6 | 95.4 | 96.6 | 96.8 | 96.6 | 96.1 | 95.9 | 96.3 | 94.3 | 95.9 | 96.4 | 96.5 | 96.2 | 96 | 96.2 |  | 2017-10-16
Shenzhen Growatt New Energy Technology Co., Ltd | Growatt 7600MTLP-US [208V] | 7.6 kW, 208 Vac Utility Interactive Inverter | 6.741 | 208 | 96 | Y | N |  | 0.05 |  |  | 270 | 380 | 480 | 674.1 | 1348.2 | 2022.3 | 3370.51 | 5055.76 | 6741.01 | 94.1 | 95.5 | 95.7 | 95.7 | 95.2 | 95 | 95.3 | 95.7 | 96.7 | 96.8 | 96.6 | 96.1 | 95.9 | 96.3 | 94.7 | 96.2 | 96.5 | 96.5 | 96.1 | 95.8 | 96.2 |  | 2017-10-16
Shenzhen Growatt New Energy Technology Co., Ltd | Growatt 7000MTLP-US [240V] | 7 kW, 240 Vac Utility Interactive Inverter | 7.011 | 240 | 96.5 | Y | N |  | 0.051 |  |  | 270 | 385 | 485 | 701.11 | 1402.22 | 2103.33 | 3505.55 | 5258.33 | 7011.1 | 94 | 95.7 | 95.9 | 96 | 95.8 | 95.5 | 95.8 | 95.7 | 96.8 | 97 | 96.9 | 96.7 | 96.4 | 96.7 | 94.6 | 96.4 | 96.8 | 96.9 | 96.7 | 96.3 | 96.6 |  | 2017-10-16
Shenzhen Growatt New Energy Technology Co., Ltd | Growatt 7000MTLP-US [277V] | 7 kW, 277 Vac Utility Interactive Inverter | 7.0161 | 277 | 96.5 | Y | N |  | 0.051 |  |  | 275 | 385 | 480 | 701.61 | 1403.21 | 2104.82 | 3508.04 | 5262.05 | 7016.07 | 92.8 | 95.2 | 95.4 | 95.9 | 96.1 | 95.9 | 95.8 | 93.6 | 96.3 | 96.7 | 96.9 | 96.8 | 96.5 | 96.6 | 95 | 96.6 | 97.1 | 97.3 | 97.2 | 97 | 97.1 |  | 2017-10-16
Shenzhen Growatt New Energy Technology Co., Ltd | Growatt 8000MTLP-US [208V] | 8 kW, 208 Vac, 110-480 Vdc Utility Interactive Inverter with boosting circuit | 7.107 | 208 | 97 | N | N |  | 3.3 |  |  | 330 | 480 | 550 | 0.7107 | 1.4214 | 2.1321 | 3.5535 | 5.3303 | 7.107 | 95.2319 | 96.8981 | 97.1668 | 97.2152 | 96.9406 | 96.7327 | 96.9445 | 95.3248 | 96.8981 | 97.3535 | 97.5256 | 97.3657 | 97.2044 | 97.2847 | 94.5675 | 96.5387 | 97.0783 | 97.371 | 97.2917 | 97.1309 | 97.1281 | 2017-10-16 | 2018-10-15
Shenzhen Growatt New Energy Technology Co., Ltd | Growatt 7600MTLP-US [240V] | 7.6 kW, 240 Vac Utility Interactive Inverter | 7.604 | 240 | 96.5 | Y | N |  | 0.051 |  |  | 270 | 380 | 480 | 760.4 | 1520.8 | 2281.19 | 3801.99 | 5702.99 | 7603.98 | 94.3 | 95.8 | 96.2 | 96.1 | 95.8 | 95.3 | 95.8 | 96.1 | 97 | 97.2 | 97.1 | 96.8 | 96.3 | 96.9 | 94.9 | 96.5 | 96.9 | 96.9 | 96.7 | 96.3 | 96.7 |  | 2017-10-16
Shenzhen Growatt New Energy Technology Co., Ltd | Growatt 7600MTLP-US [277V] | 7.6 kW, 277 Vac Utility Interactive Inverter | 7.652 | 277 | 96.5 | Y | N |  | 0.051 |  |  | 270 | 380 | 480 | 765.15 | 1530.3 | 2295.45 | 3825.75 | 5738.63 | 7651.5 | 94.3 | 95.8 | 96.2 | 96.1 | 95.8 | 95.3 | 95.8 | 96.1 | 97 | 97.2 | 97.1 | 96.8 | 96.3 | 96.9 | 94.9 | 96.5 | 96.9 | 96.9 | 96.7 | 96.3 | 96.7 |  | 2017-10-16
Shenzhen Growatt New Energy Technology Co., Ltd | Growatt 9000MTLP-US [208V] | 9 kW, 208 Vac, 110-480 Vdc Utility Interactive Inverter with boosting circuit | 7.864 | 208 | 97 | N | N |  | 3.3 |  |  | 330 | 480 | 550 | 0.7864 | 1.5728 | 2.3592 | 3.932 | 5.898 | 7.864 | 95.4343 | 96.8634 | 97.1228 | 97.0837 | 96.7601 | 96.5393 | 96.8127 | 95.5184 | 96.9899 | 97.3531 | 97.4463 | 97.1787 | 97.0001 | 97.1711 | 94.827 | 96.6169 | 97.0564 | 97.2473 | 97.0819 | 96.8936 | 96.9907 | 2017-10-16 | 2018-10-15
Shenzhen Growatt New Energy Technology Co., Ltd | Growatt 8000MTLP-US [240V] | 8 kW, 240 Vac, 110-480 Vdc Utility Interactive Inverter with boosting circuit | 8.061 | 240 | 97.5 | N | N |  | 3.5 |  |  | 330 | 480 | 550 | 0.8061 | 1.6122 | 2.4183 | 4.0305 | 6.0457 | 8.061 | 95.4816 | 96.806 | 97.2982 | 97.458 | 97.318 | 97.0166 | 97.2309 | 95.7939 | 97.0913 | 97.5954 | 97.859 | 97.7928 | 97.5766 | 97.6572 | 95.2637 | 96.7576 | 97.3124 | 97.6341 | 97.6942 | 97.5279 | 97.4834 | 2017-10-16 | 2018-10-15
Shenzhen Growatt New Energy Technology Co., Ltd | Growatt 8000TL-US [208V] | 8000W 208 Vac Utility Interactive Inverter | 8.07 | 208 | 96.5 | Y | N |  | 0.05 |  |  | 100 | 345 | 480 | 0.81 | 1.61 | 2.42 | 4.03 | 6.05 | 8.07 | 95.6 | 96.7 | 97.1 | 97.2 | 97.1 | 96.9 | 97.1 | 94.9 | 96.3 | 96.8 | 97 | 96.9 | 96.8 | 96.8 | 92.6 | 95 | 95.8 | 96.4 | 96.4 | 96.2 | 96.1
Shenzhen Growatt New Energy Technology Co., Ltd | Growatt 8000TL-US [240V] | 8000W 240 Vac Utility Interactive Inverter | 8.08 | 240 | 97 | Y | N |  | 0.08 |  |  | 100 | 380 | 480 | 0.81 | 1.62 | 2.42 | 4.04 | 6.06 | 8.08 | 95.4 | 96.7 | 97.1 | 97.4 | 97.4 | 97.2 | 97.2 | 95.1 | 96.6 | 97 | 97.3 | 97.3 | 97.2 | 97.1 | 93.2 | 95.5 | 96.2 | 96.8 | 96.4 | 96.9 | 96.3
Shenzhen Growatt New Energy Technology Co., Ltd | Growatt 8000MTLP-US [277V] | 8 kW, 277 Vac, 110-480 Vdc Utility Interactive Inverter with boosting circuit | 8.137 | 277 | 97.5 | N | N |  | 3.7 |  |  | 330 | 480 | 550 | 0.8137 | 1.6274 | 2.4411 | 4.0685 | 6.1028 | 8.137 | 95.4421 | 96.6109 | 97.1824 | 97.5198 | 97.4925 | 97.2428 | 97.3225 | 96.2697 | 97.2044 | 97.777 | 98.0996 | 98.0984 | 97.9494 | 97.9348 | 95.8631 | 96.8898 | 97.4879 | 97.8391 | 97.9642 | 97.8946 | 97.7395 | 2017-10-16 | 2018-10-15
Shenzhen Growatt New Energy Technology Co., Ltd | Growatt 10000MTLP-US [208V] | 10 kW, 208 Vac, 110-480 Vdc Utility Interactive Inverter with boosting circuit | 8.63 | 208 | 97 | N | N |  | 3.3 |  |  | 330 | 480 | 550 | 0.863 | 1.726 | 2.589 | 4.315 | 6.4725 | 8.63 | 95.5609 | 96.3702 | 96.5193 | 97.0537 | 96.6088 | 96.4293 | 96.6286 | 95.6227 | 96.7681 | 96.7901 | 97.4531 | 97.1269 | 96.9585 | 97.0684 | 95.0326 | 96.7812 | 97.1518 | 97.3399 | 96.9975 | 96.8805 | 96.9926 | 2017-10-16 | 2018-10-15
Shenzhen Growatt New Energy Technology Co., Ltd | Growatt 9000MTLP-US [240V] | 9 kW, 240 Vac, 110-480 Vdc Utility Interactive Inverter with boosting circuit | 9.061 | 240 | 97.5 | N | N |  | 3.5 |  |  | 330 | 480 | 550 | 0.9061 | 1.8122 | 2.7183 | 4.5305 | 6.7957 | 9.061 | 95.9306 | 97.0351 | 97.3624 | 97.4055 | 97.1587 | 96.7832 | 97.1609 | 96.1264 | 97.3308 | 97.7098 | 97.8566 | 97.7061 | 97.4356 | 97.6427 | 95.536 | 96.9828 | 97.3349 | 97.5876 | 97.5568 | 97.3138 | 97.415 | 2017-10-16 | 2018-10-15
Shenzhen Growatt New Energy Technology Co., Ltd | Growatt 9000TL-US [208V] | 9000W 208 Vac Utility Interactive Inverter | 9.08 | 208 | 96.5 | Y | N |  | 0.05 |  |  | 100 | 345 | 480 | 0.91 | 1.82 | 2.72 | 4.54 | 6.81 | 9.08 | 95.9 | 96.8 | 97.1 | 97.2 | 97 | 96.8 | 97 | 95.3 | 96.5 | 96.9 | 97 | 97 | 96.7 | 96.9 | 93.1 | 95.3 | 96 | 96.4 | 96.4 | 96.2 | 96.2
Shenzhen Growatt New Energy Technology Co., Ltd | Growatt 9000TL-US [240V] | 9000W 240 Vac Utility Interactive Inverter | 9.08 | 240 | 97 | Y | N |  | 0.08 |  |  | 100 | 380 | 480 | 0.91 | 1.82 | 2.72 | 4.54 | 6.81 | 9.08 | 95.8 | 96.9 | 97.2 | 97.4 | 97.4 | 97.2 | 97.2 | 95.5 | 96.8 | 97.1 | 97.3 | 97.3 | 97.1 | 97.2 | 93.8 | 95.8 | 96.4 | 96.7 | 96.9 | 96.8 | 96.6
Shenzhen Growatt New Energy Technology Co., Ltd | Growatt 9000MTLP-US [277V] | 9 kW, 277 Vac, 110-480 Vdc Utility Interactive Inverter with boosting circuit | 9.169 | 277 | 97.5 | N | N |  | 3.7 |  |  | 330 | 480 | 550 | 0.9169 | 1.8338 | 2.7507 | 4.5845 | 6.8768 | 9.169 | 95.6877 | 96.866 | 97.3366 | 97.5417 | 97.445 | 97.1574 | 97.3387 | 96.3449 | 97.2806 | 97.7734 | 98.114 | 98.0647 | 97.8914 | 97.9234 | 95.9346 | 97.0873 | 97.6193 | 97.9244 | 98.0003 | 97.8943 | 97.8051 | 2017-10-16 | 2018-10-15
Shenzhen Growatt New Energy Technology Co., Ltd | Growatt 10000MTLP-US [240V] | 10 kW, 240 Vac, 110-480 Vdc Utility Interactive Inverter with boosting circuit | 10.058 | 240 | 97 | N | N |  | 3.5 |  |  | 330 | 480 | 550 | 1.0058 | 2.0116 | 3.0174 | 5.029 | 7.5435 | 10.058 | 95.7496 | 96.5751 | 96.6916 | 96.5323 | 96.917 | 96.6087 | 96.7299 | 95.8602 | 96.9019 | 97.0339 | 97.0528 | 97.6148 | 97.3005 | 97.3055 | 95.3753 | 96.9373 | 97.3973 | 97.6401 | 97.5368 | 97.2343 | 97.4102 | 2017-10-16 | 2018-10-15
Shenzhen Growatt New Energy Technology Co., Ltd | Growatt 10000TL-US [208V] | 10000 W 208 Vac Utility Interactive Inverter | 10.09 | 208 | 96.5 | Y | N |  | 0.05 |  |  | 308 | 345 | 480 | 1.01 | 2.02 | 3.03 | 5.04 | 7.57 | 10.09 | 95.8 | 96.9 | 97.1 | 97.2 | 97 | 96.6 | 97 | 95.5 | 96.6 | 96.9 | 97 | 96.9 | 96.5 | 96.8 | 93.1 | 95.4 | 96.1 | 96.4 | 96.3 | 96 | 96.1
Shenzhen Growatt New Energy Technology Co., Ltd | Growatt 10000 TL3-US [240V] | 10000 W 240 Vac Utility Interactive Inverter | 10.1 | 240 | 95.5 | Y | N |  | 0.01 |  |  | 250 | 420 | 480 | 1.1 | 2.2 | 3.3 | 5.5 | 7.58 | 10.1 | 89.5 | 93.1 | 94.1 | 94.9 | 95 | 95 | 94.6 | 90.1 | 93.9 | 95.2 | 96 | 96.3 | 96.4 | 95.7 | 89.9 | 94.2 | 95.4 | 96.3 | 96.7 | 96.8 | 96
Shenzhen Growatt New Energy Technology Co., Ltd | Growatt 10000MTLP-US [277V] | 10 kW, 277 Vac, 110-480 Vdc Utility Interactive Inverter with boosting circuit | 10.165 | 277 | 97.5 | N | N |  | 3.7 |  |  | 330 | 480 | 550 | 1.0165 | 2.033 | 3.0495 | 5.0825 | 7.6238 | 10.165 | 95.5795 | 96.4291 | 96.9301 | 97.5168 | 97.3177 | 97.0515 | 97.1857 | 96.0695 | 97.219 | 97.3929 | 98.1228 | 97.9602 | 97.7314 | 97.8021 | 95.8737 | 97.1605 | 97.9253 | 97.9533 | 97.9509 | 97.7632 | 97.8163 | 2017-10-16 | 2018-10-15
Shenzhen Growatt New Energy Technology Co., Ltd | Growatt 12000 TL3-US [277V] | 11620W 277 Vac Utility Interactive Inverter | 11.62 | 277 | 95.5 | Y | N |  | 0.01 |  |  | 250 | 420 | 480 | 1.16 | 2.32 | 3.49 | 5.81 | 8.72 | 11.62 | 89.8 | 93.4 | 94.4 | 95.2 | 94.9 | 95 | 94.6 | 90.2 | 94.2 | 95.3 | 96.2 | 96.4 | 96.5 | 95.9 | 91 | 94.6 | 95.6 | 96.4 | 96.6 | 96.7 | 96.1
Shenzhen Growatt New Energy Technology Co., Ltd | Growatt 11000TL-US [240V] | 11000W 240 Vac Utility Interactive Inverter | 11.7 | 240 | 97 | Y | N |  | 0.08 |  |  | 356 | 380 | 480 | 1.17 | 2.34 | 3.51 | 5.85 | 8.78 | 11.7 | 96 | 97 | 97.3 | 97.3 | 97.2 | 97 | 97.2 | 95.8 | 96.9 | 97.2 | 97.3 | 97.2 | 96.9 | 97.1 | 94.3 | 96 | 96.5 | 97 | 96.8 | 96.5 | 96.6
Shenzhen Growatt New Energy Technology Co., Ltd | Growatt 18000 TL3-US [277V] | 18220W 277 Vac Utility Interactive Inverter | 18.31 | 277 | 96 | Y | N |  | 0.01 |  |  | 250 | 420 | 480 | 1.83 | 3.66 | 5.49 | 9.15 | 13.73 | 18.31 | 92.3 | 94.9 | 95.4 | 95.2 | 95.5 | 95.4 | 95.3 | 92.5 | 95.8 | 96.4 | 96.8 | 96.9 | 96.6 | 96.6 | 92.9 | 95.8 | 96.5 | 96.9 | 97.1 | 96.8 | 96.7
Shenzhen Growatt New Energy Technology Co., Ltd | Growatt 20000 TL3-US [277V] | 20000W 277 Vac Utility Interactive Inverter | 20.42 | 277 | 96.5 | Y | N |  | 0.2 |  |  | 250 | 420 | 480 | 2.04 | 4.08 | 6.12 | 10.21 | 15.31 | 20.42 | 92.7 | 95.1 | 95.5 | 95.6 | 95.7 | 95.7 | 95.5 | 93.1 | 96 | 96.5 | 96.8 | 96.8 | 96.8 | 96.6 | 93.5 | 96 | 96.6 | 97 | 97.1 | 97 | 96.8
Shenzhen Growatt New Energy Technology Co., Ltd | GROWATT 33000TL3-US [480V] | 33 kW, 480 Vac, three phases, 3/N/PE, Transformerless Utility Interactive Inverter | 32.27 | 480 | 98.5 | N | N |  | 2.092 |  |  | 480 | 700 | 800 | 3.23 | 6.45 | 9.68 | 16.14 | 24.2 | 32.27 | 97.3 | 97.8 | 98.1 | 98.1 | 97.8 | 97.5 | 97.9 | 97.8 | 98.6 | 98.8 | 98.9 | 98.7 | 98.5 | 98.7 | 97.5 | 98 | 98.3 | 98.5 | 98.3 | 98.1 | 98.3 |  | 2018-11-15
Shenzhen Growatt New Energy Technology Co., Ltd | GROWATT 36000TL3-US [480V] | 36 kW, 480 Vac, three phases, 3/N/PE, Transformerless Utility Interactive Inverter | 35.71 | 480 | 98.5 | N | N |  | 2.051 |  |  | 520 | 700 | 800 | 3.57 | 7.14 | 10.71 | 17.86 | 26.78 | 35.71 | 97.5 | 98.1 | 98.2 | 98.3 | 97.9 | 97.6 | 98 | 98 | 98.6 | 98.6 | 98.6 | 98.6 | 98.4 | 98.6 | 97.4 | 98.1 | 98.2 | 98.2 | 98.3 | 98.1 | 98.2 |  | 2018-11-15
Shenzhen Growatt New Energy Technology Co., Ltd | GROWATT 40000TL3-US [480V] | 40 kW, 480Vac, three phases, 3/N/PE, Transformerless Utility Interactive Inverter | 39.85 | 480 | 98.5 | N | N |  | 2.051 |  |  | 570 | 700 | 800 | 3.98 | 7.97 | 11.95 | 19.92 | 29.89 | 39.85 | 97.5 | 98 | 98 | 98.2 | 98 | 97.6 | 98 | 98.2 | 98.6 | 98.6 | 98.4 | 98.7 | 98.5 | 98.6 | 97.5 | 98.1 | 98.1 | 98 | 98.3 | 98.1 | 98.2 |  | 2018-11-15
Shenzhen Sinexcel Electric Co., Ltd | Rainbow PVI-10.0-I-US | Photovoltaic Inverter for grid connected with NEMA 4 enclosure | 9.98 |  | 95.5 | Y | N |  | 0.1 |  |  | 250 | 386.5 | 432 | 0.998 | 1.997 | 2.995 | 4.991 | 7.487 | 9.983 | 90.3 | 93.7 | 95.2 | 95.6 | 95.2 | 94.9 | 95 | 91 | 94.8 | 95.5 | 95.8 | 95.6 | 95.4 | 95.4 | 91.8 | 94.8 | 95.3 | 96 | 96 | 95.5 | 95.6 |  | 2018-02-15
Shenzhen Sinexcel Electric Co., Ltd | Rainbow PVI-12.5-I-US | Photovoltaic Inverter for grid connected with NEMA 4 enclosure | 12.51 |  | 95 | Y | N |  | 0.1 |  |  | 250 | 386.5 | 432 | 1.251 | 2.503 | 3.754 | 6.257 | 9.386 | 1.251 | 90.9 | 94 | 95.7 | 95.1 | 94.9 | 94.3 | 94.8 | 88 | 93.4 | 95.6 | 95.3 | 95.4 | 95.1 | 95 | 87.8 | 94.7 | 95 | 95.1 | 95.2 | 94.9 | 94.8 |  | 2018-02-15
Shenzhen Sinexcel Electric Co., Ltd | PWS2-30K-NA [480V] | 30 kW, 480 Vac wall-mounted, bi-directional Utility Interactive Energy Storage Inverter | 30.02 | 480 | 96.5 | N | N |  | 1.857 |  |  | 350 | 600 | 750 | 3.002 | 6.004 | 9.006 | 15.01 | 22.515 | 30.02 | 91.2328 | 94.2776 | 95.1804 | 95.6343 | 95.5611 | 95.1895 | 95.2749 | 94.0804 | 95.9185 | 96.6069 | 97.0086 | 97.0306 | 96.8722 | 96.7936 | 94.9891 | 96.635 | 97.1812 | 97.4446 | 97.4471 | 97.2664 | 97.2667 | 2017-11-01 | 2018-10-15
Siemens Industry | SMIINT215R60XX [208V] | 215 W, 208 Vac Inverter with integrated ground, XX are connector types | 0.215 | 208 | 96.5 | N | Y |  | 0.054 |  |  | 27.5 | 33 | 38.7 | 0.02 | 0.04 | 0.06 | 0.11 | 0.16 | 0.22 | 95.2 | 96.1 | 96.4 | 96.6 | 96.6 | 96.3 | 96.5 | 95.1 | 96.1 | 96.3 | 96.6 | 96.6 | 96.5 | 96.5 | 95 | 96 | 96.2 | 96.5 | 96.6 | 96.6 | 96.5
Siemens Industry | SMIINT215R60XX [240V] | 215 W, 240 Vac Inverter with integrated ground, XX are connector types | 0.215 | 240 | 96.5 | N | Y |  | 0.054 |  |  | 27.5 | 33 | 38.7 | 0.02 | 0.04 | 0.06 | 0.11 | 0.16 | 0.22 | 95.2 | 96.1 | 96.4 | 96.6 | 96.6 | 96.3 | 96.5 | 95.1 | 96.1 | 96.3 | 96.6 | 96.6 | 96.5 | 96.5 | 95 | 96 | 96.2 | 96.5 | 96.6 | 96.6 | 96.5
Siemens Industry | SMIINV215R60XX [208V] | 215 W, 208 Vac Inverter, XX are connector types | 0.215 | 208 | 96 | N | Y |  | 0.04 |  |  | 22 | 29 | 36 | 0.02 | 0.04 | 0.06 | 0.11 | 0.16 | 0.22 | 94.5 | 95.5 | 95.9 | 96 | 95.5 | 94.7 | 95.6 | 94.6 | 95.5 | 95.9 | 96.1 | 96 | 95.5 | 95.9 | 94.4 | 95.4 | 95.7 | 96.1 | 96.1 | 95.8 | 95.9
Siemens Industry | SMIINV215R60XX [240V] | 215 W, 240 Vac Inverter, XX are connector types | 0.215 | 240 | 96 | N | Y |  | 0.05 |  |  | 22 | 29 | 36 | 0.02 | 0.04 | 0.06 | 0.11 | 0.16 | 0.22 | 94.6 | 95.5 | 95.9 | 96.1 | 95.7 | 95.1 | 95.7 | 94.6 | 95.5 | 95.9 | 96.2 | 96.1 | 95.8 | 96 | 94.6 | 95.5 | 95.8 | 96.1 | 96.2 | 96.1 | 96.1
Siemens Industry | SMIINT250R60XX [208V] | 240 W, 208 Vac Inverter with integrated ground, XX are connector types | 0.24 | 208 | 96 | N | Y |  | 0.043 |  |  | 27 | 32 | 38 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 94.7 | 95.7 | 96.1 | 96.3 | 96 | 95.5 | 96 | 94.7 | 95.7 | 96 | 96.3 | 96.2 | 95.8 | 96.1 | 94.5 | 95.5 | 95.8 | 96.1 | 96.2 | 96 | 96
Siemens Industry | SMIINT250R60XX [240V] | 240 W, 240 Vac Inverter with integrated ground, XX are connector types | 0.24 | 240 | 96.5 | N | Y |  | 0.046 |  |  | 27 | 32 | 38 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 95.6 | 96 | 96.3 | 96.5 | 96.4 | 96.1 | 96.4 | 95 | 96 | 96.2 | 96.5 | 96.6 | 96.4 | 96.4 | 94.9 | 96 | 96 | 96.4 | 96.5 | 96.5 | 96.4
Siemens Industry | SINVERT PVM12 UL [480V] | 12 kW, 480 Vac, 3-phase Utility Interactive Inverter | 12.12 | 480 | 97.5 | Y | N |  | 0.87 |  |  | 450 | 720 | 900 | 1.21 | 2.42 | 3.64 | 6.06 | 9.09 | 12.12 | 94.9 | 96.1 | 96.9 | 97.4 | 97.5 | 97.3 | 97.2 | 96 | 96.5 | 97.4 | 97.9 | 98.1 | 98.1 | 97.8 | 95.2 | 95.9 | 96.8 | 97.4 | 97.6 | 97.7 | 97.3
Siemens Industry | SINVERT PVM16 UL [480V] | 16 kW, 480 Vac, 3-phase Utility Interactive Inverter | 16.1 | 480 | 97.5 | Y | N |  | 0.09 |  |  | 500 | 720 | 900 | 1.61 | 3.22 | 4.83 | 8.05 | 12.08 | 16.1 | 96 | 96.8 | 97.4 | 97.6 | 97.6 | 97.4 | 97.5 | 96.6 | 97.3 | 97.7 | 98 | 98.1 | 98 | 97.9 | 95.9 | 96.5 | 97.2 | 97.6 | 97.7 | 97.7 | 97.5
Siemens Industry | SINVERT PVM20 UL [480V] | 20 kW, 480 Vac, 3-phase Utility Interactive Inverter | 19.65 | 480 | 97.5 | Y | N |  | 0.09 |  |  | 550 | 720 | 900 | 1.97 | 3.93 | 5.9 | 9.83 | 14.74 | 19.65 | 96.5 | 97.3 | 97.7 | 97.8 | 97.7 | 97.5 | 97.6 | 96.7 | 97.5 | 97.9 | 98.1 | 98.1 | 98 | 98 | 96 | 96.6 | 97.2 | 97.6 | 97.6 | 97.5 | 97.4
Siemens Industry | SINVERT PVM24 UL [480V] | 22.2 kW, 480 Vac, 3-phase Utility Interactive Inverter | 22.23 | 480 | 98 | Y | N |  | 0.49 |  |  | 600 | 720 | 900 | 2.22 | 4.45 | 6.67 | 11.12 | 16.67 | 22.23 | 97.2 | 97.7 | 97.9 | 97.9 | 97.8 | 97.6 | 97.8 | 97.3 | 97.7 | 98 | 98.1 | 98 | 97.8 | 98 | 96.7 | 97.1 | 97.5 | 97.7 | 97.6 | 97.5 | 97.6
Siemens Industry | SINVERT PVS351 UL [480V] | 350 kW, 480 Vac, 3-phase Inverter (Master Unit) | 350 | 480 | 96 | Y | N |  | 25 |  |  | 330 | 400 | 480 | 35 | 70 | 105 | 175 | 262.5 | 350 | 94.7 | 96.3 | 96.9 | 96.9 | 96.8 | 96.8 | 96.7 | 84.8 | 90.7 | 93 | 94.6 | 95.5 | 95.2 | 94.3 | 91.8 | 95.5 | 97.7 | 97.7 | 97.4 | 96.6 | 97.1
Siemens Industry | SINVERT PVS701 UL [480V] | 700 kW, 480 Vac, 3-phase Inverter (Master Unit, 1 Slave Unit) | 700 | 480 | 96 | Y | N |  | 50 |  |  | 330 | 400 | 480 | 70 | 140 | 210 | 350 | 525 | 700 | 94.7 | 96.3 | 96.9 | 96.9 | 96.8 | 96.8 | 96.7 | 84.8 | 90.7 | 93 | 94.6 | 95.5 | 95.2 | 94.3 | 91.8 | 95.5 | 97.7 | 97.7 | 97.4 | 96.6 | 97.1
Siemens Industry | SINVERT PVS1051 UL [480V] | 1050 kW, 480 Vac, 3-phase Inverter (Master Unit, 2 Slave Units) | 1050 | 480 | 96 | Y | N |  | 75 |  |  | 330 | 400 | 480 | 105 | 210 | 315 | 525 | 787.5 | 1050 | 94.7 | 96.3 | 96.9 | 96.9 | 96.8 | 96.8 | 96.7 | 84.8 | 90.7 | 93 | 94.6 | 95.5 | 95.2 | 94.3 | 91.8 | 95.5 | 97.7 | 97.7 | 97.4 | 96.6 | 97.1
Siemens Industry | SINVERT PVS1401 UL [480V] | 1400 kW, 480 Vac, 3-phase Inverter (Master Unit, 3 Slave Units) | 1400 | 480 | 96 | Y | N |  | 100 |  |  | 330 | 400 | 480 | 140 | 280 | 420 | 700 | 1050 | 1400 | 94.7 | 96.3 | 96.9 | 96.9 | 96.8 | 96.8 | 96.7 | 84.8 | 90.7 | 93 | 94.6 | 95.5 | 95.2 | 94.3 | 91.8 | 95.5 | 97.7 | 97.7 | 97.4 | 96.6 | 97.1
Silicon Energy | SiE 3840 [208V] | 3.3 kW, 208 Vac Utility Interactive Inverter | 3.4 | 208 | 95.5 | Y | N |  | 12 |  |  | 100 | 250 | 400 | 0.34 | 0.68 | 1.02 | 1.7 | 2.55 | 3.4 | 92.4 | 95.4 | 96.3 | 96.5 | 96.1 | 95.3 | 96 | 91.8 | 95.1 | 96 | 96.3 | 96 | 95.2 | 95.8 | 90.1 | 93.8 | 95.1 | 95.7 | 95.5 | 94.9 | 95.2
Silicon Energy | SiE 3840 [240V] | 3.8 kW, 240 Vac Utility Interactive Inverter | 3.9 | 240 | 96 | Y | N |  | 11 |  |  | 100 | 250 | 400 | 0.39 | 0.78 | 1.17 | 1.95 | 2.93 | 3.9 | 93 | 95.7 | 96.5 | 96.7 | 96.1 | 95.5 | 96.1 | 92.9 | 95.6 | 96.4 | 96.5 | 96 | 95.4 | 96 | 90 | 93.7 | 95.2 | 95.7 | 95.5 | 95 | 95.2
Silicon Energy | SiE 5300 [208V] | 4.6 kW, 208 Vac Utility Interactive Inverter | 4.6 | 208 | 95.5 | Y | N |  | 13.95 |  |  | 100 | 275 | 400 | 0.46 | 0.92 | 1.38 | 2.3 | 3.45 | 4.6 | 93.5 | 95.6 | 96.2 | 96.1 | 95.9 | 95.3 | 95.9 | 93 | 95.3 | 96 | 95.9 | 95.9 | 95.2 | 95.7 | 91.7 | 94.4 | 95.2 | 95.7 | 95.5 | 95 | 95.3
Silicon Energy | SiE 5300 [240V] | 5.3 kW, 240 Vac Utility Interactive Inverter | 5.3 | 240 | 96 | Y | N |  | 14 |  |  | 100 | 275 | 400 | 0.53 | 1.06 | 1.59 | 2.65 | 3.98 | 5.3 | 94.3 | 96.1 | 96.3 | 96.4 | 96 | 95.2 | 96 | 93.8 | 95.9 | 96.1 | 96.3 | 95.8 | 95.2 | 95.8 | 92.5 | 95 | 95.7 | 96 | 95.5 | 94.9 | 95.4
SMA America | SB 240-US-10 [240V] | 240 W, 240 Vac Microinverter | 0.24 | 240 | 96 | N | Y |  | 0.03 |  |  | 30 | 30 | 32 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 95.2 | 95.7 | 95.9 | 95.9 | 95.9 | 95.8 | 95.8 | 95.2 | 95.7 | 95.8 | 95.9 | 95.8 | 95.8 | 95.8 | 95.1 | 95.6 | 95.8 | 95.8 | 95.8 | 95.8 | 95.8
SMA America | SB700U [120V] | 700 W, 120Vac Sunny Boy String Inverter | 0.7 | 120 | 91.5 | Y | N |  | 0.0357 |  |  | 100 | 145 | 200 | 0.07 | 0.14 | 0.21 | 0.35 | 0.53 | 0.7 | 87.17 | 91.46 | 92.68 | 92.98 | 92.42 | 91.45 | 92.26 | 86.53 | 91.26 | 92.47 | 92.32 | 91.44 | 90.36 | 91.49 | 84.83 | 90.18 | 91.07 | 91.63 | 91.03 | 90.2 | 90.83
SMA America | SB700U-SBD [120V] | 700 W, 120Vac Sunny Boy String Inverter with display | 0.7 | 120 | 91.5 | Y | N |  | 0.0357 |  |  | 100 | 145 | 200 | 0.07 | 0.14 | 0.21 | 0.35 | 0.53 | 0.7 | 87.17 | 91.46 | 92.68 | 92.98 | 92.42 | 91.45 | 92.26 | 86.53 | 91.26 | 92.47 | 92.32 | 91.44 | 90.36 | 91.49 | 84.83 | 90.18 | 91.07 | 91.63 | 91.03 | 90.2 | 90.83
SMA America | SB1100U [240V] | 1100 W, 240 Vac Sunny Boy String Inverter | 1.1 | 240 | 91 | N | N |  | 0.13 |  |  | 100 | 200 | 325 | 0.11 | 0.22 | 0.33 | 0.55 | 0.83 | 1.1 | 83.92 | 91.62 | 92.57 | 92.42 | 91.86 | 90.91 | 91.68 | 87.08 | 90.82 | 91.84 | 92.02 | 91.37 | 90.5 | 91.32 | 83.95 | 88.75 | 92.38 | 90.95 | 90.75 | 90.01 | 90.58
SMA America | SB1100U-SBD [240V] | 1100 W, 240 Vac Sunny Boy String Inverter | 1.1 | 240 | 91 | Y | N |  | 0.13 |  |  | 100 | 200 | 325 | 0.11 | 0.22 | 0.33 | 0.55 | 0.83 | 1.1 | 83.92 | 91.62 | 92.57 | 92.42 | 91.86 | 90.91 | 91.68 | 87.08 | 90.82 | 91.84 | 92.02 | 91.37 | 90.5 | 91.32 | 83.95 | 88.75 | 92.38 | 90.95 | 90.75 | 90.01 | 90.58
SMA America | SWR1800U [120V] | 1.8 kW, 120Vac Sunny Boy String Inverter | 1.8 | 120 | 91.5 | Y | N |  | 0.2659 |  |  | 100 | 200 | 400 | 0.18 | 0.36 | 0.54 | 0.9 | 1.35 | 1.8 | 89.82 | 92.39 | 93.01 | 92.83 | 91.99 | 91 | 92.17 | 89.56 | 92.12 | 92.82 | 92.7 | 91.72 | 90.8 | 91.95 | 86.79 | 90.45 | 91.44 | 91.78 | 91.18 | 90.3 | 91.08
SMA America | SWR1800U-SBD [120V] | 1.8 kW, 120Vac Sunny Boy String Inverter with display | 1.8 | 120 | 91.5 | Y | N |  | 0.2659 |  |  | 100 | 200 | 400 | 0.18 | 0.36 | 0.54 | 0.9 | 1.35 | 1.8 | 89.82 | 92.39 | 93.01 | 92.83 | 91.99 | 91 | 92.17 | 89.56 | 92.12 | 92.82 | 92.7 | 91.72 | 90.8 | 91.95 | 86.79 | 90.45 | 91.44 | 91.78 | 91.18 | 90.3 | 91.08
SMA America | SB2000HFUS-30 [208V] | 2 kW, 208 Vac Sunny Boy Utility Interactive Inverter | 2.03 | 208 | 97 | Y | N |  | 0 |  |  | 100 | 400 | 480 | 0.2 | 0.41 | 0.61 | 1.02 | 1.52 | 2.03 | 92.2 | 95.2 | 96 | 96.3 | 95.9 | 95.2 | 95.8 | 95.1 | 96.8 | 97.4 | 97.4 | 97.2 | 96.6 | 97.1 | 96.4 | 97.8 | 98.1 | 98 | 97.6 | 97.1 | 97.7
SMA America | SB2000HFUS-30 [240V] | 2 kW, 240 Vac Sunny Boy Utility Interactive Inverter | 2.05 | 240 | 97 | Y | N |  | 0 |  |  | 100 | 400 | 480 | 0.21 | 0.41 | 0.62 | 1.03 | 1.54 | 2.05 | 92.6 | 95.2 | 96.2 | 96.6 | 96.4 | 95.9 | 96.2 | 93.9 | 97 | 97.3 | 97.6 | 97.6 | 97.2 | 97.3 | 95.8 | 97.6 | 98 | 98.1 | 97.9 | 97.6 | 97.8
SMA America | SWR2100U [240V] | 2.1 kW, 240 Vac Sunny Boy String Inverter | 2.1 | 240 | 93 | Y | N |  | 0.32 |  |  | 100 | 300 | 480 | 0.21 | 0.42 | 0.63 | 1.05 | 1.575 | 2.1 | 91.2 | 93.6 | 94.3 | 94.3 | 93.9 | 93.3 | 93.9 | 90.2 | 92.7 | 93.5 | 94.5 | 93.7 | 93.1 | 93.6 | 86 | 89.9 | 91.3 | 92.1 | 92.3 | 91.8 | 91.8
SMA America | SWR2100U-SBD [240V] | 2.1 kW, 240 Vac Sunny Boy String Inverter | 2.1 | 240 | 93 | Y | N |  | 0.32 |  |  | 100 | 300 | 480 | 0.21 | 0.42 | 0.63 | 1.05 | 1.575 | 2.1 | 91.2 | 93.6 | 94.3 | 94.3 | 93.9 | 93.3 | 93.9 | 90.2 | 92.7 | 93.5 | 94.5 | 93.7 | 93.1 | 93.6 | 86 | 89.9 | 91.3 | 92.1 | 92.3 | 91.8 | 91.8
SMA America | SWR2500U [208V] | 2.1 kW, 208 Vac Sunny Boy String Inverter | 2.1 | 208 | 92.5 | Y | N |  | 0.236 |  |  | 100 | 300 | 480 | 0.21 | 0.42 | 0.63 | 1.05 | 1.58 | 2.1 | 90.86 | 93.44 | 94.02 | 93.86 | 93.06 | 92.06 | 93.22 | 89.33 | 92.49 | 93.07 | 93.3 | 92.57 | 91.52 | 92.6 | 85.59 | 89.83 | 91.11 | 91.75 | 91.25 | 90.64 | 91.01
SMA America | SWR2500U-SBD [208V] | 2.1 kW, 208 Vac Sunny Boy String Inverter with display | 2.1 | 208 | 92.5 | Y | N |  | 0.236 |  |  | 100 | 300 | 480 | 0.21 | 0.42 | 0.63 | 1.05 | 1.58 | 2.1 | 90.86 | 93.44 | 94.02 | 93.86 | 93.06 | 92.06 | 93.22 | 89.33 | 92.49 | 93.07 | 93.3 | 92.57 | 91.52 | 92.6 | 85.59 | 89.83 | 91.11 | 91.75 | 91.25 | 90.64 | 91.01
SMA America | SWR2500U [240V] | 2.5 kW, 240 Vac Sunny Boy String Inverter | 2.5 | 240 | 93 | Y | N |  | 0.318 |  |  | 100 | 300 | 480 | 0.25 | 0.5 | 0.75 | 1.25 | 1.88 | 2.5 | 91.03 | 93.93 | 94.57 | 94.53 | 93.9 | 93.26 | 93.97 | 89.79 | 93.21 | 93.89 | 94.15 | 93.66 | 92.89 | 93.57 | 86.28 | 90.48 | 91.91 | 92.59 | 92.33 | 91.84 | 91.98
SMA America | SWR2500U-SBD [240V] | 2.5 kW, 240 Vac Sunny Boy String Inverter with display | 2.5 | 240 | 93 | Y | N |  | 0.318 |  |  | 100 | 300 | 480 | 0.25 | 0.5 | 0.75 | 1.25 | 1.88 | 2.5 | 91.03 | 93.93 | 94.57 | 94.53 | 93.9 | 93.26 | 93.97 | 89.79 | 93.21 | 93.89 | 94.15 | 93.66 | 92.89 | 93.57 | 86.28 | 90.48 | 91.91 | 92.59 | 92.33 | 91.84 | 91.98
SMA America | SB2500HFUS-30 [208V] | 2.5 kW, 208 Vac Sunny Boy Utility Interactive Inverter | 2.53 | 208 | 96.5 | Y | N |  | 1.1 |  |  | 100 | 415 | 480 | 0.25 | 0.51 | 0.76 | 1.27 | 1.9 | 2.53 | 94.3 | 95.7 | 96.4 | 96.4 | 96 | 95.1 | 96 | 95.6 | 96.8 | 97.2 | 97.2 | 96.9 | 96.3 | 96.9 | 95 | 96.8 | 97.3 | 97.4 | 97.1 | 96.5 | 97.1
SMA America | SB2500HFUS-30 [240V] | 2.5 kW, 240 Vac Sunny Boy Utility Interactive Inverter | 2.53 | 240 | 96.5 | Y | N |  | 1.12 |  |  | 100 | 415 | 480 | 0.25 | 0.51 | 0.76 | 1.26 | 1.9 | 2.53 | 93.4 | 95.3 | 96.1 | 96.1 | 96.2 | 95.5 | 96 | 93.6 | 96 | 96.7 | 97.1 | 97 | 96.6 | 96.8 | 93.6 | 96.1 | 96.9 | 97.2 | 97.1 | 96.7 | 96.9
SMA America | SB3000US [208V] | 3 kW, 208 Vac Sunny Boy Utility Interactive Inverter with display | 3 | 208 | 95 | Y | N |  | 0.08 |  |  | 100 | 250 | 400 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 94 | 95.8 | 96 | 95.8 | 95.1 | 94.3 | 95.3 | 93.1 | 95.9 | 95.7 | 95.6 | 94.9 | 94 | 95.1 | 91.6 | 94.8 | 95.2 | 94.7 | 94.2 | 93.5 | 94.3
SMA America | SB3000US [240V] | 3 kW, 240 Vac Sunny Boy Utility Interactive Inverter with display | 3 | 240 | 95.5 | Y | N |  | 0.07 |  |  | 100 | 250 | 400 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 93.4 | 95.9 | 96.3 | 96.5 | 96.1 | 95.6 | 96 | 92.5 | 95.8 | 96 | 96.1 | 95.8 | 95.1 | 95.7 | 90.5 | 94.6 | 95.4 | 95.3 | 95.2 | 94.6 | 95
SMA America | SB3000US-12 [208V] | 3 kW, 208 Vac Sunny Boy Utility Interactive Inverter with arc detector with display | 3 | 208 | 95 | Y | N |  | 0.08 |  |  | 100 | 250 | 400 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 94 | 95.8 | 96 | 95.8 | 95.1 | 94.3 | 95.3 | 93.1 | 95.9 | 95.7 | 95.6 | 94.9 | 94 | 95.1 | 91.6 | 94.8 | 95.2 | 94.7 | 94.2 | 93.5 | 94.3
SMA America | SB3000US-12 [240V] | 3 kW, 240 Vac Sunny Boy Utility Interactive Inverter with arc detector with display | 3 | 240 | 95.5 | Y | N |  | 0.07 |  |  | 100 | 250 | 400 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 93.4 | 95.9 | 96.3 | 96.5 | 96.1 | 95.6 | 96 | 92.5 | 95.8 | 96 | 96.1 | 95.8 | 95.1 | 95.7 | 90.5 | 94.6 | 95.4 | 95.3 | 95.2 | 94.6 | 95
SMA America | SB3000HFUS-30 [208V] | 3 kW, 208 Vac Sunny Boy Utility Interactive Inverter | 3.01 | 208 | 96.5 | Y | N |  | 0.9 |  |  | 100 | 415 | 480 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3.01 | 94.2 | 96 | 96.4 | 96.2 | 95.5 | 94.2 | 95.7 | 95.4 | 96.7 | 96.8 | 96.8 | 96.3 | 95.5 | 96.4 | 96.2 | 97.4 | 97.6 | 97.4 | 96.8 | 96 | 97
SMA America | SB3.0-1SP-US-40 [208V] | 3.0 kW, 208 Vac transformerless Utility Interactive Inverter | 3.03 | 208 | 96 | Y | N |  | 5.36 |  |  | 155 | 365 | 480 | 0.3032 | 0.6064 | 0.9096 | 1.516 | 2.274 | 3.032 | 92.0828 | 94.9078 | 95.6295 | 95.9916 | 95.9966 | 95.7315 | 95.7273 | 92.071 | 95.6597 | 96.4583 | 97.0435 | 97.2021 | 97.084 | 96.7913 | 88.5154 | 94.503 | 95.7227 | 96.4246 | 96.7724 | 96.6443 | 96.1233 | 2018-08-01 | 2018-10-15
SMA America | SB3.0-1TP-US-40 [208V] | 3.0 kW, 208 Vac transformerless Utility Interactive Inverter with revenue grade energy meter | 3.03 | 208 | 96 | Y | N |  | 5.36 |  |  | 155 | 365 | 480 | 0.3032 | 0.6064 | 0.9096 | 1.516 | 2.274 | 3.032 | 92.0828 | 94.9078 | 95.6295 | 95.9916 | 95.9966 | 95.7315 | 95.7273 | 92.071 | 95.6597 | 96.4583 | 97.0435 | 97.2021 | 97.084 | 96.7913 | 88.5154 | 94.503 | 95.7227 | 96.4246 | 96.7724 | 96.6443 | 96.1233 | 2018-08-01 | 2018-10-15
SMA America | SB3.0-1SP-US-40 [240V] | 3.0 kW, 240 Vac transformerless Utility Interactive Inverter | 3.04 | 240 | 96.5 | Y | N |  | 5.39 |  |  | 155 | 365 | 480 | 0.30403 | 0.60805 | 0.91208 | 1.5201 | 2.2802 | 3.0403 | 90.9512 | 94.442 | 95.3831 | 95.9418 | 96.0378 | 95.9409 | 95.651 | 92.0355 | 95.7848 | 96.6411 | 97.1637 | 97.5164 | 97.5821 | 97.0347 | 88.5098 | 94.4385 | 95.7364 | 96.6779 | 97.025 | 97.0008 | 96.3263 | 2018-08-01 | 2018-10-15
SMA America | SB3.0-1TP-US-40 [240V] | 3.0 kW, 240 Vac transformerless Utility Interactive Inverter with revenue grade energy meter | 3.04 | 240 | 96.5 | Y | N |  | 5.39 |  |  | 155 | 365 | 480 | 0.30403 | 0.60805 | 0.91208 | 1.5201 | 2.2802 | 3.0403 | 90.9512 | 94.442 | 95.3831 | 95.9418 | 96.0378 | 95.9409 | 95.651 | 92.0355 | 95.7848 | 96.6411 | 97.1637 | 97.5164 | 97.5821 | 97.0347 | 88.5098 | 94.4385 | 95.7364 | 96.6779 | 97.025 | 97.0008 | 96.3263 | 2018-08-01 | 2018-10-15
SMA America | SB3000TL-US-22 [208V] | 3 kW, 208 Vac Sunny Boy Utility Interactive Inverter | 3.05 | 208 | 97 | Y | N |  | 0.53 |  |  | 100 | 400 | 480 | 0.31 | 0.61 | 0.92 | 1.53 | 2.29 | 3.05 | 92.7 | 95.3 | 95.8 | 96.1 | 96.1 | 95.9 | 95.9 | 92.6 | 95.7 | 96.5 | 97.2 | 97.2 | 97.1 | 96.8 | 92.2 | 95.4 | 96.5 | 96.9 | 97 | 97 | 96.6 |  | 2018-03-15
SMA America | SB3000TL-US-22 [240V] | 3 kW, 240 Vac Sunny Boy transformerless Utility Interactive Inverter with arc detector | 3.05 | 240 | 97 | Y | N |  | 0.49 |  |  | 100 | 400 | 480 | 0.31 | 0.61 | 0.92 | 1.53 | 2.29 | 3.05 | 92.1 | 95 | 95.8 | 96.2 | 96.2 | 96 | 95.9 | 93.7 | 96.5 | 97.1 | 97.6 | 97.5 | 97.5 | 97.3 | 92.1 | 95.6 | 96.5 | 97.2 | 97.3 | 97.4 | 96.9 |  | 2018-03-15
SMA America | SB3000HFUS-30 [240V] | 3 kW, 240 Vac Sunny Boy Utility Interactive Inverter | 3.07 | 240 | 96.5 | Y | N |  | 1.1 |  |  | 100 | 415 | 480 | 0.31 | 0.61 | 0.92 | 1.54 | 2.3 | 3.07 | 93.8 | 95.9 | 96.4 | 96.4 | 95.9 | 94.9 | 95.9 | 94.4 | 96.3 | 96.7 | 96.9 | 96.7 | 96.1 | 96.6 | 95.7 | 97.1 | 97.4 | 97.4 | 97.1 | 96.5 | 97.1
SMA America | SB3300U [240V] | 3.3 kW, 240 Vac Sunny Boy Utility Interactive Inverter with display | 3.3 | 240 | 94.5 | Y | N |  | 0.16 |  |  | 100 | 250 | 400 | 0.33 | 0.66 | 0.99 | 1.65 | 2.475 | 3.3 | 92.6 | 94.6 | 95.2 | 95.4 | 95.2 | 94.6 | 95.06 | 91.8 | 94.1 | 94.8 | 95.1 | 94.9 | 94.5 | 94.74 | 89.2 | 92.4 | 93.6 | 94 | 93.9 | 93.5 | 93.61
SMA America | SB4000US(CL) [208V] | 4 kW, 208 Vac, current limited Utility Interactive Inverter with display | 3.3 | 208 | 95.5 | Y | N |  | 0.14 |  |  | 100 | 310 | 480 | 0.33 | 0.66 | 0.99 | 1.65 | 2.475 | 3.3 | 94.3 | 96.3 | 96.5 | 96.4 | 95.8 | 94.9 | 95.9 | 93.5 | 96.2 | 96.1 | 96.1 | 95.5 | 94.8 | 95.6 | 91.5 | 94.9 | 95.4 | 95.1 | 94.8 | 94 | 94.7
SMA America | SB3800U [208V] | 3.5 kW, 208 Vac Sunny Boy Utility Interactive Inverter with display | 3.5 | 208 | 94 | Y | N |  | 0.161 |  |  | 100 | 235 | 400 | 0.35 | 0.7 | 1.05 | 1.75 | 2.625 | 3.5 | 93.59 | 94.88 | 95.15 | 94.87 | 94.14 | 93.33 | 94.39 | 92.81 | 94.5 | 94.78 | 94.62 | 93.98 | 92.95 | 94.14 | 90.26 | 92.72 | 93.44 | 93.46 | 93.06 | 92.23 | 93.02
SMA America | SB4000US [208V] | 4 kW, 208 Vac Sunny Boy Utility Interactive Inverter with display | 3.5 | 208 | 95.5 | Y | N |  | 0.14 |  |  | 100 | 310 | 480 | 0.35 | 0.7 | 1.05 | 1.75 | 2.63 | 3.5 | 94.3 | 96.3 | 96.5 | 96.4 | 95.8 | 94.9 | 95.9 | 93.5 | 96.2 | 96.1 | 96.1 | 95.5 | 94.8 | 95.6 | 91.5 | 94.9 | 95.4 | 95.1 | 94.8 | 94 | 94.7
SMA America | SB4000US-12 [208V] | 3.5 kW, 208 Vac Sunny Boy Utility Interactive Inverter with arc detector with display | 3.5 | 208 | 95.5 | Y | N |  | 0.14 |  |  | 100 | 310 | 480 | 0.35 | 0.7 | 1.05 | 1.75 | 2.63 | 3.5 | 94.3 | 96.3 | 96.5 | 96.4 | 95.8 | 94.9 | 95.9 | 93.5 | 96.2 | 96.1 | 96.1 | 95.5 | 94.8 | 95.6 | 91.5 | 94.9 | 95.4 | 95.1 | 94.8 | 94 | 94.7
SMA America | SB3.8-1SP-US-40 [208V] | 3.8 kW, 208 Vac transformerless Utility Interactive Inverter | 3.6 | 208 | 96.5 | Y | N |  | 5.36 |  |  | 195 | 365 | 480 | 0.36045 | 0.72091 | 1.0814 | 1.8023 | 2.7034 | 3.6045 | 92.9308 | 95.4761 | 96.03 | 96.4729 | 96.3788 | 96.1527 | 96.1623 | 92.5315 | 95.951 | 96.6213 | 97.0596 | 97.2247 | 96.9787 | 96.8539 | 89.8079 | 94.9193 | 95.9971 | 96.5769 | 96.77 | 96.8496 | 96.2697 | 2018-08-01 | 2018-10-15
SMA America | SB3.8-1TP-US-40 [208V] | 3.8 kW, 208 Vac transformerless Utility Interactive Inverter with revenue grade energy meter | 3.6 | 208 | 96.5 | Y | N |  | 5.36 |  |  | 195 | 365 | 480 | 0.36045 | 0.72091 | 1.0814 | 1.8023 | 2.7034 | 3.6045 | 92.9308 | 95.4761 | 96.03 | 96.4729 | 96.3788 | 96.1527 | 96.1623 | 92.5315 | 95.951 | 96.6213 | 97.0596 | 97.2247 | 96.9787 | 96.8539 | 89.8079 | 94.9193 | 95.9971 | 96.5769 | 96.77 | 96.8496 | 96.2697 | 2018-08-01 | 2018-10-15
SMA America | SB3800U [240V] | 3.8 kW, 240 Vac Sunny Boy Utility Interactive Inverter with display | 3.8 | 240 | 94.5 | Y | N |  | 0.161 |  |  | 100 | 250 | 400 | 0.38 | 0.76 | 1.14 | 1.9 | 2.85 | 3.8 | 93.32 | 95.02 | 95.5 | 95.39 | 94.98 | 94.27 | 95.03 | 92.75 | 94.63 | 95.08 | 95.07 | 94.69 | 93.81 | 94.69 | 90.15 | 92.98 | 93.89 | 94.08 | 93.82 | 93.21 | 93.66
SMA America | SB4000US(CL) [240V] | 4 kW, 240 Vac, current limited Utility Interactive Inverter with display | 3.8 | 240 | 96 | Y | N |  | 0.17 |  |  | 100 | 310 | 480 | 0.38 | 0.76 | 1.14 | 1.9 | 2.85 | 3.8 | 92.5 | 96.4 | 96.8 | 96.7 | 96.4 | 96 | 96.3 | 91.9 | 96.2 | 96.3 | 96.5 | 96 | 95.5 | 96 | 89.1 | 94.7 | 95.6 | 95.5 | 95.3 | 94.9 | 95.1
SMA America | SB3.8-1SP-US-40 [240V] | 3.8 kW, 240 Vac transformerless Utility Interactive Inverter | 3.85 | 240 | 96.5 | Y | N |  | 5.39 |  |  | 195 | 365 | 480 | 0.38543 | 0.77085 | 1.1563 | 1.9271 | 2.8907 | 3.8543 | 92.6814 | 95.3701 | 96.0702 | 96.4553 | 96.4439 | 96.2328 | 96.1867 | 93.6802 | 96.4354 | 96.8953 | 97.4346 | 97.5877 | 97.468 | 97.2525 | 90.8056 | 95.3096 | 96.4049 | 96.9099 | 97.1557 | 97.3074 | 96.6753 | 2018-08-01 | 2018-10-15
SMA America | SB3.8-1TP-US-40 [240V] | 3.8 kW, 240 Vac transformerless Utility Interactive Inverter with revenue grade energy meter | 3.85 | 240 | 96.5 | Y | N |  | 5.39 |  |  | 195 | 365 | 480 | 0.38543 | 0.77085 | 1.1563 | 1.9271 | 2.8907 | 3.8543 | 92.6814 | 95.3701 | 96.0702 | 96.4553 | 96.4439 | 96.2328 | 96.1867 | 93.6802 | 96.4354 | 96.8953 | 97.4346 | 97.5877 | 97.468 | 97.2525 | 90.8056 | 95.3096 | 96.4049 | 96.9099 | 97.1557 | 97.3074 | 96.6753 | 2018-08-01 | 2018-10-15
SMA America | SB3800TL-US-22 [208V] | 3.8 kW, 208 Vac Sunny Boy transformerless Utility Interactive Inverter with arc detector | 3.85 | 208 | 96.5 | Y | N |  | 0.53 |  |  | 100 | 400 | 480 | 0.39 | 0.77 | 1.16 | 1.93 | 2.89 | 3.85 | 93.8 | 95.7 | 96.1 | 96.1 | 96 | 95.6 | 95.9 | 93.7 | 96.2 | 97.1 | 97.2 | 97.1 | 96.9 | 96.9 | 93.7 | 96 | 96.7 | 97 | 97 | 96.9 | 96.8
SMA America | SB3800TL-US-22 [240V] | 3 kW, 240 Vac Sunny Boy transformerless Utility Interactive Inverter with arc detector | 3.85 | 240 | 97 | Y | N |  | 0.49 |  |  | 100 | 400 | 480 | 0.39 | 0.77 | 1.16 | 1.93 | 2.89 | 3.85 | 93.3 | 95.6 | 96 | 96.2 | 96 | 95.7 | 95.9 | 95.3 | 96.9 | 97.4 | 97.5 | 97.5 | 97.4 | 97.4 | 93.1 | 96.4 | 97 | 97.4 | 97.3 | 97.3 | 97.1
SMA America | SB4000US [240V] | 4 kW, 240 Vac Sunny Boy Utility Interactive Inverter with display | 4 | 240 | 96 | Y | N |  | 0.17 |  |  | 100 | 310 | 480 | 0.4 | 0.8 | 1.2 | 2 | 3 | 4 | 92.5 | 96.4 | 96.8 | 96.7 | 96.4 | 96 | 96.3 | 91.9 | 96.2 | 96.3 | 96.5 | 96 | 95.5 | 96 | 89.1 | 94.7 | 95.6 | 95.5 | 95.3 | 94.9 | 95.1
SMA America | SB4000US-12 [240V] | 4 kW, 240 Vac Sunny Boy Utility Interactive Inverter with arc detector with display | 4 | 240 | 96 | Y | N |  | 0.17 |  |  | 100 | 310 | 480 | 0.4 | 0.8 | 1.2 | 2 | 3 | 4 | 92.5 | 96.4 | 96.8 | 96.7 | 96.4 | 96 | 96.3 | 91.9 | 96.2 | 96.3 | 96.5 | 96 | 95.5 | 96 | 89.1 | 94.7 | 95.6 | 95.5 | 95.3 | 94.9 | 95.1
SMA America | Sunny Island SI4548 | 4 kW multi-mode Inverter | 4 |  | 94.5 | Y | N |  | 0 |  |  | 100 | 48 | 63 | 0.4 | 0.8 | 1.2 | 2 | 3 | 4 | 93.8 | 94.5 | 95.9 | 95.3 | 94.8 | 93.5 | 94.9 | 93.8 | 94.6 | 95.6 | 95.2 | 94.6 | 93.2 | 94.7 | 93.8 | 95.1 | 95.1 | 94.8 | 94.2 | 92.8 | 94.4
SMA America | SB3800US [240V] | 3.8 kW, 240 Vac Sunny Boy Utility Interactive Inverter with display | 4.05 | 240 | 96 | Y | N |  | 0.08 |  |  | 100 | 310 | 480 | 0.405 | 0.81 | 1.215 | 2.025 | 3.038 | 4.05 | 94.59 | 96.32 | 96.71 | 96.78 | 96.38 | 95.83 | 96.4 | 93.53 | 95.5 | 96.13 | 96.31 | 96.03 | 95.47 | 95.95 | 91.56 | 94.38 | 95.28 | 95.58 | 95.55 | 95.08 | 95.29
SMA America | SB3800US-12 [240V] | 3.8 kW, 240 Vac Sunny Boy Utility Interactive Inverter with arc detector with display | 4.05 | 240 | 96 | Y | N |  | 0.08 |  |  | 100 | 310 | 480 | 0.405 | 0.81 | 1.215 | 2.025 | 3.038 | 4.05 | 94.59 | 96.32 | 96.71 | 96.78 | 96.38 | 95.83 | 96.4 | 93.53 | 95.5 | 96.13 | 96.31 | 96.03 | 95.47 | 95.95 | 91.56 | 94.38 | 95.28 | 95.58 | 95.55 | 95.08 | 95.29
SMA America | SB4000TL-US-22 [208V] | 4 kW, 208 Vac Sunny Boy transformerless Utility Interactive Inverter with arc detector | 4.05 | 208 | 96.5 | Y | N |  | 0.53 |  |  | 100 | 400 | 480 | 0.41 | 0.81 | 1.22 | 2.03 | 3.04 | 4.05 | 94.1 | 95.8 | 96.1 | 96.1 | 95.9 | 95.4 | 95.9 | 94.1 | 96.3 | 97.2 | 97.2 | 97.1 | 96.8 | 97 | 93.4 | 96.2 | 96.8 | 97 | 97 | 96.8 | 96.8
SMA America | SB4000TL-US-22 [240V] | 3.8 kW, 240 Vac Sunny Boy transformerless Utility Interactive Inverter with arc detector | 4.05 | 240 | 97 | Y | N |  | 0.49 |  |  | 100 | 400 | 480 | 0.41 | 0.81 | 1.22 | 2.03 | 3.04 | 4.05 | 93.5 | 95.6 | 96 | 96.2 | 96 | 95.7 | 95.9 | 95.3 | 97.1 | 97.4 | 97.5 | 97.5 | 97.3 | 97.4 | 93.8 | 96.4 | 97.2 | 97.4 | 97.4 | 97.3 | 97.2
SMA America | SB5000TL-US-22 [208V] | 5 kW, 208 Vac Sunny Boy transformerless Utility Interactive Inverter | 4.58 | 208 | 96.5 | Y | N |  | 0.53 |  |  | 100 | 400 | 480 | 0.46 | 0.92 | 1.37 | 2.29 | 3.43 | 4.58 | 94.5 | 95.9 | 96.1 | 96.1 | 95.7 | 95.4 | 95.8 | 94.7 | 96.5 | 97.2 | 97.1 | 97 | 96.7 | 96.9 | 94 | 96.5 | 96.9 | 97 | 96.9 | 96.6 | 96.8
SMA America | SB5000US [208V] | 5 kW, 208 Vac Sunny Boy Utility Interactive Inverter with display | 5 | 208 | 95.5 | Y | N |  | 0.46 |  |  | 100 | 310 | 480 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 91.5 | 95.7 | 96.2 | 96.7 | 96.7 | 96.3 | 96.4 | 89.9 | 95 | 95.7 | 96.2 | 96.4 | 96 | 95.9 | 86.3 | 92.5 | 94.3 | 95 | 95.1 | 95 | 94.5
SMA America | SB5000US [240V] | 5 kW, 240 Vac Sunny Boy Utility Interactive Inverter with display | 5 | 240 | 95.5 | Y | N |  | 0.72 |  |  | 100 | 310 | 480 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 91 | 95.7 | 96.2 | 96.8 | 96.8 | 96.5 | 96.4 | 89.7 | 94.9 | 95.7 | 96.2 | 96.4 | 96.2 | 95.9 | 86.2 | 92.5 | 94.3 | 95.2 | 95.2 | 95.1 | 94.6
SMA America | SB5000US [277V] | 5 kW, 277 Vac Sunny Boy Utility Interactive Inverter with display | 5 | 277 | 95.5 | Y | N |  | 1.41 |  |  | 100 | 310 | 480 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 91.5 | 95.8 | 96.5 | 96.8 | 96.5 | 96.6 | 96.3 | 90 | 95 | 95.8 | 96.2 | 96.5 | 96.2 | 96 | 86.3 | 92.3 | 94.4 | 95.2 | 95.2 | 95.2 | 94.6
SMA America | SB5000US-11 [208V] | 5 kW, 208 Vac Sunny Boy Utility Interactive Inverter with display | 5 | 208 | 95.5 | Y | N |  | 0.46 |  |  | 100 | 310 | 480 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 91.5 | 95.7 | 96.2 | 96.7 | 96.7 | 96.3 | 96.4 | 89.9 | 95 | 95.7 | 96.2 | 96.4 | 96 | 95.9 | 86.3 | 92.5 | 94.3 | 95 | 95.1 | 95 | 94.5
SMA America | SB5000US-11 [240V] | 5 kW, 240 Vac Sunny Boy Utility Interactive Inverter with display | 5 | 240 | 95.5 | Y | N |  | 0.72 |  |  | 100 | 310 | 480 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 91 | 95.7 | 96.2 | 96.8 | 96.8 | 96.5 | 96.4 | 89.7 | 94.9 | 95.7 | 96.2 | 96.4 | 96.2 | 95.9 | 86.2 | 92.5 | 94.3 | 95.2 | 95.2 | 95.1 | 94.6
SMA America | SB5000US-11 [277V] | 5 kW, 277 Vac Sunny Boy Utility Interactive Inverter with display | 5 | 277 | 95.5 | Y | N |  | 1.41 |  |  | 100 | 310 | 480 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 91.5 | 95.8 | 96.5 | 96.8 | 96.5 | 96.6 | 96.3 | 90 | 95 | 95.8 | 96.2 | 96.5 | 96.2 | 96 | 86.3 | 92.3 | 94.4 | 95.2 | 95.2 | 95.2 | 94.6
SMA America | SB5000US-12 [208V] | 5 kW, 208 Vac Sunny Boy Utility Interactive Inverter with arc detector with display | 5 | 208 | 95.5 | Y | N |  | 0.46 |  |  | 100 | 310 | 480 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 91.5 | 95.7 | 96.2 | 96.7 | 96.7 | 96.3 | 96.4 | 89.9 | 95 | 95.7 | 96.2 | 96.4 | 96 | 95.9 | 86.3 | 92.5 | 94.3 | 95 | 95.1 | 95 | 94.5
SMA America | SB5000US-12 [240V] | 5 kW, 240 Vac Sunny Boy Utility Interactive Inverter with arc detector with display | 5 | 240 | 95.5 | Y | N |  | 0.72 |  |  | 100 | 310 | 480 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 91 | 95.7 | 96.2 | 96.8 | 96.8 | 96.5 | 96.4 | 89.7 | 94.9 | 95.7 | 96.2 | 96.4 | 96.2 | 95.9 | 86.2 | 92.5 | 94.3 | 95.2 | 95.2 | 95.1 | 94.6
SMA America | SB5000US-12 [277V] | 5 kW, 277 Vac Sunny Boy Utility Interactive Inverter with arc detector with display | 5 | 277 | 95.5 | Y | N |  | 1.41 |  |  | 100 | 310 | 480 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 91.5 | 95.8 | 96.5 | 96.8 | 96.5 | 96.6 | 96.3 | 90 | 95 | 95.8 | 96.2 | 96.5 | 96.2 | 96 | 86.3 | 92.3 | 94.4 | 95.2 | 95.2 | 95.2 | 94.6
SMA America | Sunny Island SI6048 | 5 kW multi-mode Inverter | 5 |  | 94 | Y | N |  | 0 |  |  | 41 | 48 | 63 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 93.8 | 95.9 | 95.9 | 94.8 | 93.5 | 92.1 | 94.1 | 93.8 | 95.6 | 95.7 | 94.6 | 93.2 | 91.7 | 93.9 | 93.8 | 95.1 | 95.2 | 94.2 | 92.8 | 91.4 | 93.5
SMA America | SB5.0-1SP-US-40 [240V] | 5.0 kW, 240 Vac transformerless Utility Interactive Inverter | 5.05 | 240 | 97 | Y | N |  | 5.21 |  |  | 220 | 365 | 480 | 0.51 | 1.01 | 1.52 | 2.53 | 3.79 | 5.05 | 93.3 | 96 | 96.5 | 96.7 | 96.6 | 96.4 | 96.4 | 93.4 | 96.9 | 97.2 | 97.5 | 97.4 | 97.2 | 97.2 | 91.2 | 96.2 | 96.8 | 97.2 | 97.4 | 97.3 | 97 | 2018-08-01 | 2018-10-15
SMA America | SB5.0-1TP-US-40 [240V] | 5.0 kW, 240 Vac transformerless Utility Interactive Inverter with revenue grade energy meter | 5.05 | 240 | 97 | Y | N |  | 5.21 |  |  | 220 | 365 | 480 | 0.51 | 1.01 | 1.52 | 2.53 | 3.79 | 5.05 | 93.3 | 96 | 96.5 | 96.7 | 96.6 | 96.4 | 96.4 | 93.4 | 96.9 | 97.2 | 97.5 | 97.4 | 97.2 | 97.2 | 91.2 | 96.2 | 96.8 | 97.2 | 97.4 | 97.3 | 97 | 2018-08-01 | 2018-10-15
SMA America | SB5000TL-US-22 [240V] | 5 kW, 240 Vac Sunny Boy transformerless Utility Interactive Inverter with arc detector | 5.05 | 240 | 97 | Y | N |  | 0.49 |  |  | 100 | 400 | 480 | 0.51 | 1.01 | 1.52 | 2.53 | 3.79 | 5.05 | 94.3 | 95.9 | 96.2 | 96.2 | 95.8 | 95.5 | 95.8 | 95.9 | 97.2 | 97.6 | 97.6 | 97.3 | 97 | 97.3 | 95.1 | 97 | 97.2 | 97.5 | 97.3 | 97.1 | 97.2
SMA America | SB5.0-1SP-US-40 [208V] | 5.0 kW, 208 Vac transformerless Utility Interactive Inverter | 5.06 | 208 | 96.5 | Y | N |  | 5.06 |  |  | 220 | 365 | 480 | 0.51 | 1.01 | 1.52 | 2.53 | 3.8 | 5.06 | 94.7 | 96.3 | 96.6 | 96.6 | 96.4 | 96 | 96.4 | 94.7 | 96.7 | 97.1 | 97.2 | 97.1 | 96.8 | 97 | 91.1 | 96.1 | 96.7 | 96.9 | 97 | 96.8 | 96.6 | 2018-08-01 | 2018-10-15
SMA America | SB5.0-1TP-US-40 [208V] | 5.0 kW, 208 Vac transformerless Utility Interactive Inverter with revenue grade energy meter | 5.06 | 208 | 96.5 | Y | N |  | 5.06 |  |  | 220 | 365 | 480 | 0.51 | 1.01 | 1.52 | 2.53 | 3.8 | 5.06 | 94.7 | 96.3 | 96.6 | 96.6 | 96.4 | 96 | 96.4 | 94.7 | 96.7 | 97.1 | 97.2 | 97.1 | 96.8 | 97 | 91.1 | 96.1 | 96.7 | 96.9 | 97 | 96.8 | 96.6 | 2018-08-01 | 2018-10-15
SMA America | SB6000TL-US-22 [208V] | 5 kW, 208 Vac Sunny Boy transformerless Utility Interactive Inverter with arc detector | 5.2 | 208 | 97 | Y | N |  | 0.51 |  |  | 100 | 412 | 480 | 0.52 | 1.04 | 1.56 | 2.6 | 3.9 | 5.2 | 94.5 | 96 | 96.3 | 96.3 | 96 | 95.6 | 96 | 94.3 | 96.4 | 96.8 | 97 | 96.9 | 96.7 | 96.8 | 93.3 | 95.9 | 96.5 | 96.7 | 96.7 | 96.5 | 96.5
SMA America | SB6000U [208V] | 6000 W, 208 Vac Sunny Boy Utility Interactive Inverter with meter | 5.2 | 208 | 94.5 | Y | N |  | 0.2042 |  |  | 100 | 334 | 480 | 0.57 | 1.11 | 1.63 | 2.7 | 4.01 | 5.32 | 93.09 | 95.24 | 95.6 | 95.61 | 94.78 | 94.16 | 94.98 | 91.6 | 94.65 | 95.15 | 95.27 | 94.63 | 93.76 | 94.66 | 88.63 | 92.33 | 93.49 | 93.94 | 93.69 | 93.1 | 93.42
SMA America | SB6.0-1SP-US-40 [208V] | 6.0 kW, 208 Vac transformerless Utility Interactive Inverter | 5.49 | 208 | 96.5 | Y | N |  | 5.06 |  |  | 220 | 365 | 480 | 0.55 | 1.1 | 1.65 | 2.75 | 4.12 | 5.49 | 94.8 | 96.3 | 96.6 | 96.6 | 96.4 | 96 | 96.4 | 94.8 | 96.7 | 97.1 | 97.2 | 97.1 | 96.8 | 97 | 91.7 | 96.2 | 96.7 | 96.8 | 97 | 96.8 | 96.6 | 2018-08-01 | 2018-10-15
SMA America | SB6.0-1TP-US-40 [208V] | 6.0 kW, 208 Vac transformerless Utility Interactive Inverter with revenue grade energy meter | 5.49 | 208 | 96.5 | Y | N |  | 5.06 |  |  | 220 | 365 | 480 | 0.55 | 1.1 | 1.65 | 2.75 | 4.12 | 5.49 | 94.8 | 96.3 | 96.6 | 96.6 | 96.4 | 96 | 96.4 | 94.8 | 96.7 | 97.1 | 97.2 | 97.1 | 96.8 | 97 | 91.7 | 96.2 | 96.7 | 96.8 | 97 | 96.8 | 96.6 | 2018-08-01 | 2018-10-15
SMA America | SB6000TL-US [208V] | 6 kW, 208 Vac Sunny Boy transformerless Utility Interactive Inverter | 6 | 208 | 98 | Y | N |  | 0.34 |  |  | 100 | 345 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 97.6 | 98.4 | 98.6 | 98.5 | 98.4 | 97.9 | 98.4 | 97.4 | 98.2 | 98.4 | 98.3 | 98.1 | 97.7 | 98.1 | 96.5 | 97.6 | 97.9 | 98 | 97.9 | 97.6 | 97.8
SMA America | SB6000TL-US [240V] | 6 kW, 240 Vac Sunny Boy transformerless Utility Interactive Inverter | 6 | 240 | 98.5 | Y | N |  | 0.14 |  |  | 100 | 379 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 97.4 | 98.4 | 98.7 | 98.6 | 98.5 | 98.3 | 98.5 | 97.4 | 98.3 | 98.5 | 98.6 | 98.5 | 98.1 | 98.4 | 96.5 | 97.6 | 98.1 | 98.3 | 98.3 | 98.1 | 98.2
SMA America | SB6000TL-US-12 [208V] | 6 kW, 208 Vac Sunny Boy transformerless Utility Interactive Inverter with arc detector | 6 | 208 | 98 | Y | N |  | 0.34 |  |  | 100 | 345 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 97.6 | 98.4 | 98.6 | 98.5 | 98.4 | 97.9 | 98.4 | 97.4 | 98.2 | 98.4 | 98.3 | 98.1 | 97.7 | 98.1 | 96.5 | 97.6 | 97.9 | 98 | 97.9 | 97.6 | 97.8
SMA America | SB6000TL-US-12 [240V] | 6 kW, 240 Vac Sunny Boy transformerless Utility Interactive Inverter with arc detector | 6 | 240 | 98.5 | Y | N |  | 0.14 |  |  | 100 | 379 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 97.4 | 98.4 | 98.7 | 98.6 | 98.5 | 98.3 | 98.5 | 97.4 | 98.3 | 98.5 | 98.6 | 98.5 | 98.1 | 98.4 | 96.5 | 97.6 | 98.1 | 98.3 | 98.3 | 98.1 | 98.2
SMA America | SB6000TL-US-22 [240V] | 6 kW, 240 Vac Sunny Boy transformerless Utility Interactive Inverter | 6 | 240 | 97 | Y | N |  | 0.46 |  |  | 100 | 400 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 95 | 96.3 | 96.4 | 96.4 | 96.1 | 95.7 | 96.1 | 95.6 | 97.1 | 97.3 | 97.4 | 97.3 | 96.9 | 97.2 | 94.5 | 96.5 | 96.9 | 97.1 | 97.1 | 96.9 | 96.9
SMA America | SB6000U [240V] | 6 kW, 240 Vac Sunny Boy Utility Interactive Inverter with display | 6 | 240 | 94.5 | Y | N |  | 0.2042 |  |  | 100 | 310 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 93.17 | 95.47 | 95.76 | 95.48 | 94.86 | 94.2 | 95.03 | 92.3 | 94.88 | 95.22 | 95.23 | 94.58 | 93.82 | 94.68 | 90.1 | 93.3 | 94.14 | 94.25 | 93.93 | 93.17 | 93.8
SMA America | SB6000U [277V] | 6 kW, 277 Vac Sunny Boy Utility Interactive Inverter with display | 6 | 277 | 94.5 | Y | N |  | 0.23 |  |  | 100 | 310 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 93.09 | 95.21 | 95.88 | 95.62 | 95.15 | 94.53 | 95.22 | 91.88 | 94.75 | 95.4 | 95.23 | 94.84 | 94.22 | 94.83 | 89.79 | 93.18 | 94.13 | 94.4 | 94.02 | 93.42 | 93.87
SMA America | SB6000US [208V] | 6 kW, 208 Vac Sunny Boy Utility Interactive Inverter with display | 6 | 208 | 95.5 | Y | N |  | 0.46 |  |  | 100 | 310 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 92.5 | 95.8 | 96.5 | 96.9 | 96.5 | 95.9 | 96.3 | 91.2 | 95.6 | 95.9 | 96.3 | 96.1 | 95.6 | 95.9 | 88 | 93.5 | 94.8 | 94.6 | 94.9 | 94.6 | 94.5
SMA America | SB6000US [240V] | 6 kW, 240 Vac Sunny Boy Utility Interactive Inverter with display | 6 | 240 | 95.5 | Y | N |  | 0.72 |  |  | 100 | 310 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 92.6 | 96.1 | 96.5 | 96.8 | 96.7 | 96 | 96.4 | 91.3 | 95.6 | 96 | 96.3 | 96.3 | 95.9 | 96 | 87.9 | 93.6 | 94.8 | 95.1 | 95 | 94.8 | 94.7
SMA America | SB6000US [277V] | 6 kW, 277 Vac Sunny Boy Utility Interactive Inverter with display | 6 | 277 | 96 | Y | N |  | 1.41 |  |  | 100 | 310 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 92.3 | 96 | 96.7 | 97 | 96.7 | 96.5 | 96.5 | 91.3 | 95.6 | 96.2 | 96.4 | 96.4 | 96 | 96.1 | 87.8 | 93.6 | 94.9 | 95.2 | 95.1 | 94.9 | 94.7
SMA America | SB6000US-11 [208V] | 6 kW, 208 Vac Sunny Boy Utility Interactive Inverter with display | 6 | 208 | 95.5 | Y | N |  | 0.46 |  |  | 100 | 310 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 92.5 | 95.8 | 96.5 | 96.9 | 96.5 | 95.9 | 96.3 | 91.2 | 95.6 | 95.9 | 96.3 | 96.1 | 95.6 | 95.9 | 88 | 93.5 | 94.8 | 94.6 | 94.9 | 94.6 | 94.5
SMA America | SB6000US-11 [240V] | 6 kW, 240 Vac Sunny Boy Utility Interactive Inverter with display | 6 | 240 | 95.5 | Y | N |  | 0.72 |  |  | 100 | 310 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 92.6 | 96.1 | 96.5 | 96.8 | 96.7 | 96 | 96.4 | 91.3 | 95.6 | 96 | 96.3 | 96.3 | 95.9 | 96 | 87.9 | 93.6 | 94.8 | 95.1 | 95 | 94.8 | 94.7
SMA America | SB6000US-11 [277V] | 6 kW, 277 Vac Sunny Boy Utility Interactive Inverter with display | 6 | 277 | 96 | Y | N |  | 1.41 |  |  | 100 | 310 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 92.3 | 96 | 96.7 | 97 | 96.7 | 96.5 | 96.5 | 91.3 | 95.6 | 96.2 | 96.4 | 96.4 | 96 | 96.1 | 87.8 | 93.6 | 94.9 | 95.2 | 95.1 | 94.9 | 94.7
SMA America | SB6000US-12 [208V] | 6 kW, 208 Vac Sunny Boy Utility Interactive Inverter with arc detector with display | 6 | 208 | 95.5 | Y | N |  | 0.46 |  |  | 100 | 310 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 92.5 | 95.8 | 96.5 | 96.9 | 96.5 | 95.9 | 96.3 | 91.2 | 95.6 | 95.9 | 96.3 | 96.1 | 95.6 | 95.9 | 88 | 93.5 | 94.8 | 94.6 | 94.9 | 94.6 | 94.5
SMA America | SB6000US-12 [240V] | 6 kW, 240 Vac Sunny Boy Utility Interactive Inverter with arc detector with display | 6 | 240 | 95.5 | Y | N |  | 0.72 |  |  | 100 | 310 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 92.6 | 96.1 | 96.5 | 96.8 | 96.7 | 96 | 96.4 | 91.3 | 95.6 | 96 | 96.3 | 96.3 | 95.9 | 96 | 87.9 | 93.6 | 94.8 | 95.1 | 95 | 94.8 | 94.7
SMA America | SB6000US-12 [277V] | 6 kW, 277 Vac Sunny Boy Utility Interactive Inverter with arc detector with display | 6 | 277 | 96 | Y | N |  | 1.41 |  |  | 100 | 310 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 92.3 | 96 | 96.7 | 97 | 96.7 | 96.5 | 96.5 | 91.3 | 95.6 | 96.2 | 96.4 | 96.4 | 96 | 96.1 | 87.8 | 93.6 | 94.9 | 95.2 | 95.1 | 94.9 | 94.7
SMA America | SB7000TL-US-22 [208V] | 7 kW (208 Vac) Utility Interactive Inverter | 6.01 | 208 | 96.5 | Y | N |  | 0.395 |  |  | 100 | 400 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.51 | 6.01 | 94.2 | 95.9 | 96.2 | 96.2 | 95.9 | 95.5 | 95.9 | 93.1 | 96.2 | 96.6 | 96.8 | 96.7 | 96.5 | 96.5 | 91.7 | 95.8 | 96.3 | 96.7 | 96.6 | 96.4 | 96.4
SMA America | SB6.0-1SP-US-40 [240V] | 6.0 kW, 240 Vac transformerless Utility Interactive Inverter | 6.05 | 240 | 97 | Y | N |  | 5.21 |  |  | 220 | 365 | 480 | 0.61 | 1.21 | 1.82 | 3.03 | 4.54 | 6.05 | 94.7 | 96.3 | 96.6 | 96.6 | 96.5 | 96.1 | 96.4 | 95.4 | 97.1 | 97.4 | 97.6 | 97.3 | 97 | 97.3 | 93.4 | 96.5 | 97 | 97.3 | 97.3 | 97 | 97.1 | 2018-08-01 | 2018-10-15
SMA America | SB6.0-1TP-US-40 [240V] | 6.0 kW, 240 Vac transformerless Utility Interactive Inverter with revenue grade energy meter | 6.05 | 240 | 97 | Y | N |  | 5.21 |  |  | 220 | 365 | 480 | 0.61 | 1.21 | 1.82 | 3.03 | 4.54 | 6.05 | 94.7 | 96.3 | 96.6 | 96.6 | 96.5 | 96.1 | 96.4 | 95.4 | 97.1 | 97.4 | 97.6 | 97.3 | 97 | 97.3 | 93.4 | 96.5 | 97 | 97.3 | 97.3 | 97 | 97.1 | 2018-08-01 | 2018-10-15
SMA America | SB7700TL-US-22 [208V] | 7 kW (208 Vac) Utility Interactive Inverter | 6.73 | 208 | 96.5 | Y | N |  | 0.395 |  |  | 100 | 400 | 480 | 0.67 | 1.35 | 2.02 | 3.37 | 5.05 | 6.73 | 94.9 | 96.2 | 96.4 | 96.3 | 95.9 | 95.2 | 96 | 94.2 | 96.4 | 96.7 | 96.8 | 96.7 | 96.3 | 96.6 | 94.7 | 96.1 | 96.4 | 96.7 | 96.7 | 96.4 | 96.6
SMA America | SB7.0-1SP-US-40 [208V] | 7.0 kW, 208 Vac transformerless Utility Interactive Inverter | 6.92 | 208 | 96.5 | Y | N |  | 5.37 |  |  | 245 | 365 | 480 | 0.69229 | 1.3846 | 2.0769 | 3.4615 | 5.1922 | 6.9229 | 95.4191 | 96.4997 | 96.8805 | 96.3931 | 96.1295 | 95.5922 | 96.2382 | 95.3532 | 96.6628 | 97.1412 | 97.0424 | 96.6648 | 96.2346 | 96.7272 | 94.1363 | 96.3475 | 96.6764 | 96.6839 | 96.3523 | 96.3048 | 96.3696 | 2018-08-01 | 2018-10-15
SMA America | SB7.0-1TP-US-40 [208V] | 7.0 kW, 208 Vac transformerless Utility Interactive Inverter with revenue grade energy meter | 6.92 | 208 | 96.5 | Y | N |  | 5.37 |  |  | 245 | 365 | 480 | 0.69229 | 1.3846 | 2.0769 | 3.4615 | 5.1922 | 6.9229 | 95.4191 | 96.4997 | 96.8805 | 96.3931 | 96.1295 | 95.5922 | 96.2382 | 95.3532 | 96.6628 | 97.1412 | 97.0424 | 96.6648 | 96.2346 | 96.7272 | 94.1363 | 96.3475 | 96.6764 | 96.6839 | 96.3523 | 96.3048 | 96.3696 | 2018-08-01 | 2018-10-15
SMA America | SB7.7-1SP-US-40 [208V] | 7.7 kW, 208 Vac transformerless Utility Interactive Inverter | 6.92 | 208 | 96.5 | Y | N |  | 5.37 |  |  | 270 | 365 | 480 | 0.69229 | 1.3846 | 2.0769 | 3.4615 | 5.1922 | 6.9229 | 95.6881 | 96.7105 | 96.729 | 96.5396 | 96.0507 | 95.6947 | 96.2354 | 95.3532 | 96.6628 | 97.1412 | 97.0424 | 96.6648 | 96.2346 | 96.7272 | 94.1363 | 96.3475 | 96.6764 | 96.6839 | 96.3523 | 96.3048 | 96.3696 | 2018-08-01 | 2018-10-15
SMA America | SB7.7-1TP-US-40 [208V] | 7.7 kW, 208 Vac transformerless Utility Interactive Inverter with revenue grade energy meter | 6.92 | 208 | 96.5 | Y | N |  | 5.37 |  |  | 270 | 365 | 480 | 0.69229 | 1.3846 | 2.0769 | 3.4615 | 5.1922 | 6.9229 | 95.6881 | 96.7105 | 96.729 | 96.5396 | 96.0507 | 95.6947 | 96.2354 | 95.3532 | 96.6628 | 97.1412 | 97.0424 | 96.6648 | 96.2346 | 96.7272 | 94.1363 | 96.3475 | 96.6764 | 96.6839 | 96.3523 | 96.3048 | 96.3696 | 2018-08-01 | 2018-10-15
SMA America | SB7000TL-US [208V] | 7 kW, 208 Vac Sunny Boy transformerless Utility Interactive Inverter | 7 | 208 | 98 | Y | N |  | 0.34 |  |  | 100 | 345 | 480 | 0.7 | 1.4 | 2.1 | 3.5 | 5.25 | 7 | 97.8 | 98.6 | 98.6 | 98.4 | 98.2 | 97.6 | 98.3 | 97.7 | 98.3 | 98.4 | 98.3 | 97.9 | 97.5 | 98.1 | 96.9 | 97.8 | 98 | 98 | 97.8 | 97.4 | 97.8
SMA America | SB7000TL-US [240V] | 7 kW, 240 Vac Sunny Boy transformerless Utility Interactive Inverter | 7 | 240 | 98.5 | Y | N |  | 0.14 |  |  | 100 | 379 | 480 | 0.7 | 1.4 | 2.1 | 3.5 | 5.25 | 7 | 97.7 | 98.5 | 98.7 | 98.6 | 98.4 | 98 | 98.4 | 97.8 | 98.4 | 98.5 | 98.2 | 98.3 | 97.8 | 98.3 | 96.8 | 97.8 | 98.2 | 98.3 | 98.2 | 97.9 | 98.1
SMA America | SB7000TL-US-12 [208V] | 7 kW, 208 Vac Sunny Boy transformerless Utility Interactive Inverter with arc detector | 7 | 208 | 98 | Y | N |  | 0.34 |  |  | 100 | 345 | 480 | 0.7 | 1.4 | 2.1 | 3.5 | 5.25 | 7 | 97.8 | 98.6 | 98.6 | 98.4 | 98.2 | 97.6 | 98.3 | 97.7 | 98.3 | 98.4 | 98.3 | 97.9 | 97.5 | 98.1 | 96.9 | 97.8 | 98 | 98 | 97.8 | 97.4 | 97.8
SMA America | SB7000TL-US-12 [240V] | 6 kW, 240 Vac Sunny Boy transformerless Utility Interactive Inverter with arc detector | 7 | 240 | 98.5 | Y | N |  | 0.14 |  |  | 100 | 379 | 480 | 0.7 | 1.4 | 2.1 | 3.5 | 5.25 | 7 | 97.7 | 98.5 | 98.7 | 98.6 | 98.4 | 98 | 98.4 | 97.8 | 98.4 | 98.5 | 98.2 | 98.3 | 97.8 | 98.3 | 96.8 | 97.8 | 98.2 | 98.3 | 98.2 | 97.9 | 98.1
SMA America | SB7000US [208V] | 7 kW, 208 Vac Sunny Boy Utility Interactive Inverter with display | 7 | 208 | 95.5 | Y | N |  | 0.46 |  |  | 100 | 310 | 480 | 0.7 | 1.4 | 2.1 | 3.5 | 5.25 | 7 | 94 | 96.3 | 97.1 | 96.7 | 96.2 | 95.4 | 96.3 | 92.7 | 96.1 | 96.1 | 96.2 | 95.9 | 95.3 | 95.9 | 89.7 | 94.2 | 95 | 94.9 | 94.8 | 94.1 | 94.6
SMA America | SB7000US [240V] | 7 kW, 240 Vac Sunny Boy Utility Interactive Inverter with display | 7 | 240 | 96 | Y | N |  | 0.72 |  |  | 100 | 310 | 480 | 0.7 | 1.4 | 2.1 | 3.5 | 5.25 | 7 | 93.7 | 96.2 | 96.8 | 96.9 | 96.5 | 95.8 | 96.5 | 92.3 | 96.1 | 96.1 | 96.4 | 96.1 | 95.6 | 96 | 89.3 | 94.3 | 95.1 | 95.6 | 95 | 94.7 | 94.8
SMA America | SB7000US [277V] | 7 kW, 277 Vac Sunny Boy Utility Interactive Inverter with display | 7 | 277 | 96 | Y | N |  | 1.41 |  |  | 100 | 310 | 480 | 0.7 | 1.4 | 2.1 | 3.5 | 5.25 | 7 | 93.7 | 96.3 | 96.8 | 97 | 96.5 | 95.9 | 96.5 | 92.5 | 96.1 | 96.3 | 96.5 | 96.2 | 95.6 | 96.1 | 89.3 | 94.2 | 95.2 | 95 | 95.1 | 94.6 | 94.8
SMA America | SB7000US-11 [208V] | 7 kW, 208 Vac Sunny Boy Utility Interactive Inverter with display | 7 | 208 | 95.5 | Y | N |  | 0.46 |  |  | 100 | 310 | 480 | 0.7 | 1.4 | 2.1 | 3.5 | 5.25 | 7 | 94 | 96.3 | 97.1 | 96.7 | 96.2 | 95.4 | 96.3 | 92.7 | 96.1 | 96.1 | 96.2 | 95.9 | 95.3 | 95.9 | 89.7 | 94.2 | 95 | 94.9 | 94.8 | 94.1 | 94.6
SMA America | SB7000US-11 [240V] | 7 kW, 240 Vac Sunny Boy Utility Interactive Inverter with display | 7 | 240 | 96 | Y | N |  | 0.72 |  |  | 100 | 310 | 480 | 0.7 | 1.4 | 2.1 | 3.5 | 5.25 | 7 | 93.7 | 96.2 | 96.8 | 96.9 | 96.5 | 95.8 | 96.5 | 92.3 | 96.1 | 96.1 | 96.4 | 96.1 | 95.6 | 96 | 89.3 | 94.3 | 95.1 | 95.6 | 95 | 94.7 | 94.8
SMA America | SB7000US-11 [277V] | 7 kW, 277 Vac Sunny Boy Utility Interactive Inverter with display | 7 | 277 | 96 | Y | N |  | 1.41 |  |  | 100 | 310 | 480 | 0.7 | 1.4 | 2.1 | 3.5 | 5.25 | 7 | 93.7 | 96.3 | 96.8 | 97 | 96.5 | 95.9 | 96.5 | 92.5 | 96.1 | 96.3 | 96.5 | 96.2 | 95.6 | 96.1 | 89.3 | 94.2 | 95.2 | 95 | 95.1 | 94.6 | 94.8
SMA America | SB7000US-12 [208V] | 7 kW, 208 Vac Sunny Boy Utility Interactive Inverter with arc detector with display | 7 | 208 | 95.5 | Y | N |  | 0.46 |  |  | 100 | 310 | 480 | 0.7 | 1.4 | 2.1 | 3.5 | 5.25 | 7 | 94 | 96.3 | 97.1 | 96.7 | 96.2 | 95.4 | 96.3 | 92.7 | 96.1 | 96.1 | 96.2 | 95.9 | 95.3 | 95.9 | 89.7 | 94.2 | 95 | 94.9 | 94.8 | 94.1 | 94.6
SMA America | SB7000US-12 [240V] | 7 kW, 240 Vac Sunny Boy Utility Interactive Inverter with arc detector with display | 7 | 240 | 96 | Y | N |  | 0.72 |  |  | 100 | 310 | 480 | 0.7 | 1.4 | 2.1 | 3.5 | 5.25 | 7 | 93.7 | 96.2 | 96.8 | 96.9 | 96.5 | 95.8 | 96.5 | 92.3 | 96.1 | 96.1 | 96.4 | 96.1 | 95.6 | 96 | 89.3 | 94.3 | 95.1 | 95.6 | 95 | 94.7 | 94.8
SMA America | SB7000US-12 [277V] | 7 kW, 277 Vac Sunny Boy Utility Interactive Inverter with arc detector with display | 7 | 277 | 96 | Y | N |  | 1.41 |  |  | 100 | 310 | 480 | 0.7 | 1.4 | 2.1 | 3.5 | 5.25 | 7 | 93.7 | 96.3 | 96.8 | 97 | 96.5 | 95.9 | 96.5 | 92.5 | 96.1 | 96.3 | 96.5 | 96.2 | 95.6 | 96.1 | 89.3 | 94.2 | 95.2 | 95 | 95.1 | 94.6 | 94.8
SMA America | SB7000TL-US-22 [240V] | 7 kW, 240 Vac Utility Interactive Inverter | 7.01 | 240 | 96.5 | Y | N |  | 0.46 |  |  | 100 | 400 | 480 | 0.7 | 1.4 | 2.1 | 3.5 | 5.26 | 7.01 | 94.9 | 96.2 | 96.4 | 96.3 | 95.9 | 95.2 | 96 | 94.2 | 96.4 | 96.7 | 96.8 | 96.7 | 96.3 | 96.6 | 94.7 | 96.1 | 96.4 | 96.7 | 96.7 | 96.4 | 96.6
SMA America | SB7.0-1SP-US-40 [240V] | 7.0 kW, 240 Vac transformerless Utility Interactive Inverter | 7.1 | 240 | 97 | Y | N |  | 5.1 |  |  | 245 | 365 | 480 | 0.70973 | 1.4195 | 2.1292 | 3.5486 | 5.323 | 7.0973 | 95.1025 | 96.5289 | 96.6286 | 96.7453 | 96.5202 | 96.0676 | 96.5016 | 95.7207 | 97.4129 | 97.4943 | 97.3994 | 96.9791 | 96.5173 | 97.0775 | 93.7611 | 96.5495 | 96.9096 | 97.1923 | 96.9996 | 96.6677 | 96.8607 | 2018-08-01 | 2018-10-15
SMA America | SB7.0-1TP-US-40 [240V] | 7.0 kW, 240 Vac transformerless Utility Interactive Inverter with revenue grade energy meter | 7.1 | 240 | 97 | Y | N |  | 5.1 |  |  | 245 | 365 | 480 | 0.70973 | 1.4195 | 2.1292 | 3.5486 | 5.323 | 7.0973 | 95.1025 | 96.5289 | 96.6286 | 96.7453 | 96.5202 | 96.0676 | 96.5016 | 95.7207 | 97.4129 | 97.4943 | 97.3994 | 96.9791 | 96.5173 | 97.0775 | 93.7611 | 96.5495 | 96.9096 | 97.1923 | 96.9996 | 96.6677 | 96.8607 | 2018-08-01 | 2018-10-15
SMA America | SB8000US [240V] | 8 kW, 240 Vac Sunny Boy Utility Interactive Inverter with display | 7.6 | 240 | 96 | Y | N |  | 0.17 |  |  | 100 | 345 | 480 | 0.76 | 1.52 | 2.28 | 3.8 | 5.7 | 7.6 | 95.04 | 96.48 | 96.84 | 96.82 | 96.5 | 96.01 | 96.53 | 94.59 | 96.19 | 96.61 | 96.63 | 96.3 | 96.29 | 96.33 | 93.13 | 95.28 | 95.83 | 95.98 | 95.72 | 95.94 | 95.67
SMA America | SB8000US-11 [240V] | 8 kW, 240 Vac Sunny Boy Utility Interactive Inverter with display | 7.6 | 240 | 96 | Y | N |  | 0.17 |  |  | 100 | 345 | 480 | 0.76 | 1.52 | 2.28 | 3.8 | 5.7 | 7.6 | 95.04 | 96.48 | 96.84 | 96.82 | 96.5 | 96.01 | 96.53 | 94.59 | 96.19 | 96.61 | 96.63 | 96.3 | 96.29 | 96.33 | 93.13 | 95.28 | 95.83 | 95.98 | 95.72 | 95.94 | 95.67
SMA America | SB8000US-12 [240V] | 8 kW, 240 Vac Sunny Boy Utility Interactive Inverter with arc detector with display | 7.6 | 240 | 96 | Y | N |  | 0.17 |  |  | 100 | 345 | 480 | 0.76 | 1.52 | 2.28 | 3.8 | 5.7 | 7.6 | 95.04 | 96.48 | 96.84 | 96.82 | 96.5 | 96.01 | 96.53 | 94.59 | 96.19 | 96.61 | 96.63 | 96.3 | 96.29 | 96.33 | 93.13 | 95.28 | 95.83 | 95.98 | 95.72 | 95.94 | 95.67
SMA America | SB7700TL-US-22 [240V] | 7 kW, 240 Vac Utility Interactive Inverter | 7.7 | 240 | 96.5 | Y | N |  | 0.464 |  |  | 100 | 400 | 480 | 0.77 | 1.54 | 2.31 | 3.85 | 5.78 | 7.7 | 94.8 | 96.4 | 96.6 | 96.7 | 96.4 | 96 | 96.4 | 94.4 | 97 | 97.3 | 97.3 | 97.1 | 96.8 | 97 | 92.7 | 96.5 | 96.9 | 97.1 | 97 | 96.7 | 96.8
SMA America | SB7.7-1SP-US-40 [240V] | 7.7 kW, 240 Vac transformerless Utility Interactive Inverter | 7.76 | 240 | 97 | Y | N |  | 5.1 |  |  | 270 | 365 | 480 | 0.7758 | 1.5516 | 2.3274 | 3.879 | 5.8185 | 7.758 | 95.6595 | 96.7574 | 97.0783 | 96.9478 | 96.5357 | 96.0095 | 96.6371 | 96.0321 | 97.523 | 97.4427 | 97.3146 | 96.7877 | 96.3456 | 96.9614 | 94.6825 | 96.8252 | 97.0236 | 97.1923 | 96.8751 | 96.7284 | 96.862 | 2018-08-01 | 2018-10-15
SMA America | SB7.7-1TP-US-40 [240V] | 7.7 kW, 240 Vac transformerless Utility Interactive Inverter with revenue grade energy meter | 7.76 | 240 | 97 | Y | N |  | 5.1 |  |  | 270 | 365 | 480 | 0.7758 | 1.5516 | 2.3274 | 3.879 | 5.8185 | 7.758 | 95.6595 | 96.7574 | 97.0783 | 96.9478 | 96.5357 | 96.0095 | 96.6371 | 96.0321 | 97.523 | 97.4427 | 97.3146 | 96.7877 | 96.3456 | 96.9614 | 94.6825 | 96.8252 | 97.0236 | 97.1923 | 96.8751 | 96.7284 | 96.862 | 2018-08-01 | 2018-10-15
SMA America | SB8000TL-US [240V] | 8 kW, 240 Vac Sunny Boy transformerless Utility Interactive Inverter | 8 | 240 | 98 | Y | N |  | 0.14 |  |  | 345 | 379 | 480 | 0.8 | 1.6 | 2.4 | 4 | 6 | 8 | 97.9 | 98.5 | 98.6 | 98.6 | 98.3 | 97.8 | 98.4 | 98 | 98.5 | 98.5 | 98.6 | 98.2 | 97.5 | 98.3 | 97 | 98 | 98.3 | 98.3 | 98.1 | 97.7 | 98.1
SMA America | SB8000TL-US-12 [208V] | 8 kW, 208 Vac Sunny Boy transformerless Utility Interactive Inverter with arc detector | 8 | 208 | 98 | Y | N |  | 0.34 |  |  | 100 | 345 | 480 | 0.8 | 1.6 | 2.4 | 4 | 6 | 8 | 98 | 98.6 | 98.6 | 98.4 | 98 | 97.2 | 98.1 | 97.9 | 98.4 | 98.4 | 98.2 | 97.8 | 97.2 | 97.9 | 97.1 | 97.9 | 97.9 | 98 | 97.7 | 97.2 | 97.7
SMA America | SB8000TL-US-12 [240V] | 8 kW, 240 Vac Sunny Boy transformerless Utility Interactive Inverter with arc detector | 8 | 240 | 98 | Y | N |  | 0.14 |  |  | 100 | 379 | 480 | 0.8 | 1.6 | 2.4 | 4 | 6 | 8 | 97.9 | 98.5 | 98.6 | 98.6 | 98.3 | 97.8 | 98.4 | 98 | 98.5 | 98.5 | 98.6 | 98.2 | 97.5 | 98.3 | 97 | 98 | 98.3 | 98.3 | 98.1 | 97.7 | 98.1
SMA America | SB8000US [277V] | 8 kW, 277 Vac Sunny Boy Utility Interactive Inverter with arc detector with display | 8 | 277 | 96 | Y | N |  | 0.15 |  |  | 100 | 345 | 480 | 0.8 | 1.6 | 2.4 | 4 | 6 | 8 | 95.12 | 96.22 | 96.48 | 96.46 | 96.17 | 95.56 | 96.2 | 94.85 | 95.86 | 96.28 | 96.25 | 95.89 | 95.28 | 95.93 | 93.45 | 95.01 | 95.41 | 95.51 | 95.24 | 94.7 | 95.21
SMA America | SB8000US-11 [277V] | 8 kW, 277 Vac Sunny Boy Utility Interactive Inverter with display | 8 | 277 | 96 | Y | N |  | 0.15 |  |  | 100 | 345 | 480 | 0.8 | 1.6 | 2.4 | 4 | 6 | 8 | 95.12 | 96.22 | 96.48 | 96.46 | 96.17 | 95.56 | 96.2 | 94.85 | 95.86 | 96.28 | 96.25 | 95.89 | 95.28 | 95.93 | 93.45 | 95.01 | 95.41 | 95.51 | 95.24 | 94.7 | 95.21
SMA America | SB8000US-12 [277V] | 8 kW, 277 Vac Sunny Boy Utility Interactive Inverter with arc detector with display | 8 | 277 | 96 | Y | N |  | 0.15 |  |  | 100 | 345 | 480 | 0.8 | 1.6 | 2.4 | 4 | 6 | 8 | 95.12 | 96.22 | 96.48 | 96.46 | 96.17 | 95.56 | 96.2 | 94.85 | 95.86 | 96.28 | 96.25 | 95.89 | 95.28 | 95.93 | 93.45 | 95.01 | 95.41 | 95.51 | 95.24 | 94.7 | 95.21
SMA America | SB9000TL-US [208V] | 9 kW, 208 Vac Sunny Boy transformerless Utility Interactive Inverter | 9 | 208 | 98 | Y | N |  | 0.34 |  |  | 100 | 345 | 480 | 0.9 | 1.8 | 2.7 | 4.5 | 6.75 | 9 | 98.2 | 98.6 | 98.5 | 98.3 | 97.7 | 96.9 | 97.9 | 98 | 98.4 | 98.4 | 98.2 | 97.6 | 96.9 | 97.8 | 97.4 | 97.9 | 98 | 97.9 | 97.5 | 96.9 | 97.6
SMA America | SB9000TL-US [240V] | 9 kW, 240 Vac Sunny Boy transformerless Utility Interactive Inverter | 9 | 240 | 98 | Y | N |  | 0.14 |  |  | 100 | 379 | 480 | 0.9 | 1.8 | 2.7 | 4.5 | 6.75 | 9 | 98 | 98.7 | 98.7 | 98.5 | 98.1 | 97.6 | 98.3 | 98.1 | 98.6 | 98.6 | 98.5 | 97.9 | 97.4 | 98.1 | 97.2 | 98.1 | 98.3 | 98.3 | 98 | 97.6 | 98
SMA America | SB9000TL-US-12 [208V] | 9 kW, 208 Vac Sunny Boy transformerless Utility Interactive Inverter with arc detector | 9 | 208 | 98 | Y | N |  | 0.34 |  |  | 100 | 345 | 480 | 0.9 | 1.8 | 2.7 | 4.5 | 6.75 | 9 | 98.2 | 98.6 | 98.5 | 98.3 | 97.7 | 96.9 | 97.9 | 98 | 98.4 | 98.4 | 98.2 | 97.6 | 96.9 | 97.8 | 97.4 | 97.9 | 98 | 97.9 | 97.5 | 96.9 | 97.6
SMA America | SB9000TL-US-12 [240V] | 9 kW, 240 Vac Sunny Boy transformerless Utility Interactive Inverter with arc detector | 9 | 240 | 98 | Y | N |  | 0.14 |  |  | 100 | 379 | 480 | 0.9 | 1.8 | 2.7 | 4.5 | 6.75 | 9 | 98 | 98.7 | 98.7 | 98.5 | 98.1 | 97.6 | 98.3 | 98.1 | 98.6 | 98.6 | 98.5 | 97.9 | 97.4 | 98.1 | 97.2 | 98.1 | 98.3 | 98.3 | 98 | 97.6 | 98
SMA America | SB10000TL-US [240V] | 10 kW, 240 Vac Sunny Boy transformerless Utility Interactive Inverter | 10 | 240 | 98 | Y | N |  | 0.14 |  |  | 100 | 379 | 480 | 1 | 2 | 3 | 5 | 7.5 | 10 | 98.3 | 98.7 | 98.6 | 98.5 | 97.9 | 97.3 | 98.2 | 98.2 | 98.5 | 98.6 | 98.4 | 97.7 | 97.1 | 98 | 97.4 | 98.2 | 98.3 | 98.3 | 97.8 | 97.3 | 97.9
SMA America | SB10000TL-US-12 [240V] | 10 kW, 240 Vac Sunny Boy transformerless Utility Interactive Inverter with arc detector | 10 | 240 | 98 | Y | N |  | 0.14 |  |  | 100 | 379 | 480 | 1 | 2 | 3 | 5 | 7.5 | 10 | 98.3 | 98.7 | 98.6 | 98.5 | 97.9 | 97.3 | 98.2 | 98.2 | 98.5 | 98.6 | 98.4 | 97.7 | 97.1 | 98 | 97.4 | 98.2 | 98.3 | 98.3 | 97.8 | 97.3 | 97.9
SMA America | SB10000TL-US [208V] | 10 kW, 208 Vac Sunny Boy transformerless Utility Interactive Inverter | 10.1 | 208 | 97.5 | Y | N |  | 0.34 |  |  | 100 | 345 | 480 | 1.01 | 2.02 | 3.03 | 5.05 | 7.58 | 10.1 | 98.3 | 98.6 | 98.5 | 98.3 | 97.5 | 96.5 | 97.8 | 98.1 | 98.4 | 98.3 | 98 | 97.4 | 96.6 | 97.7 | 97.5 | 98 | 98 | 97.9 | 97.3 | 96.7 | 97.5
SMA America | SB10000TL-US-12 [208V] | 10 kW, 208 Vac Sunny Boy transformerless Utility Interactive Inverter with arc detector | 10.1 | 208 | 97.5 | Y | N |  | 0.34 |  |  | 100 | 345 | 480 | 1.01 | 2.02 | 3.03 | 5.05 | 7.58 | 10.1 | 98.3 | 98.6 | 98.5 | 98.3 | 97.5 | 96.5 | 97.8 | 98.1 | 98.4 | 98.3 | 98 | 97.4 | 96.6 | 97.7 | 97.5 | 98 | 98 | 97.9 | 97.3 | 96.7 | 97.5
SMA America | SB11000TL-US [240V] | 11kW, 240 Vac Sunny Boy transformerless Utility Interactive Inverter | 11.1 | 240 | 98 | Y | N |  | 0.14 |  |  | 345 | 379 | 480 | 1.11 | 2.22 | 3.33 | 5.55 | 8.33 | 11.1 | 98.4 | 98.7 | 98.6 | 98.4 | 97.8 | 97 | 98 | 98.3 | 98.5 | 98.3 | 98.3 | 97.5 | 96.8 | 97.8 | 97.6 | 98.2 | 98.3 | 98.2 | 97.7 | 97.1 | 97.9
SMA America | SB11000TL-US-12 [240V] | 11kW, 240 Vac Sunny Boy transformerless Utility Interactive Inverter with arc detector | 11.1 | 240 | 98 | Y | N |  | 0.14 |  |  | 345 | 379 | 480 | 1.11 | 2.22 | 3.33 | 5.55 | 8.33 | 11.1 | 98.4 | 98.7 | 98.6 | 98.4 | 97.8 | 97 | 98 | 98.3 | 98.5 | 98.3 | 98.3 | 97.5 | 96.8 | 97.8 | 97.6 | 98.2 | 98.3 | 98.2 | 97.7 | 97.1 | 97.9
SMA America | STP12000TL-US-10 [480V] | Sunny Tripower TL-US 12 kW, 480Vac, 3-phase, Transformerless Utility Interactive Inverter | 12 | 480 | 97.5 | Y | N |  | 1.79 |  |  | 300 | 675 | 800 | 1.2 | 2.4 | 3.6 | 6 | 9 | 12 | 92.8947 | 95.8254 | 96.4946 | 96.6907 | 96.6273 | 96.507 | 96.4293 | 94.8857 | 96.883 | 97.4944 | 97.777 | 97.8321 | 97.8114 | 97.6137 | 94.1548 | 97.204 | 97.7008 | 98.014 | 98.1838 | 98.1898 | 97.8803 | 2018-08-01 | 2018-10-15
SMA America | STP15000TL-US-10 [480V] | Sunny Tripower TL-US 15 kW, 480Vac, 3-phase, Transformerless Utility Interactive Inverter | 15 | 480 | 97.5 | Y | N |  | 1.79 |  |  | 300 | 675 | 800 | 1.5 | 3 | 4.5 | 7.5 | 11.25 | 15 | 93.8557 | 96.2201 | 96.7314 | 96.6627 | 96.5254 | 96.3471 | 96.448 | 95.4959 | 97.1929 | 97.7963 | 97.8029 | 97.833 | 97.7774 | 97.694 | 95.5529 | 97.5151 | 97.9236 | 98.173 | 98.2148 | 98.1572 | 98.0267 | 2018-08-01 | 2018-10-15
SMA America | STP20000TL-US-10 [480V] | Sunny Tripower TL-US 20 kW, 480Vac, 3-phase, Transformerless Utility Interactive Inverter | 20 | 480 | 97.5 | Y | N |  | 1.79 |  |  | 380 | 695 | 800 | 2 | 4 | 6 | 10 | 15 | 20 | 95.166 | 96.9605 | 97.2062 | 97.0835 | 96.9341 | 96.7051 | 96.9173 | 97.2288 | 98.2895 | 98.5099 | 98.5485 | 97.8368 | 97.7051 | 98.0588 | 96.4929 | 97.8688 | 98.1306 | 98.2198 | 98.1746 | 98.0422 | 98.0897 | 2018-08-01 | 2018-10-15
SMA America | STP24000TL-US-10 [480V] | Sunny Tripower TL-US 24 kW, 480Vac, 3-phase, Transformerless Utility Interactive Inverter | 24.06 | 480 | 98 | Y | N |  | 1.79 |  |  | 450 | 712 | 800 | 2.406 | 4.812 | 7.218 | 12.03 | 18.045 | 24.06 | 96.0825 | 97.4242 | 97.4447 | 97.3151 | 97.1222 | 96.8659 | 97.1621 | 97.4599 | 98.348 | 98.5031 | 98.5314 | 98.4351 | 98.2665 | 98.4117 | 96.9099 | 98.0049 | 98.1886 | 98.2041 | 98.0766 | 97.8823 | 98.0569 | 2018-08-01 | 2018-10-15
SMA America | STP30000TL-US-10 [480V] | Sunny Tripower TL-US 30 kW, 480Vac, 3-phase, Transformerless Utility Interactive Inverter | 30.01 | 480 | 98 | Y | N |  | 1.22 |  |  | 500 | 720 | 800 | 3.001 | 6.002 | 9.003 | 15.005 | 22.5075 | 30.01 | 96.588 | 97.716 | 97.926 | 97.98 | 97.838 | 97.622 | 97.8115 | 97.588 | 98.448 | 98.69 | 98.602 | 98.538 | 98.328 | 98.5167 | 97.026 | 98.06 | 98.452 | 98.386 | 98.282 | 98.08 | 98.2528 | 2018-08-01 | 2018-10-15
SMA America | STP 33-US-41 [480V] | 33.3 kW, 480 Vac, 3-phase, transformerless, Utility Interactive Inverter | 33.3 | 480 | 97.5 | N | N |  | 5.43 |  |  | 330 | 683 | 800 | 3.33 | 6.66 | 9.99 | 16.65 | 24.975 | 33.3 | 94.259 | 96.337 | 96.705 | 96.644 | 96.46 | 96.003 | 96.411 | 94.707 | 96.755 | 97.303 | 97.647 | 97.694 | 97.719 | 97.472 | 95.731 | 97.626 | 98.044 | 98.229 | 98.119 | 97.988 | 98.0064 | 2018-12-17
SMA America | ST36 [208V] | 36 kW, 208 Vac Sunny Tower Utility Interactive Inverter with display | 36 | 208 | 95.5 | Y | N |  | 2.76 |  |  | 250 | 310 | 480 | 3.6 | 7.2 | 10.8 | 18 | 27 | 36 | 92.5 | 95.8 | 96.5 | 96.9 | 96.5 | 95.9 | 96.3 | 91.2 | 95.6 | 95.9 | 96.3 | 96.1 | 95.6 | 95.9 | 88 | 93.5 | 94.8 | 94.6 | 94.9 | 94.6 | 94.5
SMA America | ST36 [240V] | 36 kW, 240 Vac Sunny Tower Utility Interactive Inverter with display | 36 | 240 | 96 | Y | N |  | 0.6 |  |  | 250 | 310 | 480 | 3.6 | 7.2 | 10.8 | 18 | 27 | 36 | 92.6 | 96.1 | 96.5 | 96.8 | 96.7 | 96 | 96.4 | 91.3 | 95.6 | 96 | 96.3 | 96.3 | 95.9 | 96 | 87.9 | 93.6 | 94.8 | 95.1 | 95 | 94.8 | 94.7
SMA America | ST36 [277V] | 36 kW, 277 Vac Sunny Tower Utility Interactive Inverter with display | 36 | 277 | 96 | Y | N |  | 8.46 |  |  | 250 | 310 | 480 | 3.6 | 7.2 | 10.8 | 18 | 27 | 36 | 92.3 | 96 | 96.7 | 97 | 96.7 | 96.5 | 96.5 | 91.3 | 95.6 | 96.2 | 96.4 | 96.4 | 96 | 96.1 | 87.8 | 93.6 | 94.9 | 95.2 | 95.1 | 94.9 | 94.7
SMA America | ST42 [208V] | 42 kW, 208 Vac Sunny Tower Utility Interactive Inverter with display | 42 | 208 | 95.5 | Y | N |  | 0.46 |  |  | 250 | 310 | 480 | 4.2 | 8.4 | 12.6 | 21 | 31.5 | 42 | 94 | 96.3 | 97.1 | 96.7 | 96.2 | 95.4 | 96.3 | 92.7 | 96.1 | 96.1 | 96.2 | 95.9 | 95.3 | 95.9 | 89.7 | 94.2 | 95 | 94.9 | 94.8 | 94.1 | 94.6
SMA America | ST42 [240V] | 42 kW, 240 Vac Sunny Tower Utility Interactive Inverter with display | 42 | 240 | 96 | Y | N |  | 0.6 |  |  | 250 | 310 | 480 | 4.2 | 8.4 | 12.6 | 21 | 31.5 | 42 | 93.7 | 96.2 | 96.8 | 96.9 | 96.5 | 95.8 | 96.5 | 92.3 | 96.1 | 96.1 | 96.4 | 96.1 | 95.6 | 96 | 89.3 | 94.3 | 95.1 | 95.6 | 95 | 94.7 | 94.8
SMA America | ST42 [277V] | 42 kW, 277 Vac Sunny Tower Utility Interactive Inverter with display | 42 | 277 | 96 | Y | N |  | 1.41 |  |  | 250 | 310 | 480 | 4.2 | 8.4 | 12.6 | 21 | 31.5 | 42 | 93.7 | 96.3 | 96.8 | 97 | 96.5 | 95.9 | 96.5 | 92.5 | 96.1 | 96.3 | 96.5 | 96.2 | 95.6 | 96.1 | 89.3 | 94.2 | 95.2 | 95 | 95.1 | 94.6 | 94.8
SMA America | ST48 [240V] | 45.6 kW, 240 Vac Sunny Tower Utility Interactive Inverter with display | 45.6 | 240 | 96 | Y | N |  | 1.01 |  |  | 300 | 345 | 480 | 4.56 | 9.12 | 13.68 | 22.8 | 34.2 | 45.6 | 95 | 96.5 | 96.8 | 96.8 | 96.5 | 96 | 96.5 | 94.6 | 96.2 | 96.6 | 96.6 | 96.3 | 96.3 | 96.3 | 93.1 | 95.3 | 95.8 | 96 | 95.7 | 95.9 | 95.7
SMA America | ST48 [277V] | 48kW, 277 Vac Sunny Tower Utility Interactive Inverter with display | 48 | 277 | 96 | Y | N |  | 0.9 |  |  | 300 | 345 | 480 | 4.8 | 9.6 | 14.4 | 24 | 36 | 48 | 95.1 | 96.2 | 96.5 | 96.5 | 96.2 | 95.6 | 96.2 | 94.9 | 95.9 | 96.3 | 96.2 | 95.9 | 95.3 | 95.9 | 93.5 | 95 | 95.4 | 95.5 | 95.2 | 94.7 | 95.2
SMA America | STP 50-US-41 [480V] | 50 kW, 480 Vac, 3-phase, transformerless, Utility Interactive Inverter | 50.006 | 480 | 97.5 | N | N |  | 5.43 |  |  | 500 | 725 | 800 | 5.0006 | 10.0012 | 15.0018 | 25.003 | 37.5045 | 50.006 | 95.552 | 97.123 | 97.41 | 97.362 | 97.005 | 96.688 | 97.0605 | 96.195 | 97.446 | 97.741 | 97.833 | 97.604 | 97.357 | 97.5919 | 97.062 | 98.074 | 98.229 | 98.119 | 97.965 | 97.765 | 97.9884 | 2018-12-17 | 2019-01-02
SMA America | STP50-US-40 [480V] | Sunny Tripower CORE1 50 kW, 480 Vac, 3-phase, transformerless Utility Interactive Inverter | 50.072 | 480 | 98 | N | N |  | 5.1 |  |  | 500 | 725 | 800 | 5.0072 | 10.0144 | 15.0216 | 25.036 | 37.554 | 50.072 | 94.9771 | 97.1941 | 97.7158 | 97.8318 | 97.5793 | 97.2902 | 97.5109 | 96.4618 | 97.7508 | 98.1301 | 98.2175 | 98.0757 | 97.8645 | 98.0206 | 97.214 | 97.859 | 98.0248 | 97.7868 | 98.1846 | 97.8628 | 98.0107 | 2017-09-01 | 2018-10-15
SMA America | STP 60-US-10 [400V] | 60 kW, 400 Vac Utility Interactive Inverter | 59.86 | 400 | 98 | Y | N |  | 7.1 |  |  | 570 | 630 | 800 | 5.99 | 11.97 | 17.96 | 29.93 | 44.89 | 59.86 | 97.9 | 98.6 | 98.7 | 98.6 | 98.4 | 98.1 | 98.4 | 97.5 | 98.3 | 98.4 | 98.3 | 98.1 | 97.9 | 98.2 | 96.5 | 97.7 | 98 | 98 | 97.7 | 97.5 | 97.8
SMA America | STP 60-US-10 [480V] | 60 kW, 480 Vac Utility Interactive Inverter | 60 | 480 | 98.5 | Y | N |  | 8.16 |  |  | 685 | 710 | 800 | 6 | 12 | 18 | 30 | 45 | 60 | 97.7 | 98.5 | 98.7 | 98.8 | 98.6 | 98.5 | 98.6 | 97.5 | 98.4 | 98.7 | 98.7 | 98.6 | 98.4 | 98.6 | 96.9 | 98.1 | 98.4 | 98.4 | 98.3 | 98.1 | 98.3
SMA America | STP 62-US-41 [480V] | 62.5 kW, 480 Vac, 3-phase, transformerless, Utility Interactive Inverter | 62.5 | 480 | 97.5 | N | N |  | 5.43 |  |  | 500 | 725 | 800 | 6.25 | 12.5 | 18.75 | 31.25 | 46.875 | 62.5 | 96.186 | 97.249 | 97.41 | 97.376 | 97.171 | 96.538 | 97.1756 | 96.699 | 97.65 | 97.804 | 97.788 | 97.42 | 97.048 | 97.5074 | 97.377 | 98.172 | 98.225 | 98.063 | 97.819 | 97.457 | 97.9008 | 2018-12-17
SMA America | SC125U [208V] | 125 kW, 208 Vac, 3-phase, 275-600 Vdc, Utility Interactive Inverter | 125 | 208 | 93.5 | Y | N |  | 26.46 |  |  | 275 | 330 | 480 | 12.5 | 25 | 37.5 | 62.5 | 93.75 | 125 | 92.39 | 94.58 | 94.61 | 95.03 | 93.7 | 93.51 | 94.07 | 91.15 | 93.15 | 93.89 | 94.15 | 93.31 | 93.02 | 93.45 | 88.83 | 91.92 | 93.69 | 93.77 | 93.46 | 92.82 | 93.26
SMA America | SC125U [480V] | 126 kW, 480 Vac, 3-phase, 275-600 Vdc, Utility Interactive Inverter | 125 | 480 | 94 | Y | N |  | 23.92 |  |  | 275 | 330 | 480 | 12.5 | 25 | 37.5 | 62.5 | 93.75 | 125 | 91.65 | 94.17 | 94.58 | 95.13 | 93.96 | 94.07 | 94.2 | 91.52 | 93.69 | 94.02 | 94.54 | 93.7 | 93.49 | 93.82 | 88.88 | 92.99 | 93.31 | 94.32 | 93.36 | 93.23 | 93.35
SMA America | SHP 125-US-20 [480V] | Sunny Highpower PEAK3, 125 kW, 1500 VDC, 480 VAC, 3-phase, transformerless, Utility Interactive Inverter | 125 | 480 | 98.5 | N | N |  | 5.37 |  |  | 705 | 830 | 1200 | 12.5007 | 25.0014 | 37.5021 | 62.5035 | 93.7553 | 125.007 | 98.7556 | 98.9976 | 98.8838 | 98.8276 | 98.6062 | 98.2844 | 98.6955 | 98.4402 | 98.8236 | 98.6952 | 98.6274 | 98.4048 | 98.0538 | 98.4912 | 97.4702 | 98.0424 | 98.235 | 98.2842 | 98.1476 | 97.8116 | 98.1376 | 2019-07-01
SMA America | SHP 150-US-20 [600V] | Sunny Highpower PEAK3, 150 kW, 1500 VDC, 600 VAC, 3-phase, transformerless, Utility Interactive Inverter | 150 | 600 | 99 | N | N |  | 6.63 |  |  | 880 | 960 | 1200 | 15.0079 | 30.0157 | 45.0236 | 75.0393 | 112.559 | 150.0787 | 98.7136 | 99.052 | 98.979 | 98.955 | 98.8152 | 98.582 | 98.8603 | 98.722 | 99.0322 | 99.0162 | 98.9622 | 98.7618 | 98.5232 | 98.8344 | 98.0838 | 98.6294 | 98.704 | 98.7056 | 98.5702 | 98.3194 | 98.5857 | 2019-07-01
SMA America | SC250U [480V] | 250 kW, 480 Vac, 3-phase Utility Interactive Inverter | 250 | 480 | 97 | Y | N | Discontinued | 50 |  |  | 330 | 370 | 480 | 25 | 50 | 75 | 125 | 187.5 | 250 | 93.7 | 95.8 | 96.5 | 97.5 | 97.4 | 96.4 | 97 | 95 | 95.6 | 96.3 | 97.4 | 97.3 | 96.5 | 97 | 92.2 | 95 | 95.9 | 97.2 | 97 | 96.4 | 96.6 |  | 2018-04-16
SMA America | SC500HE-US-MV (with Cooper transformer) | 500 kW, 3-phase, Utility Interactive Inverter with Medium Voltage Cooper transformer | 500 |  | 97 | Y | N |  | 110 |  |  | 330 | 370 | 480 | 50 | 100 | 150 | 250 | 375 | 500 | 96.03 | 97.64 | 97.93 | 97.88 | 97.43 | 96.82 | 97.51 | 95.31 | 97.24 | 97.65 | 97.73 | 97.28 | 96.69 | 97.31 | 93.33 | 96.28 | 96.95 | 97.23 | 96.95 | 96.36 | 96.8
SMA America | SC500HE-US-MV (with NEMA TP-1 transformer) | 500 kW, 3-phase, Utility Interactive Inverter with Medium Voltage NEMA NEMA TP1 transformer | 500 |  | 96.5 | Y | N |  | 110 |  |  | 330 | 370 | 480 | 50 | 100 | 150 | 250 | 375 | 500 | 94.09 | 96.56 | 97.1 | 97.18 | 96.73 | 96.04 | 96.72 | 93.38 | 96.16 | 96.83 | 97.03 | 96.58 | 95.91 | 96.52 | 91.44 | 95.21 | 96.13 | 96.53 | 96.24 | 95.58 | 96.01
SMA America | SC500U [480V] | 500 kW, 480 Vac, 3-phase Utility Interactive Inverter | 506.7 | 480 | 97 | Y | N | Discontinued | 79.3 |  |  | 330 | 370 | 480 | 50.67 | 101.3 | 152 | 253.4 | 380 | 506.7 | 0.949 | 0.9678 | 0.9725 | 0.9737 | 0.9722 | 0.9667 | 0.9711 | 0.946 | 0.9652 | 0.9707 | 0.9725 | 0.9711 | 0.9659 | 0.9698 | 0.938 | 0.9601 | 0.9669 | 0.9694 | 0.9686 | 0.9642 | 0.9667 |  | 2018-04-16
SMA America | SC500CP-US (with ABB EcoDry Ultra transformer) | 500 kW, 3-phase, Utility Interactive Inverter with Medium Voltage ABB transformer | 514 |  | 97 | Y | N |  | 307.9 |  |  | 430 | 530 | 820 | 51.4 | 102.8 | 154.2 | 257 | 385.5 | 514 | 96.1 | 97.4 | 97.8 | 97.8 | 97.6 | 97.2 | 97.6 | 95.3 | 97 | 97.4 | 97.6 | 97.4 | 97 | 97.3 | 93.2 | 95.7 | 96.5 | 97 | 96.8 | 96.6 | 96.6
SMA America | SC500CP-US 600V (with ABB transformer) | 500 kW, 3-phase, Utility Interactive Inverter with Medium Voltage ABB transformer | 516.2 |  | 97 | Y | N |  | 185.5 |  |  | 360 | 391 | 480 | 51.62 | 103.2 | 154.9 | 258.1 | 387.1 | 516.2 | 94.8 | 96.8 | 97.5 | 97.6 | 97.1 | 96.6 | 97.1 | 94.3 | 96.5 | 97.3 | 97.5 | 96.9 | 96.5 | 96.9 | 93.1 | 95.8 | 96.7 | 97.1 | 96.6 | 96.2 | 96.5
SMA America | SC630CP-US (with ABB EcoDry Ultra transformer) | 630 kW, 3-phase, Utility Interactive Inverter with Medium Voltage ABB transformer | 653 |  | 97.5 | Y | N |  | 371.9 |  |  | 500 | 580 | 820 | 65.3 | 130.6 | 195.9 | 326.5 | 489.8 | 653 | 96.2 | 97.5 | 97.8 | 97.9 | 97.7 | 97.4 | 97.7 | 95.6 | 97.2 | 97.6 | 97.8 | 97.5 | 97.2 | 97.5 | 94.1 | 96.3 | 96.9 | 97.3 | 97.1 | 96.8 | 97
SMA America | SC720CP-US (with ABB EcoDry Ultra transformer) | 720 kW, 3-phase, Utility Interactive Inverter with Medium Voltage ABB transformer | 742 |  | 97.5 | Y | N |  | 363.8 |  |  | 515 | 592 | 820 | 74.2 | 148.4 | 222.6 | 371 | 556.5 | 742 | 96.3 | 97.6 | 97.9 | 97.9 | 97.6 | 97.3 | 97.7 | 95.9 | 97.3 | 97.7 | 97.8 | 97.6 | 97.2 | 97.5 | 94.5 | 96.5 | 97.1 | 97.4 | 97.2 | 96.8 | 97.1
SMA America | SC750CP-US (with ABB EcoDry Ultra transformer) | 750 kW, 3-phase, Utility Interactive Inverter with Medium Voltage ABB transformer | 770 |  | 97.5 | Y | N |  | 364.7 |  |  | 545 | 614 | 820 | 76.98 | 154 | 230.9 | 384.9 | 577.4 | 769.8 | 96.4 | 97.6 | 97.9 | 98 | 97.7 | 97.3 | 97.7 | 95.9 | 97.3 | 97.7 | 97.9 | 97.7 | 97.3 | 97.6 | 94.7 | 96.6 | 97.2 | 97.5 | 97.3 | 97 | 97.2
SMA America | SC800CP-US (with ABB EcoDry Ultra transformer) | 800 kW, 3-phase, Utility Interactive Inverter with Medium Voltage ABB transformer | 823 |  | 97.5 | Y | N |  | 362.9 |  |  | 570 | 633 | 820 | 82.3 | 164.6 | 246.9 | 411.5 | 617.3 | 823 | 96.4 | 97.6 | 98 | 98.1 | 97.8 | 97.4 | 97.8 | 96 | 97.4 | 97.8 | 98 | 97.7 | 97.3 | 97.7 | 94.9 | 96.8 | 97.4 | 97.6 | 97.4 | 97 | 97.3
SMA America | SC850CP-US (with ABB EcoDry Ultra transformer) | 850 kW, 1000 Vdc, 3-phase, Utility Interactive Inverter with Medium Voltage ABB transformer | 888 |  | 97.5 | Y | N |  | 202.3 |  |  | 620 | 671 | 820 | 88.8 | 177.6 | 266.4 | 444 | 666 | 888 | 95.6 | 97.2 | 97.9 | 98 | 97.8 | 97.4 | 97.7 | 95.3 | 97.1 | 97.7 | 97.9 | 97.7 | 97.3 | 97.6 | 94.5 | 96.6 | 97.4 | 97.6 | 97.5 | 97.1 | 97.3
SMA America | SC900CP-US (with ABB EcoDry Ultra transformer) | 900 kW, 1000 Vdc, 3-phase, Utility Interactive Inverter with Medium Voltage ABB transformer | 942 |  | 97.5 | Y | N |  | 198.2 |  |  | 655 | 697 | 820 | 94.2 | 188.4 | 282.6 | 471 | 706.5 | 942 | 95.6 | 97.2 | 97.9 | 98 | 97.8 | 97.5 | 97.7 | 95.3 | 97 | 97.8 | 97.9 | 97.8 | 97.4 | 97.6 | 94.7 | 96.7 | 97.5 | 97.7 | 97.6 | 97.2 | 97.4
SMA America | SC-1850-US [385V] | Sunny Central 1850 kW, 385 Vac Utility Interactive Inverter | 1661 | 385 | 97 | Y | N | Weighted efficiency includes transformer efficiency of Eaton 34.5kV. | 294 |  |  | 570 | 665 | 950 | 166.1 | 332.2 | 498.3 | 830.5 | 1245.75 | 1661 | 96.09 | 97.54 | 97.81 | 97.79 | 97.59 | 97.25 | 97.58 | 95.5 | 97.22 | 97.55 | 97.62 | 97.45 | 97.13 | 97.39 | 93.24 | 96.22 | 96.74 | 97.07 | 96.98 | 96.67 | 96.77 | 2018-04-16 | 2018-10-15
SMA America | SC-2200-US [385V] | Sunny Central 2200 kW, 385 Vac Utility Interactive Inverter | 2079 | 385 | 97 | Y | N | Weighted efficiency includes transformer efficiency of Eaton 34.5kV. | 297 |  |  | 570 | 665 | 950 | 207.9 | 415.8 | 623.7 | 1039.5 | 1559.25 | 2079 | 96.63 | 97.68 | 97.8 | 97.69 | 97.33 | 96.68 | 97.42 | 96.07 | 97.38 | 97.58 | 97.53 | 97.21 | 96.57 | 97.25 | 94.45 | 96.53 | 96.96 | 97.05 | 96.73 | 96.18 | 96.69 | 2018-04-16 | 2018-10-15
Solar Liberty | SLX 3000 [208V] | 2.8 kW, 208 Vac Utility Interactive Inverter | 2.81 | 208 | 95.5 | Y | N |  | 0.35 |  |  | 100 | 275 | 400 | 0.28 | 0.56 | 0.84 | 1.41 | 2.11 | 2.81 | 89.4 | 94.4 | 95.5 | 96.2 | 96.2 | 95.9 | 95.8 | 88.7 | 93.8 | 95.2 | 95.9 | 96 | 95.7 | 95.5 | 86.5 | 92.1 | 94 | 95.1 | 95.3 | 95.2 | 94.6
Solar Liberty | SLX 3000 [240V] | 3 kW, 240 Vac Utility Interactive Inverter | 3.01 | 240 | 96 | Y | N |  | 0.47 |  |  | 100 | 275 | 400 | 0.3 | 0.6 | 0.9 | 1.51 | 2.26 | 3.01 | 90.6 | 95 | 96 | 96.6 | 96.6 | 96.2 | 96.2 | 89.8 | 94.4 | 95.6 | 96.4 | 96.4 | 96 | 95.9 | 87.7 | 92.9 | 94.5 | 95.6 | 95.8 | 95.5 | 95.1
Solar Liberty | SLX 4000 [208V] | 3.5 kW, 208 Vac Utility Interactive Inverter | 3.51 | 208 | 95.5 | Y | N |  | 0.35 |  |  | 100 | 275 | 400 | 0.35 | 0.7 | 1.05 | 1.76 | 2.63 | 3.51 | 91.3 | 95.1 | 96 | 96.3 | 96.1 | 95.4 | 95.9 | 90.4 | 94.7 | 95.7 | 96 | 95.9 | 95.3 | 95.6 | 88.4 | 93.3 | 94.7 | 95.3 | 95.3 | 94.7 | 94.8
Solar Liberty | SLX 4000 [240V] | 4 kW, 240 Vac Utility Interactive Inverter | 4.02 | 240 | 96 | Y | N |  | 0.47 |  |  | 100 | 275 | 400 | 0.4 | 0.8 | 1.21 | 2.01 | 3.02 | 4.02 | 92.6 | 95.7 | 96.4 | 96.5 | 96.3 | 95.5 | 96.1 | 91.8 | 95.3 | 96.1 | 96.3 | 96.1 | 95.4 | 95.9 | 90 | 94.1 | 95.2 | 95.7 | 95.5 | 94.9 | 95.2
Solar Liberty | SLX 5000 [208V] | 4.4 kW, 208 Vac Utility Interactive Inverter | 4.4 | 208 | 96 | Y | N |  | 0.47 |  |  | 100 | 275 | 400 | 0.44 | 0.88 | 1.32 | 2.2 | 3.3 | 4.4 | 92.9 | 95.8 | 96.5 | 96.8 | 96.6 | 95.9 | 96.4 | 92.2 | 95.3 | 96.2 | 96.4 | 96.2 | 95.5 | 96 | 90.1 | 93.9 | 95 | 95.7 | 95.6 | 95.2 | 95.2
Solar Liberty | SLX 5000 [240V] | 5 kW, 240 Vac Utility Interactive Inverter | 4.6 | 240 | 95.5 | Y | N |  | 13.95 |  |  | 100 | 275 | 400 | 0.46 | 0.92 | 1.38 | 2.3 | 3.45 | 4.6 | 93.5 | 95.6 | 96.2 | 96.1 | 95.9 | 95.3 | 95.9 | 93 | 95.3 | 96 | 95.9 | 95.9 | 95.2 | 95.7 | 91.7 | 94.4 | 95.2 | 95.7 | 95.5 | 95 | 95.3
Solar Liberty | SLX 5300 [208V] | 4.6 kW, 208 Vac Utility Interactive Inverter | 5.01 | 208 | 96 | Y | N |  | 0.47 |  |  | 100 | 275 | 400 | 0.5 | 1 | 1.5 | 2.51 | 3.76 | 5.01 | 93.9 | 96.1 | 96.6 | 96.7 | 96.4 | 95.7 | 96.3 | 92.7 | 95.8 | 96.4 | 96.5 | 96.2 | 95.6 | 96.1 | 91.2 | 94.7 | 95.7 | 96.1 | 95.9 | 95.4 | 95.7
Solar Liberty | SLX 5300 [240V] | 5.3 kW, 240 Vac Utility Interactive Inverter | 5.3 | 240 | 96 | Y | N |  | 14 |  |  | 100 | 275 | 400 | 0.53 | 1.06 | 1.59 | 2.65 | 3.98 | 5.3 | 94.3 | 96.1 | 96.3 | 96.4 | 96 | 95.2 | 96 | 93.8 | 95.9 | 96.1 | 96.3 | 95.8 | 95.2 | 95.8 | 92.5 | 95 | 95.7 | 96 | 95.5 | 94.9 | 95.4
Solar Liberty | SLX 6500 [208V] | 6.43 kW, 208 Vac Utility Interactive Inverter | 6.43 | 208 | 95.5 | Y | N |  | 0.5 |  |  | 100 | 275 | 400 | 0.64 | 1.29 | 1.93 | 3.22 | 4.82 | 6.43 | 93.3 | 95.6 | 96 | 96 | 95.6 | 94.8 | 95.6 | 92.9 | 95.4 | 95.9 | 95.9 | 95.5 | 94.8 | 95.5 | 91.6 | 94.8 | 95.4 | 95.6 | 95.2 | 94.6 | 95.1
Solar Liberty | SLX 6500 [240V] | 6.45 kW, 240 Vac Utility Interactive Inverter | 6.45 | 240 | 96 | Y | N |  | 0.65 |  |  | 100 | 275 | 400 | 0.65 | 1.29 | 1.94 | 3.23 | 4.84 | 6.45 | 93.5 | 95.9 | 96.3 | 96.3 | 96 | 95.4 | 96 | 93.1 | 95.7 | 96.2 | 96.3 | 96 | 95.3 | 95.9 | 91.8 | 95 | 95.6 | 95.9 | 95.7 | 95.2 | 95.5
Solar Liberty | SLX 6500 [277V] | 6.45 kW, 277 Vac Utility Interactive Inverter | 6.45 | 277 | 96 | Y | N |  | 0.9 |  |  | 100 | 275 | 400 | 0.645 | 1.29 | 1.935 | 3.225 | 4.838 | 6.45 | 93.82 | 96.14 | 96.54 | 96.67 | 96.41 | 95.82 | 96.33 | 93.37 | 95.93 | 96.36 | 96.54 | 96.31 | 95.75 | 96.2 | 92.05 | 95.29 | 95.88 | 96.19 | 96.04 | 95.56 | 95.83
Solar Liberty | SLX 7500 [208V] | 7.43 kW, 208 Vac Utility Interactive Inverter | 7.43 | 208 | 95.5 | Y | N |  | 0.52 |  |  | 100 | 275 | 400 | 0.74 | 1.49 | 2.23 | 3.72 | 5.57 | 7.43 | 94.1 | 96 | 96.2 | 96.1 | 95.4 | 94.6 | 95.6 | 93.7 | 95.7 | 96 | 96 | 95.3 | 94.5 | 95.5 | 92.5 | 95.1 | 95.6 | 95.6 | 95.1 | 94.3 | 95.1
Solar Liberty | SLX 7500 [240V] | 7.45 kW, 240 Vac Utility Interactive Inverter | 7.45 | 240 | 96 | Y | N |  | 0.68 |  |  | 100 | 275 | 400 | 0.745 | 1.49 | 2.235 | 3.725 | 5.588 | 7.45 | 94.32 | 96.24 | 96.54 | 96.47 | 95.87 | 95.16 | 96 | 93.91 | 96.02 | 96.34 | 96.34 | 95.81 | 95.1 | 95.89 | 92.69 | 95.39 | 95.93 | 95.99 | 95.52 | 94.9 | 95.52
Solar Liberty | SLX 7500 [277V] | 7.46 kW, 277 Vac Utility Interactive Inverter | 7.46 | 277 | 96 | Y | N |  | 0.9 |  |  | 100 | 275 | 400 | 0.746 | 1.492 | 2.238 | 3.73 | 5.595 | 7.46 | 94.44 | 96.42 | 96.66 | 96.61 | 96.24 | 95.52 | 96.27 | 94.04 | 96.11 | 96.5 | 96.56 | 96.17 | 95.46 | 96.17 | 92.87 | 95.53 | 96.08 | 96.19 | 95.89 | 95.3 | 95.81
Solar Power | YS-1500TL [208V] | 1500 W, 208 Vac Utility Interactive Inverter | 1.5 | 208 | 96 | Y | N |  | 0.07 |  |  | 100 | 330 | 360 | 0.15 | 0.3 | 0.45 | 0.75 | 1.12 | 1.5 | 91.1 | 94.9 | 96 | 96.4 | 96.2 | 96 | 95.9 | 91.7 | 95.5 | 96.5 | 96.8 | 96.7 | 96.5 | 96.4 | 91.5 | 95.2 | 96.2 | 96.7 | 96.7 | 96.5 | 96.3
Solar Power | YS-1500TL [240V] | 1500 W, 240 Vac Utility Interactive Inverter | 1.62 | 240 | 96 | Y | N |  | 0.11 |  |  | 100 | 330 | 360 | 0.16 | 0.32 | 0.49 | 0.81 | 1.21 | 1.62 | 89.5 | 94.2 | 95.5 | 96.3 | 96.3 | 96 | 95.8 | 90.2 | 94.7 | 95.9 | 96.6 | 96.6 | 96.5 | 96.2 | 91.3 | 95.4 | 96.5 | 97 | 97 | 96.8 | 96.6
Solar Power | YS-1500TL [277V] | 1500 W, 277 Vac Utility Interactive Inverter | 1.62 | 277 | 96 | Y | N |  | 0.13 |  |  | 100 | 330 | 360 | 0.16 | 0.32 | 0.48 | 0.81 | 1.21 | 1.62 | 89.2 | 93.5 | 95 | 96.1 | 96.2 | 96.1 | 95.6 | 89.3 | 94 | 95.6 | 96.4 | 96.6 | 96.7 | 96 | 89.3 | 94.3 | 95.7 | 96.6 | 96.8 | 96.8 | 96.2
Solar Power | YS-2000TL [208V] | 2000 W, 208 Vac Utility Interactive Inverter | 1.81 | 208 | 96.5 | Y | N |  | 0.09 |  |  | 100 | 360 | 400 | 0.18 | 0.36 | 0.54 | 0.9 | 1.35 | 1.81 | 92.3 | 95.4 | 96 | 96.4 | 96.3 | 96 | 96.1 | 92.8 | 96 | 96.6 | 96.8 | 96.6 | 96.4 | 96.5 | 92.7 | 95.7 | 96.3 | 96.6 | 96.5 | 96.3 | 96.3
Solar Power | YS-2000TL [277V] | 2000 W, 277 Vac Utility Interactive Inverter | 2 | 277 | 96.5 | Y | N |  | 0.14 |  |  | 100 | 360 | 400 | 0.2 | 0.4 | 0.6 | 1 | 1.5 | 2 | 89.3 | 93.7 | 95.1 | 96 | 96.3 | 96.1 | 95.7 | 91.1 | 94.8 | 95.9 | 96.5 | 96.8 | 96.8 | 96.3 | 92.9 | 96.1 | 96.9 | 97.3 | 97.4 | 97.3 | 97.1
Solar Power | YS-2000TL [240V] | 2000 W, 240 Vac Utility Interactive Inverter | 2.01 | 240 | 96.5 | Y | N |  | 0.1 |  |  | 100 | 360 | 400 | 0.2 | 0.4 | 0.6 | 1 | 1.5 | 2.01 | 91.4 | 94.6 | 95.7 | 96.3 | 96.4 | 96.1 | 96 | 92.9 | 96.1 | 96.8 | 97.1 | 97.1 | 96.9 | 96.9 | 92.3 | 95.8 | 96.6 | 96.9 | 97 | 96.8 | 96.7
Solar Power | YS-3000TL [208V] | 3000 W, 208 Vac Utility Interactive Inverter | 2.5 | 208 | 96.5 | Y | N |  | 0.1 |  |  | 100 | 360 | 400 | 0.25 | 0.5 | 0.75 | 1.25 | 1.88 | 2.5 | 92.3 | 95.4 | 96.2 | 96.5 | 96.2 | 95.8 | 96 | 93.9 | 96.2 | 96.8 | 97 | 96.8 | 96.4 | 96.7 | 92.7 | 95.8 | 96.5 | 96.8 | 96.6 | 96.3 | 96.4
Solar Power | YS-3000TL [240V] | 3000 W, 240 Vac Utility Interactive Inverter | 2.8 | 240 | 96.5 | Y | N |  | 0.15 |  |  | 100 | 360 | 400 | 0.28 | 0.56 | 0.84 | 1.4 | 2.1 | 2.8 | 91 | 94.4 | 95.6 | 96.4 | 96.4 | 96.1 | 96 | 94 | 96.6 | 97.1 | 97.5 | 97.4 | 97 | 97.2 | 93.3 | 96.1 | 96.8 | 97.4 | 97.3 | 97 | 97
Solar Power | YS-3000TL [277V] | 3000 W, 277 Vac Utility Interactive Inverter | 2.8 | 277 | 96.5 | Y | N |  | 0.19 |  |  | 100 | 360 | 400 | 0.28 | 0.56 | 0.84 | 1.4 | 2.1 | 2.8 | 89.4 | 93.4 | 94.8 | 95.9 | 96.2 | 96 | 95.5 | 91.6 | 95.2 | 96.3 | 96.9 | 97 | 96.8 | 96.6 | 94.1 | 96.6 | 97.3 | 97.7 | 97.6 | 97.4 | 97.4
Solar Power | YS-3600MTL [208V] | 3600 W, 208 Vac Utility Interactive Inverter | 3.6 | 208 | 97 | Y | N |  | 0.23 |  |  | 100 | 375 | 450 | 0.36 | 0.72 | 1.08 | 1.8 | 2.7 | 3.6 | 91.9 | 94.6 | 95.5 | 96.4 | 96.5 | 96.3 | 96.1 | 94.5 | 96.7 | 97.3 | 97.6 | 97.4 | 97.2 | 97.3 | 93 | 96 | 96.9 | 97.3 | 97.3 | 97.1 | 97
Solar Power | YS-3600MTL [240V] | 3600 W, 240 Vac Utility Interactive Inverter | 3.6 | 240 | 97 | Y | N |  | 0.31 |  |  | 100 | 375 | 450 | 0.36 | 0.72 | 1.08 | 1.8 | 2.7 | 3.6 | 92.4 | 94.6 | 95.5 | 96.5 | 96.7 | 96.7 | 96.2 | 95.3 | 97.1 | 97.5 | 97.8 | 97.7 | 97.5 | 97.6 | 94.2 | 96.5 | 97.1 | 97.5 | 97.6 | 97.4 | 97.3
Solar Power | YS-3600MTL [277V] | 3600 W, 277 Vac Utility Interactive Inverter | 3.61 | 277 | 97 | Y | N |  | 0.4 |  |  | 100 | 375 | 450 | 0.36 | 0.72 | 1.08 | 1.8 | 2.7 | 3.61 | 91.2 | 93.9 | 94.7 | 96.1 | 96.6 | 96.6 | 95.9 | 93.4 | 96 | 96.6 | 97.4 | 97.5 | 97.5 | 97.2 | 94.5 | 96.8 | 97.4 | 97.9 | 98 | 97.9 | 97.7
Solar Power | YS-4200MTL [208V] | 4200 W, 208 Vac Utility Interactive Inverter | 4.2 | 208 | 97 | Y | N |  | 0.25 |  |  | 100 | 375 | 450 | 0.42 | 0.84 | 1.26 | 2.1 | 3.15 | 4.2 | 91.6 | 94.4 | 95.5 | 96.6 | 96.8 | 96.7 | 96.3 | 94.1 | 96.5 | 97.1 | 97.3 | 97.1 | 96.7 | 97 | 93.6 | 96.2 | 96.8 | 97.2 | 97.5 | 97.1 | 97.1
Solar Power | YS-4200MTL [240V] | 4200 W, 240 Vac Utility Interactive Inverter | 4.2 | 240 | 97 | Y | N |  | 0.4 |  |  | 100 | 375 | 450 | 0.42 | 0.84 | 1.26 | 2.1 | 3.15 | 4.2 | 91.4 | 94.4 | 96 | 96.6 | 96.8 | 96.6 | 96.3 | 92.1 | 95.2 | 96.3 | 97.3 | 97.6 | 97.1 | 97 | 93.6 | 96.3 | 97.2 | 97.6 | 97.6 | 97.6 | 97.4
Solar Power | YS-4200MTL [277V] | 4200 W, 277 Vac Utility Interactive Inverter | 4.21 | 277 | 97 | Y | N |  | 0.33 |  |  | 100 | 375 | 450 | 0.42 | 0.84 | 1.26 | 2.1 | 3.15 | 4.21 | 92.4 | 94.6 | 95.5 | 96.5 | 96.7 | 96.7 | 96.2 | 95.3 | 97.1 | 97.5 | 97.8 | 97.7 | 97.5 | 97.6 | 94.2 | 96.5 | 97.1 | 97.5 | 97.6 | 97.4 | 97.3
Solar Power | YS-5000MTL [208V] | 5000 W, 208 Vac Utility Interactive Inverter | 4.6 | 208 | 97 | Y | N |  | 0.26 |  |  | 100 | 375 | 450 | 0.46 | 0.92 | 1.38 | 2.3 | 3.45 | 4.6 | 94.7 | 96.5 | 96.8 | 96.9 | 96.5 | 96 | 96.5 | 95.4 | 97 | 97.3 | 97.4 | 97 | 96.5 | 97 | 94.3 | 96.4 | 96.9 | 97.1 | 97 | 96.5 | 96.8
Solar Power | YS-5000MTL [240V] | 5000 W, 240 Vac Utility Interactive Inverter | 4.6 | 240 | 97 | Y | N |  | 0.36 |  |  | 100 | 375 | 450 | 0.46 | 0.92 | 1.38 | 2.3 | 3.45 | 4.6 | 92.8 | 95.2 | 96 | 96.7 | 96.6 | 96.4 | 96.3 | 95.8 | 97.3 | 97.7 | 97.8 | 97.5 | 97.1 | 97.5 | 96.7 | 96.7 | 97.2 | 97.5 | 97.4 | 97.1 | 97.3
Solar Power | YS-5000MTL [277V] | 5000 W, 277 Vac Utility Interactive Inverter | 4.6 | 277 | 97 | Y | N |  | 0.43 |  |  | 100 | 375 | 450 | 0.46 | 0.92 | 1.38 | 2.3 | 3.45 | 4.6 | 92.2 | 94.9 | 95.6 | 96.6 | 96.8 | 96.8 | 96.4 | 94.6 | 96.7 | 97.2 | 97.6 | 97.6 | 97.4 | 97.4 | 95.4 | 97.1 | 97.6 | 97.9 | 97.8 | 97.7 | 97.7
Solar Power | YS-8000TL [208V] | 8000 W, 208 Vac Utility Interactive Inverter | 8.07 | 208 | 96.5 | Y | N |  | 0.053 |  |  | 100 | 345 | 480 | 0.81 | 1.61 | 2.42 | 4.03 | 6.05 | 8.07 | 95.6 | 96.7 | 97.1 | 97.2 | 97.1 | 96.9 | 97.1 | 94.9 | 96.3 | 96.8 | 97 | 96.9 | 96.8 | 96.8 | 92.6 | 95 | 95.8 | 96.4 | 96.4 | 96.2 | 96.1
Solar Power | YS-8000TL [240V] | 8000 W, 240 Vac Utility Interactive Inverter | 8.08 | 240 | 97 | Y | N |  | 0.075 |  |  | 100 | 380 | 480 | 0.81 | 1.62 | 2.42 | 4.04 | 6.06 | 8.08 | 95.4 | 96.7 | 97.1 | 97.4 | 97.4 | 97.2 | 97.2 | 95.1 | 96.6 | 97 | 97.3 | 97.3 | 97.2 | 97.1 | 93.2 | 95.5 | 96.2 | 96.8 | 96.4 | 96.9 | 96.3
Solar Power | YS-9000TL [208V] | 9000 W, 208 Vac Utility Interactive Inverter | 9.08 | 208 | 96.5 | Y | N |  | 0.053 |  |  | 100 | 345 | 480 | 0.91 | 1.82 | 2.72 | 4.54 | 6.81 | 9.08 | 95.9 | 96.8 | 97.1 | 97.2 | 97 | 96.8 | 97 | 95.3 | 96.5 | 96.9 | 97 | 97 | 96.7 | 96.9 | 93.1 | 95.3 | 96 | 96.4 | 96.4 | 96.2 | 96.2
Solar Power | YS-9000TL [240V] | 9000 W, 240 Vac Utility Interactive Inverter | 9.08 | 240 | 97 | Y | N |  | 0.075 |  |  | 100 | 380 | 480 | 0.91 | 1.82 | 2.72 | 4.54 | 6.81 | 9.08 | 95.8 | 96.9 | 97.2 | 97.4 | 97.4 | 97.2 | 97.2 | 95.5 | 96.8 | 97.1 | 97.3 | 97.3 | 97.1 | 97.2 | 93.8 | 95.8 | 96.4 | 96.7 | 96.9 | 96.8 | 96.6
Solar Power | YS-10000TL [208V] | 10000 W, 208 Vac Utility Interactive Inverter | 10.09 | 208 | 96.5 | Y | N |  | 0.053 |  |  | 100 | 345 | 480 | 1.01 | 2.02 | 3.03 | 5.04 | 7.57 | 10.09 | 95.8 | 96.9 | 97.1 | 97.2 | 97 | 96.6 | 97 | 95.5 | 96.6 | 96.9 | 97 | 96.9 | 96.5 | 96.8 | 93.1 | 95.4 | 96.1 | 96.4 | 96.3 | 96 | 96.1
Solar Power | YS-10000TL [240V] | 10000 W, 240 Vac Utility Interactive Inverter | 10.09 | 240 | 97 | Y | N |  | 0.075 |  |  | 100 | 380 | 480 | 1.01 | 2.02 | 3.03 | 5.04 | 7.56 | 10.09 | 96 | 97 | 97.3 | 97.4 | 97.3 | 97.1 | 97.2 | 95.8 | 96.9 | 97.2 | 97.4 | 97.3 | 97 | 97.2 | 94.3 | 96 | 96.5 | 96.9 | 96.8 | 96.7 | 96.7
Solar Power | YS-11000TL [240V] | 11000 W, 240 Vac Utility Interactive Inverter | 11.7 | 240 | 97 | Y | N |  | 0.075 |  |  | 356 | 380 | 480 | 1.17 | 2.34 | 3.51 | 5.85 | 8.775 | 11.7 | 96 | 97 | 97.3 | 97.3 | 97.2 | 97 | 97.2 | 95.8 | 96.9 | 97.2 | 97.3 | 97.2 | 96.9 | 97.1 | 94.3 | 96 | 96.5 | 97 | 96.8 | 96.5 | 96.6
Solarbine | S6T AC [120V] | 212 W, 120 Vac Inverter | 0.21 | 120 | 94.5 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0 |  |  | 36 | 50 | 55 | 0.021 | 0.04 | 0.06 | 0.11 | 0.16 | 0.21 | 87.9 | 94.4 | 95.8 | 95.7 | 94.8 | 93.5 | 94.8 | 85.2 | 92.5 | 94.6 | 95.3 | 95.1 | 94.2 | 94.5 | 83.6 | 92 | 94.3 | 94.9 | 94.9 | 93.9 | 94.2
SolarBridge Technologies | P235HV-240 [240V] | 225 W, 240 Vac Inverter | 0.225 | 240 | 94.5 | N | Y |  | 0.03 | 0.225 | 0.03 | 30 | 43 | 50 | 0.02 | 0.05 | 0.07 | 0.11 | 0.17 | 0.23 | 86.6 | 91.6 | 93.3 | 94.6 | 94.7 | 94.5 | 94 | 85.9 | 91.3 | 93.2 | 94.9 | 95.3 | 95.3 | 94.4 | 87.3 | 90.7 | 93.3 | 95 | 95.5 | 95.4 | 94.5
SolarBridge Technologies | P235LV-240 [240V] | 225 W, 240 Vac Inverter | 0.225 | 240 | 94.5 | N | Y |  | 0.02 |  |  | 21 | 31.5 | 35 | 0.0225 | 0.045 | 0.0675 | 0.1125 | 0.1688 | 0.225 | 86.98 | 91.98 | 93.37 | 94.53 | 94.52 | 94.11 | 93.93 | 85.82 | 91.51 | 93.51 | 95.05 | 96.08 | 95.32 | 94.88 | 85.39 | 91.3 | 93.34 | 94.9 | 95.33 | 95.5 | 94.41
SolarBridge Technologies | SBT250-NA240-A111 [240V] | 225 W, 240 Vac Inverter, 1-phase ACPV | 0.225 | 240 | 94.5 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.02 |  |  | 21 | 31.5 | 35 | 0.02 | 0.05 | 0.07 | 0.11 | 0.17 | 0.23 | 87 | 92 | 93.4 | 94.5 | 94.5 | 94.1 | 93.9 | 85.8 | 91.5 | 93.5 | 95.1 | 96.1 | 95.3 | 94.9 | 85.4 | 91.3 | 93.3 | 94.9 | 95.3 | 95.5 | 94.4
SolarBridge Technologies | SBT250-NA240-A311 [240V] | 225 W, 240 Vac Inverter, 1-phase ACPV | 0.225 | 240 | 94.5 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.02 |  |  | 21 | 31.5 | 35 | 0.02 | 0.05 | 0.07 | 0.11 | 0.17 | 0.23 | 87 | 92 | 93.4 | 94.5 | 94.5 | 94.1 | 93.9 | 85.8 | 91.5 | 93.5 | 95.1 | 96.1 | 95.3 | 94.9 | 85.4 | 91.3 | 93.3 | 94.9 | 95.3 | 95.5 | 94.4
SolarBridge Technologies | P250HV-208/240-xxx | 240 W, 208 or 240 Vac Inverter, where xxx may be up to 20 characters | 0.24 |  | 95 | N | Y |  | 0.15 |  |  | 33.5 | 42.5 | 46 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.7 | 94.6 | 95.7 | 95 | 95 | 94.7 | 94.9 | 90 | 94.5 | 95.4 | 95.2 | 95.3 | 95.1 | 95 | 89.3 | 93.7 | 95.1 | 95 | 95.3 | 95.2 | 94.9
SolarBridge Technologies | P250HV-240-xxx [240V] | 240 W, 240 Vac Inverter, "xxx" may be up to 20 characters | 0.24 | 240 | 95 | N | Y |  | 0.21 |  |  | 33.5 | 42.5 | 46 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 89.1 | 93.6 | 94.7 | 95 | 95.1 | 94.8 | 94.7 | 88.6 | 93.5 | 94.7 | 95.3 | 95.6 | 94.8 | 95 | 88.1 | 93.3 | 94.7 | 95.3 | 95.7 | 95.7 | 95
SolarBridge Technologies | P250LV-208/240-xxx | 240 W, 208 or 240 Vac Inverter, where xxx may be up to 20 characters | 0.24 |  | 95 | N | Y |  | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6
SolarBridge Technologies | P250LV-240-xxx [240V] | 240 W, 240 Vac Inverter, "xxx" may be up to 20 characters | 0.24 | 240 | 95 | N | Y |  | 0.22 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 88.7 | 93.7 | 94 | 94.9 | 95 | 94.7 | 94.5 | 87.7 | 93.5 | 94.8 | 95.1 | 95.5 | 95.5 | 94.9 | 86.9 | 93.2 | 94.6 | 95.1 | 95.7 | 95.7 | 94.9
SolarBridge Technologies | SBT250-NA208/240-A121 | 240 W, 208 Vac or 240 Vac 1-phase ACPV | 0.24 |  | 94.5 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.02 |  |  | 21 | 31.5 | 35 | 0.02 | 0.05 | 0.07 | 0.11 | 0.17 | 0.23 | 87 | 92 | 93.4 | 94.5 | 94.5 | 94.1 | 93.9 | 85.8 | 91.5 | 93.5 | 95.1 | 96.1 | 95.3 | 94.9 | 85.4 | 91.3 | 93.3 | 94.9 | 95.3 | 95.5 | 94.4
SolarBridge Technologies | SBT250-NA208/240-A321 | 240 W, 208 Vac or 240 Vac 1-phase ACPV | 0.24 |  | 94.5 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.02 |  |  | 21 | 31.5 | 35 | 0.02 | 0.05 | 0.07 | 0.11 | 0.17 | 0.23 | 87 | 92 | 93.4 | 94.5 | 94.5 | 94.1 | 93.9 | 85.8 | 91.5 | 93.5 | 95.1 | 96.1 | 95.3 | 94.9 | 85.4 | 91.3 | 93.3 | 94.9 | 95.3 | 95.5 | 94.4
SolarCity | H6 | 6 kW Utility Interactive Solar and Storage Inverter | 6 |  | 97 | Y | N |  | 6 |  |  | 200 | 400 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 92.638 | 95.448 | 96.164 | 96.652 | 96.53 | 96.134 | 96.2821 | 93.212 | 95.944 | 96.742 | 97.264 | 97.286 | 97.094 | 96.9764 | 93.212 | 95.944 | 96.742 | 97.264 | 97.286 | 97.094 | 96.9764
SolarCity | H6L | 6 kW Utility Interactive Solar and Storage Inverter | 6 |  | 97 | Y | N |  | 6 |  |  | 200 | 400 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 92.638 | 95.448 | 96.164 | 96.652 | 96.53 | 96.134 | 96.2821 | 93.212 | 95.944 | 96.742 | 97.264 | 97.286 | 97.094 | 96.9764 | 93.548 | 96.14 | 96.932 | 97.426 | 97.436 | 97.238 | 97.1432
SolarEdge Technologies Ltd. | SE3000H-US [240V] | 3.0 kW, 240 Vac HD-Wave technology Utility Interactive Inverter | 2.962 | 240 | 99 | Y | N |  | 0 |  |  | 360 | 395 | 480 | 0.3 | 0.6 | 0.9 | 1.6 | 2.1 | 2.8 | 95.67 | 98.01 | 98.63 | 99.01 | 99.19 | 99.19 | 98.89 | 95.39 | 97.88 | 98.54 | 98.96 | 99.16 | 99.16 | 98.83 | 95.93 | 98.04 | 98.57 | 99 | 99.08 | 99.17 | 98.83 | 2017-07-01 | 2018-10-15
SolarEdge Technologies Ltd. | SE3000 [240V] | 3 kW, 240 Vac, Utility Interactive Inverter | 3.01 | 240 | 97.5 | Y | N |  | 3.39 |  |  | 100 | 388 | 480 | 0.3 | 0.6 | 0.9 | 1.51 | 2.26 | 3.01 | 95.1 | 97.1 | 97.5 | 97.8 | 97.8 | 97.7 | 97.6 | 94.8 | 96.8 | 97.4 | 97.7 | 97.7 | 97.6 | 97.5 | 93.4 | 96.4 | 97 | 97.4 | 97.5 | 97.5 | 97.2
SolarEdge Technologies Ltd. | SE3000 [208V] | 3 kW, 208 Vac, Utility Interactive Inverter | 3.02 | 208 | 97.5 | Y | N |  | 3.71 |  |  | 305 | 350 | 480 | 0.3 | 0.6 | 0.91 | 1.51 | 2.27 | 3.02 | 96 | 97.4 | 97.6 | 97.7 | 97.6 | 97.4 | 97.5 | 95.6 | 97.1 | 97.5 | 97.6 | 97.5 | 97.3 | 97.4 | 93.6 | 96.3 | 96.9 | 97.2 | 97.2 | 97.1 | 97
SolarEdge Technologies Ltd. | SE3300 [240V] | 3.3 kW, 240 Vac, Utility Interactive Inverter | 3.251 | 240 | 97.5 | Y | N |  | 5.46 |  |  | 370 | 435 | 500 | 0.33 | 0.65 | 0.98 | 1.63 | 2.44 | 3.25 | 95.3 | 97.1 | 97.5 | 97.6 | 97.6 | 97.5 | 97.5 | 94.9 | 96.8 | 97.3 | 97.5 | 97.5 | 97.3 | 97.3 | 94.2 | 96.5 | 96.9 | 97.3 | 97.4 | 97.2 | 97.1
SolarEdge Technologies Ltd. | SE3800H-US [208V] | 3.3 kW, 208 Vac HD-Wave technology Utility Interactive Inverter | 3.255 | 208 | 99 | N | N |  | 4.12 |  |  | 360 | 395 | 480 | 0.3255 | 0.651 | 0.9765 | 1.6275 | 2.4413 | 3.255 | 89.795 | 99.3907 | 99.3812 | 99.2769 | 99.0026 | 98.7791 | 98.7455 | 92.1061 | 99.3518 | 99.377 | 99.2454 | 98.986 | 98.7542 | 98.8189 | 95.5802 | 99.4287 | 99.3924 | 99.2524 | 98.9976 | 98.7297 | 98.9699 | 2018-06-01 | 2018-10-15
SolarEdge Technologies Ltd. | SE3300 [208V] | 3.3 kW, 208 Vac, Utility Interactive Inverter | 3.288 | 208 | 97 | Y | N |  | 5.55 |  |  | 320 | 410 | 500 | 0.33 | 0.66 | 0.99 | 1.64 | 2.47 | 3.29 | 95.5 | 97.2 | 97.3 | 97.4 | 97.2 | 97.4 | 97.2 | 94.8 | 96.7 | 97 | 97.2 | 97 | 96.8 | 96.9 | 93.5 | 96.3 | 96.6 | 96.9 | 96.9 | 96.8 | 96.7
SolarEdge Technologies Ltd. | SE3800H-US [240V] | 3.8 kW, 240 Vac, 1-phase, HD-Wave technology Utility Interactive Inverter | 3.747 | 240 | 99 | Y | N |  | 0 |  |  | 360 | 395 | 480 | 0.3 | 0.8 | 1.2 | 2 | 2.8 | 3.6 | 96.56 | 98.4 | 98.82 | 99.18 | 99.19 | 99.2 | 99 | 96.34 | 98.3 | 98.75 | 99.14 | 99.16 | 99.12 | 98.95 | 96.72 | 98.57 | 98.82 | 99.07 | 99.17 | 99.08 | 98.97 | 2017-07-01 | 2018-10-15
SolarEdge Technologies Ltd. | SE3800 [240V] | 3.8 kW, 240 Vac Utility Interactive Inverter | 3.79 | 240 | 98 | Y | N |  | 2.24 |  |  | 360 | 400 | 480 | 0.38 | 0.76 | 1.14 | 1.9 | 2.84 | 3.79 | 96.1 | 97.6 | 98 | 98.1 | 98.1 | 98.2 | 98 | 95.7 | 97.3 | 97.8 | 98.1 | 98 | 98.2 | 97.9 | 94.6 | 96.8 | 97.5 | 97.9 | 97.9 | 97.8 | 97.6
SolarEdge Technologies Ltd. | SE4000 [240V] | 4 kW, 240 Vac Utility Interactive Inverter | 3.97 | 240 | 97.5 | Y | N |  | 5.92 |  |  | 370 | 435 | 500 | 0.4 | 0.79 | 1.19 | 1.99 | 2.98 | 3.97 | 95.3 | 97.2 | 97.6 | 97.7 | 97.4 | 97.7 | 97.4 | 94.9 | 96.9 | 97.4 | 97.5 | 97.3 | 97.2 | 97.3 | 94.2 | 96.5 | 97.1 | 97.3 | 97.2 | 97.1 | 97.1
SolarEdge Technologies Ltd. | SE3800 [208V] | 3.8 kW, 208 Vac Utility Interactive Inverter | 3.99 | 208 | 97 | Y | N |  | 5.1 |  |  | 320 | 410 | 500 | 0.4 | 0.8 | 1.2 | 2 | 2.99 | 3.99 | 95.5 | 97.2 | 97.3 | 97.3 | 97.4 | 97.1 | 97.3 | 94.8 | 96.7 | 97.1 | 97.2 | 96.8 | 97 | 96.9 | 93.5 | 96.3 | 96.8 | 96.9 | 96.8 | 96.4 | 96.6
SolarEdge Technologies Ltd. | SE4000 [208V] | 4 kW, 208 Vac Utility Interactive Inverter | 3.99 | 208 | 97 | Y | N |  | 5.1 |  |  | 320 | 410 | 500 | 0.4 | 0.8 | 1.2 | 2 | 2.99 | 3.99 | 95.5 | 97.2 | 97.3 | 97.3 | 97.4 | 97.1 | 97.3 | 94.8 | 96.7 | 97.1 | 97.2 | 96.8 | 97 | 96.9 | 93.5 | 96.3 | 96.8 | 96.9 | 96.8 | 96.4 | 96.6
SolarEdge Technologies Ltd. | SE5000H-US [208V] | 5 kW, 208 Vac, 1-phase, HD-Wave technology Utility Interactive Inverter | 4.979 | 208 | 98.5 | Y | N |  | 4.51 |  |  | 360 | 395 | 480 | 0.4 | 1 | 1.6 | 2.7 | 3.6 | 4.9 | 96.58 | 98.34 | 98.72 | 98.82 | 98.82 | 98.91 | 98.7 | 96.34 | 98.22 | 98.64 | 98.76 | 98.77 | 98.64 | 98.62 | 95.89 | 97.99 | 98.46 | 98.68 | 98.7 | 98.57 | 98.51 | 2017-07-01 | 2018-10-15
SolarEdge Technologies Ltd. | SE5000 [208V] | 5 kW, 208 Vac Utility Interactive Inverter | 4.98 | 208 | 97 | Y | N |  | 5.46 |  |  | 320 | 410 | 500 | 0.5 | 1 | 1.49 | 2.49 | 3.73 | 4.98 | 96.6 | 97.3 | 97.4 | 97.2 | 97.1 | 96.6 | 97.1 | 95.9 | 97 | 97.2 | 97 | 97 | 96.6 | 97 | 96.2 | 96.6 | 96.9 | 96.9 | 96.4 | 96.5 | 96.5
SolarEdge Technologies Ltd. | SE5000 [240V] | 5 kW, 240 Vac Utility Interactive Inverter | 4.99 | 240 | 98 | Y | N |  | 2.24 |  |  | 370 | 400 | 480 | 0.5 | 1 | 1.5 | 2.5 | 3.74 | 4.99 | 96.7 | 97.9 | 98.1 | 98.1 | 98.3 | 98.1 | 98.1 | 96.4 | 97.7 | 98 | 98 | 98.2 | 98 | 98 | 95.7 | 97.4 | 97.7 | 97.8 | 97.8 | 97.9 | 97.7
SolarEdge Technologies Ltd. | SE5000 [277V] | 5 kW, 277 Vac Utility Interactive Inverter | 5.01 | 277 | 98 | Y | N |  | 2.24 |  |  | 405 | 425 | 480 | 0.5 | 1 | 1.5 | 2.51 | 3.76 | 5.01 | 97.1 | 98 | 98.2 | 98.3 | 98.1 | 98 | 98.1 | 97 | 98 | 98.2 | 98.2 | 98.1 | 97.9 | 98.1 | 96.5 | 97.7 | 98 | 98.1 | 98 | 97.8 | 97.9
SolarEdge Technologies Ltd. | SE5000H-US [240V] | 5 kW, 240 Vac, 1-phase, HD-Wave technology Utility Interactive Inverter | 5.052 | 240 | 99 | Y | N |  | 4.52 |  |  | 360 | 395 | 480 | 0.4 | 1 | 1.6 | 2.7 | 3.6 | 4.9 | 96.65 | 98.42 | 98.79 | 99 | 98.97 | 99.11 | 98.84 | 96.38 | 98.28 | 98.7 | 98.94 | 98.92 | 98.86 | 98.76 | 96.03 | 98.07 | 98.57 | 98.87 | 98.87 | 98.81 | 98.68 | 2017-07-01 | 2018-10-15
SolarEdge Technologies Ltd. | SE6000H-US [208V] | 5 kW, 208 Vac HD-Wave technology Utility Interactive Inverter | 5.054 | 208 | 99 | N | N |  | 4.52 |  |  | 360 | 395 | 480 | 0.5054 | 1.0108 | 1.5162 | 2.527 | 3.7905 | 5.054 | 96.6546 | 98.421 | 98.7873 | 99.0003 | 98.9676 | 99.1108 | 98.8401 | 96.3757 | 98.2834 | 98.7004 | 98.9384 | 98.9206 | 98.8604 | 98.7612 | 96.0285 | 98.0689 | 98.5658 | 98.8689 | 98.8702 | 98.8054 | 98.6764 | 2018-06-01 | 2018-10-15
SolarEdge Technologies Ltd. | SE6000 [208V] | 5.3 kW, 208 Vac, Utility Interactive Inverter | 5.33 | 208 | 97 | Y | N |  | 5.22 |  |  | 320 | 410 | 500 | 0.53 | 1.07 | 1.6 | 2.66 | 3.99 | 5.33 | 96.6 | 97.3 | 97.4 | 97.2 | 97.1 | 96.4 | 97.1 | 95.9 | 97 | 97.2 | 97 | 97 | 96.4 | 97 | 96.2 | 96.6 | 96.9 | 96.9 | 96.4 | 96.3 | 96.5
SolarEdge Technologies Ltd. | SE6000 [240V] | 6 kW, 240 Vac, Utility Interactive Inverter | 5.99 | 240 | 97.5 | Y | N |  | 3.52 |  |  | 370 | 435 | 500 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 5.99 | 96.5 | 97.6 | 97.7 | 97.5 | 97.3 | 97 | 97.4 | 96 | 97.4 | 97.5 | 97.3 | 97.3 | 97 | 97.3 | 95.7 | 97.1 | 97.3 | 97.2 | 97.3 | 96.9 | 97.2
SolarEdge Technologies Ltd. | SE6000 [277V] | 6 kW, 277 Vac, Utility Interactive Inverter | 6.04 | 277 | 98 | Y | N |  | 2.74 |  |  | 405 | 425 | 480 | 0.6 | 1.21 | 1.81 | 3.02 | 4.53 | 6.04 | 97.5 | 98.2 | 98.3 | 98.2 | 98 | 97.9 | 98.1 | 97.3 | 98.1 | 98.2 | 98.2 | 98 | 97.8 | 98 | 96.9 | 97.8 | 98.1 | 98.1 | 97.9 | 97.7 | 97.9
SolarEdge Technologies Ltd. | SE6000H-US [240V] | 6 kW, 240 Vac, 1-phase, HD-Wave technology Utility Interactive Inverter | 6.046 | 240 | 99 | Y | N |  | 4.52 |  |  | 360 | 395 | 480 | 0.5 | 1.3 | 1.9 | 3 | 4.3 | 5.8 | 97.17 | 98.61 | 98.9 | 98.95 | 98.95 | 98.98 | 98.96 | 96.95 | 98.51 | 98.82 | 98.89 | 98.9 | 98.95 | 98.79 | 96.65 | 98.32 | 98.7 | 98.83 | 98.85 | 98.71 | 98.7 | 2017-07-01 | 2018-10-15
SolarEdge Technologies Ltd. | SE7000 [277V] | 7 kW, 277 Vac Utility Interactive Inverter | 7.02 | 277 | 98 | Y | N |  | 2.24 |  |  | 100 | 425 | 480 | 0.7 | 1.4 | 2.1 | 3.51 | 5.26 | 7.02 | 97.7 | 98.2 | 98.3 | 98.2 | 97.9 | 97.6 | 98 | 97.6 | 98.2 | 98.2 | 98.1 | 97.9 | 97.6 | 98 | 97.2 | 98 | 98.1 | 98 | 97.8 | 97.5 | 97.8
SolarEdge Technologies Ltd. | SE7600A-US [208V] | 7.6 kW, 208 Vac, 1-phase Utility Interactive Inverter | 7.56 | 208 | 97.5 | Y | N |  | 5.75 |  |  | 325 | 375 | 480 | 0.756 | 1.512 | 2.268 | 3.78 | 5.67 | 7.56 | 96.3 | 97.4 | 97.6 | 97.6 | 97.5 | 97.3 | 97.5 | 96 | 97.2 | 97.5 | 97.5 | 97.4 | 97.2 | 97.3 | 95.2 | 96.8 | 97.1 | 97.2 | 97.1 | 96.8 | 97 | 2017-07-01 | 2018-10-15
SolarEdge Technologies Ltd. | SE7600A-US [277V] | 7.6 kW, 277 Vac, 1-phase Utility Interactive Inverter | 7.6 | 277 | 97.5 | Y | N |  | 6.03 |  |  | 100 | 435 | 480 | 0.76 | 1.52 | 2.28 | 3.8 | 5.7 | 7.6 | 95.8 | 97.3 | 97.6 | 97.8 | 97.8 | 97.8 | 97.7 | 95.7 | 97.3 | 97.6 | 97.8 | 97.7 | 97.7 | 97.6 | 95.6 | 97.1 | 97.4 | 97.7 | 97.7 | 97.6 | 97.6
SolarEdge Technologies Ltd. | SE7600H-US [240V] | 7.6 kW, 240 Vac, 1-phase Utility Interactive Inverter | 7.616 | 240 | 99 | Y | N |  | 4.52 |  |  | 360 | 395 | 480 | 0.7 | 1.6 | 2.4 | 3.6 | 5.5 | 7.3 | 97.72 | 98.8 | 98.97 | 98.97 | 99.04 | 98.73 | 98.94 | 97.52 | 98.7 | 98.91 | 98.93 | 99.02 | 98.69 | 98.89 | 97.24 | 98.57 | 98.83 | 98.87 | 98.75 | 98.71 | 98.71 | 2017-07-01 | 2018-10-15
SolarEdge Technologies Ltd. | SE7600 [240V] | 7.6 kW, 240 Vac, 1-phase Utility Interactive Inverter | 7.625 | 240 | 97.5 | Y | N |  | 2.16 |  |  | 360 | 400 | 480 | 0.7625 | 1.525 | 2.288 | 3.813 | 5.719 | 7.625 | 97 | 97.9 | 98 | 97.9 | 97.7 | 97.3 | 97.7 | 96.6 | 97.8 | 97.9 | 97.9 | 97.6 | 97.3 | 97.7 | 95.7 | 97.4 | 97.6 | 97.6 | 97.5 | 97.1 | 97.5
SolarEdge Technologies Ltd. | SE7600A-US [240V] | 7.6 kW, 240 Vac, 1-phase Utility Interactive Inverter | 7.625 | 240 | 97.5 | Y | N |  | 2.16 |  |  | 360 | 400 | 480 | 0.7625 | 1.525 | 2.288 | 3.813 | 5.719 | 7.625 | 97 | 97.9 | 98 | 97.9 | 97.7 | 97.3 | 97.7 | 96.6 | 97.8 | 97.9 | 97.9 | 97.6 | 97.3 | 97.7 | 95.7 | 97.4 | 97.6 | 97.6 | 97.5 | 97.1 | 97.5 | 2017-07-01 | 2018-10-15
SolarEdge Technologies Ltd. | SE9K [208V] | 9 kW, 208 Vac, 3-phase Utility Interactive Inverter | 8.963 | 208 | 96.5 | Y | N |  | 3.08 |  |  | 384 | 424 | 504 | 0.9 | 1.79 | 2.69 | 4.48 | 6.72 | 8.96 | 95.2 | 96.5 | 96.8 | 96.6 | 96.3 | 96.1 | 96.4 | 94.9 | 96.3 | 96.7 | 96.5 | 96.3 | 96 | 96.3 | 94.3 | 96 | 96.4 | 96.4 | 96.1 | 95.8 | 96.1
SolarEdge Technologies Ltd. | SE10K [480V] | 10 kW, 480 Vac, 3-phase Utility Interactive Inverter | 9.85 | 480 | 98 | Y | N |  | 3.13 |  |  | 100 | 882 | 962 | 0.98 | 1.97 | 2.95 | 4.92 | 7.38 | 9.85 | 95.5 | 97.4 | 97.8 | 98.1 | 98.1 | 98 | 97.9 | 95.1 | 97.3 | 97.7 | 98 | 98 | 97.9 | 97.8 | 94.2 | 97 | 97.5 | 97.9 | 98 | 97.9 | 97.7
SolarEdge Technologies Ltd. | SE10000A-US [208V] | 10 kW, 208 Vac, 1-phase Utility Interactive Inverter | 9.93 | 208 | 97 | Y | N |  | 5.75 |  |  | 325 | 375 | 480 | 0.993 | 1.986 | 2.979 | 4.965 | 7.448 | 9.93 | 96.8 | 97.6 | 97.7 | 97.5 | 97.4 | 97.1 | 97.4 | 96.5 | 97.4 | 97.5 | 97.4 | 97.2 | 96.9 | 97.3 | 96.2 | 97 | 97.2 | 97.1 | 96.9 | 96.7 | 96.9 | 2017-07-01 | 2018-10-15
SolarEdge Technologies Ltd. | SE10000A-US [240V] | 10 kW, 240 Vac, 1-phase Utility Interactive Inverter | 9.94 | 240 | 97.5 | Y | N |  | 5.95 |  |  | 360 | 400 | 480 | 0.99 | 1.99 | 2.98 | 4.97 | 7.46 | 9.94 | 96.8 | 97.6 | 97.8 | 97.8 | 97.7 | 97.5 | 97.7 | 96.6 | 97.5 | 97.7 | 97.6 | 97.6 | 97.4 | 97.6 | 96.4 | 97.3 | 97.5 | 97.4 | 97.4 | 97.2 | 97.3 | 2017-07-01 | 2018-10-15
SolarEdge Technologies Ltd. | SE10000A-US [277V] | 10 kW, 277 Vac, 1-phase Utility Interactive Inverter | 9.95 | 277 | 97.5 | Y | N |  | 6.03 |  |  | 415 | 435 | 480 | 0.995 | 1.99 | 2.985 | 4.975 | 7.463 | 9.95 | 96.5 | 97.5 | 97.8 | 97.8 | 97.8 | 97.7 | 97.7 | 96.4 | 97.5 | 97.8 | 97.8 | 97.7 | 97.6 | 97.7 | 96.3 | 97.4 | 97.6 | 97.7 | 97.6 | 97.5 | 97.5
SolarEdge Technologies Ltd. | SE10000H-US [240V] | 10 kW, 240 Vac, 1-phase, HD-Wave technology Utility Interactive Inverter | 9.994 | 240 | 99 | N | N |  | 6 |  |  | 360 | 395 | 480 | 0.999 | 1.999 | 2.998 | 4.997 | 7.496 | 9.994 | 97.86 | 98.83 | 98.94 | 99.23 | 98.95 | 98.63 | 98.94 | 97.69 | 98.74 | 98.88 | 99.18 | 98.91 | 98.55 | 98.89 | 97.44 | 98.54 | 98.68 | 98.7 | 98.62 | 98.1 | 98.57 | 2018-04-02 | 2018-10-15
SolarEdge Technologies Ltd. | SE10000H-US [208V] | 10 kW, 208 Vac, 1-phase, HD-Wave technology Utility Interactive Inverter | 10.001 | 208 | 98.5 | N | N |  | 5.71 |  |  | 360 | 395 | 480 | 1 | 2 | 3 | 5.001 | 7.501 | 10.001 | 97.77 | 98.73 | 98.83 | 99.07 | 98.67 | 98.17 | 98.71 | 97.65 | 98.66 | 98.77 | 98.97 | 98.58 | 98.09 | 98.62 | 97.44 | 98.54 | 98.7 | 98.7 | 98.62 | 98.1 | 98.57 | 2018-04-02 | 2018-10-15
SolarEdge Technologies Ltd. | SE11400A-US [277V] | 11.4 kW, 277 Vac, 1-phase Utility Interactive Inverter | 11.34 | 277 | 97.5 | Y | N |  | 6.03 |  |  | 415 | 435 | 480 | 1.134 | 2.268 | 3.402 | 5.67 | 8.505 | 11.34 | 96.8 | 97.6 | 97.9 | 97.8 | 97.7 | 97.6 | 97.7 | 96.7 | 97.6 | 97.8 | 97.7 | 97.7 | 97.5 | 97.7 | 96.5 | 97.4 | 97.7 | 97.7 | 97.6 | 97.5 | 97.6
SolarEdge Technologies Ltd. | SE11400A-US [240V] | 11.4 kW, 240 Vac, 1-phase Utility Interactive Inverter | 11.39 | 240 | 97.5 | Y | N |  | 5.95 |  |  | 360 | 400 | 480 | 1.139 | 2.278 | 3.417 | 5.695 | 8.543 | 11.39 | 96.9 | 97.7 | 97.8 | 97.8 | 97.6 | 97.4 | 97.7 | 96.8 | 97.6 | 97.7 | 97.6 | 97.5 | 97.3 | 97.5 | 96.5 | 97.4 | 97.5 | 97.5 | 97.3 | 97.1 | 97.3 | 2017-07-01 | 2018-10-15
SolarEdge Technologies Ltd. | SE11400H-US [240V] | 11.4 kW, 240 Vac, HD-Wave technology Utility Interactive Inverter | 11.393 | 240 | 99 | N | N |  | 6 |  |  | 360 | 395 | 480 | 1.139 | 2.279 | 3.418 | 5.697 | 8.545 | 11.393 | 97.88 | 98.84 | 98.95 | 99.16 | 98.82 | 98.41 | 98.85 | 97.91 | 98.83 | 98.93 | 99.17 | 98.83 | 98.4 | 98.85 | 97.42 | 98.63 | 98.79 | 98.82 | 98.8 | 98.39 | 98.72 | 2018-04-02 | 2018-10-15
SolarEdge Technologies Ltd. | SE14.4KUS [208V] | 14.4 kW, 208 Vac, 3-phase Utility Interactive Inverter | 14.51 | 208 | 97 | Y | N |  | 4.16 |  |  | 400 | 460 | 600 | 1.45 | 2.9 | 4.35 | 7.26 | 10.88 | 14.51 | 95.9 | 97.3 | 97.5 | 97.5 | 97 | 96.6 | 97.1 | 95.2 | 97.1 | 97.2 | 97.3 | 97.2 | 96.8 | 97.1 | 94.7 | 96.3 | 96.7 | 96.9 | 96.4 | 96.2 | 96.4 | 2017-07-01 | 2018-10-15
SolarEdge Technologies Ltd. | SE43.2KUS [208V] | 43.2 kW, 208 Vac, 3-phase Utility Interactive Inverter. (Made up of three SE14.4KUS installed together rated max output power = 43.2kW) | 14.51 | 208 | 97 | Y | N | Performance data is the same as SE14.4KUS. | 4.16 |  |  | 400 | 460 | 600 | 1.451 | 2.902 | 4.353 | 7.255 | 10.8825 | 14.51 | 95.8927 | 97.2782 | 97.4837 | 97.462 | 97.0093 | 96.6434 | 97.1118 | 95.2252 | 97.0865 | 97.1922 | 97.3046 | 97.1963 | 96.8019 | 97.1145 | 94.6669 | 96.2868 | 96.6724 | 96.8566 | 96.3889 | 96.1759 | 96.4365 | 2018-02-01 | 2018-10-15
SolarEdge Technologies Ltd. | SE20K [480V] | 20 kW, 480 Vac, 3-phase Utility Interactive Inverter | 20.05 | 480 | 98 | Y | N |  | 3.48 |  |  | 842 | 882 | 962 | 2.01 | 4.01 | 6.02 | 10.03 | 15.04 | 20.05 | 96.6 | 97.6 | 97.9 | 98 | 98 | 97.9 | 97.9 | 96.6 | 97.5 | 97.9 | 98 | 98 | 97.9 | 97.9 | 96 | 97.3 | 97.7 | 97.9 | 97.8 | 97.8 | 97.7
SolarEdge Technologies Ltd. | SE30KUS [480V] | 30 kW, 480 Vac, 3-phase Utility Interactive Inverter | 30.159 | 480 | 98.5 | N | N |  | 7.06 |  |  | 790 | 850 | 950 | 3 | 6 | 9 | 15 | 22.5 | 30 | 97.4085 | 98.3647 | 98.5506 | 98.5075 | 98.4804 | 98.3856 | 98.4411 | 97.0794 | 98.2049 | 98.429 | 98.4194 | 98.4029 | 98.314 | 98.3422 | 96.4164 | 97.9007 | 98.2089 | 98.2953 | 98.2622 | 98.2 | 98.1677 | 2018-01-02 | 2018-10-15
SolarEdge Technologies Ltd. | SE100KUS [480V] | 100 kW, 480 Vac, 3-phase Utility Interactive Inverter. (Made up of three SE33.3KUS installed together rated max output power = 100kW). | 33.3 | 480 | 98.5 | Y | N | Performance data is the same as SE33.3KUS. | 5.05 |  |  | 790 | 850 | 950 | 3.34 | 6.68 | 10.02 | 16.7 | 25.05 | 33.4 | 97.1892 | 98.2429 | 98.8889 | 98.5098 | 98.6777 | 98.4615 | 98.5757 | 96.664 | 98.0844 | 98.1132 | 98.5059 | 98.3704 | 98.1595 | 98.2749 | 96.3383 | 97.844 | 97.8428 | 98.4706 | 98.3128 | 98.1595 | 98.1794 | 2018-02-01 | 2018-10-15
SolarEdge Technologies Ltd. | SE33.3KUS [480V] | 33.3 kW, 480 Vac, 3-phase Utility Interactive Inverter | 33.3 | 480 | 98.5 | Y | N |  | 5.05 |  |  | 790 | 850 | 950 | 3.34 | 6.68 | 10.02 | 16.7 | 25.05 | 33.4 | 97.2 | 98.2 | 98.9 | 98.5 | 98.7 | 98.5 | 98.6 | 96.7 | 98.1 | 98.1 | 98.5 | 98.4 | 98.2 | 98.3 | 96.3 | 97.8 | 97.8 | 98.5 | 98.3 | 98.2 | 98.2 | 2017-07-01 | 2018-10-15
SolarEdge Technologies Ltd. | SE66.6KUS [480V] | 66.6 kW, 480 Vac, 3-phase Utility Interactive Inverter. (Made up of two SE33.3KUS installed together rated max output power = 66.6kW). | 33.3 | 480 | 98.5 | Y | N | Performance data is the same as SE33.3KUS. | 5.05 |  |  | 790 | 850 | 950 | 3.34 | 6.68 | 10.02 | 16.7 | 25.05 | 33.4 | 97.1892 | 98.2429 | 98.8889 | 98.5098 | 98.6777 | 98.4615 | 98.5757 | 96.664 | 98.0844 | 98.1132 | 98.5059 | 98.3704 | 98.1595 | 98.2749 | 96.3383 | 97.844 | 97.8428 | 98.4706 | 98.3128 | 98.1595 | 98.1794 | 2018-02-01 | 2018-10-15
Solargate | SG-4000 [240V] | 4000 W 240 Vac Utility Interactive Inverter | 4.03 | 240 | 95 | Y | N |  | 0.19 |  |  | 100 | 310 | 440 | 0.4 | 0.81 | 1.21 | 2.02 | 3.02 | 4.03 | 91.6 | 94.5 | 95.2 | 95.3 | 95 | 93.9 | 94.9 | 90.2 | 94.5 | 95.5 | 95.8 | 95.6 | 95 | 95.3 | 87.4 | 92.8 | 94 | 95 | 95.2 | 94.6 | 94.5
Solaria Corporation | Solaria PowerXT-345R-AC [240V] | 345 W Monocrystalline ACPV Module. DC Module: Solaria PowerXT-345R-PD. Microinverter IQ7PLUS-72-x-ACM-US [240V]. | 0.29 | 240 | 97 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.025 |  |  | 27 | 36 | 45 | 0.03 | 0.06 | 0.09 | 0.15 | 0.22 | 0.29 | 95 | 96.2 | 97.1 | 97.4 | 97.2 | 96.6 | 97.1 | 94.2 | 95.6 | 96.8 | 97.5 | 97.4 | 97.2 | 97.1 | 93.3 | 94.8 | 96.4 | 97.3 | 97.3 | 97.1 | 96.9 | 2018-06-01 | 2019-05-01
Solaria Corporation | Solaria PowerXT-350R-AC [240V] | 350 W Monocrystalline ACPV Module. DC Module: Solaria PowerXT-350R-PD. Microinverter IQ7PLUS-72-x-ACM-US [240V]. | 0.29 | 240 | 97 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.025 |  |  | 27 | 36 | 45 | 0.03 | 0.06 | 0.09 | 0.15 | 0.22 | 0.29 | 95 | 96.2 | 97.1 | 97.4 | 97.2 | 96.6 | 97.1 | 94.2 | 95.6 | 96.8 | 97.5 | 97.4 | 97.2 | 97.1 | 93.3 | 94.8 | 96.4 | 97.3 | 97.3 | 97.1 | 96.9 | 2018-06-01 | 2019-05-01
Solaria Corporation | Solaria PowerXT-355R-AC [240V] | 355 W Monocrystalline ACPV Module. DC Module: Solaria PowerXT-355R-PD. Microinverter IQ7PLUS-72-x-ACM-US [240V]. | 0.29 | 240 | 97 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.025 |  |  | 27 | 36 | 45 | 0.03 | 0.06 | 0.09 | 0.15 | 0.22 | 0.29 | 95 | 96.2 | 97.1 | 97.4 | 97.2 | 96.6 | 97.1 | 94.2 | 95.6 | 96.8 | 97.5 | 97.4 | 97.2 | 97.1 | 93.3 | 94.8 | 96.4 | 97.3 | 97.3 | 97.1 | 96.9 | 2018-06-01 | 2019-05-01
Solaria Corporation | Solaria PowerXT-360R-AC [240V] | 360 W Monocrystalline ACPV Module. DC Module: Solaria PowerXT-360R-PD. Microinverter IQ7PLUS-72-x-ACM-US [240V] [SI1]. | 0.29 | 240 | 97 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.025 |  |  | 27 | 36 | 45 | 0.03 | 0.06 | 0.09 | 0.15 | 0.22 | 0.29 | 95 | 96.2 | 97.1 | 97.4 | 97.2 | 96.6 | 97.1 | 94.2 | 95.6 | 96.8 | 97.5 | 97.4 | 97.2 | 97.1 | 93.3 | 94.8 | 96.4 | 97.3 | 97.3 | 97.1 | 96.9 | 2018-06-01 | 2019-05-01
Solaria Corporation | Solaria PowerXT-365R-AC [240V] | 365 W Monocrystalline ACPV Module. DC Module: Solaria PowerXT-365R-PD. Microinverter IQ7PLUS-72-x-ACM-US [240V]. | 0.29 | 240 | 97 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.025 |  |  | 27 | 36 | 45 | 0.029 | 0.058 | 0.087 | 0.145 | 0.2175 | 0.29 | 95.0036 | 96.2457 | 97.1477 | 97.4291 | 97.1641 | 96.6039 | 97.0574 | 94.162 | 95.5752 | 96.7802 | 97.4953 | 97.4428 | 97.1569 | 97.1354 | 93.3214 | 94.8059 | 96.394 | 97.2732 | 97.3095 | 97.0757 | 96.8956 | 2019-05-01
Sol-Ark | Sol-Ark-8k-48-ST [208V] | 8000 W, 208 Vac, 1-phase, Hybrid Utility Interactive PV and Battery Inverter | 7.839 | 208 | 96.5 | N | N |  | 13.4 |  |  | 240 | 370 | 425 | 0.784 | 1.568 | 2.352 | 3.92 | 5.88 | 7.84 | 91.4863 | 94.7602 | 95.3527 | 97.2963 | 97.1851 | 96.8599 | 96.6231 | 91.7 | 94.9639 | 95.4957 | 97.4288 | 97.2316 | 96.9297 | 96.715 | 91.9073 | 94.929 | 95.3698 | 97.3187 | 96.9256 | 97.0631 | 96.5278 | 2018-11-01
Sol-Ark | Sol-Ark-8k-48-ST [240V] | 8000 W, 240V, 1-phase, Hybrid Utility Interactive PV and Battery Inverter | 7.976 | 240 | 96.5 | N | N |  | 13.4 |  |  | 240 | 370 | 425 | 0.798 | 1.596 | 2.394 | 3.99 | 5.985 | 7.98 | 91.8196 | 94.911 | 95.5205 | 97.0796 | 96.988 | 97.1305 | 96.5277 | 91.6709 | 95.0008 | 95.7077 | 97.5465 | 97.4459 | 97.0835 | 96.8871 | 91.5513 | 95.0717 | 95.8584 | 97.6006 | 97.274 | 97.0868 | 96.8243 | 2018-11-01
Solarmax | SM 12MT2A | Photovoltaic Inverter | 11.7 |  | 97.5 | Y | N |  | 0.45 |  |  | 340 | 500 | 850 | 1.17 | 2.33 | 3.5 | 5.83 | 8.75 | 11.67 | 95.2 | 96.6 | 96.6 | 97 | 96.7 | 96.5 | 96.7 | 95.8 | 97.1 | 97.6 | 97.5 | 97.5 | 97.2 | 97.4 | 97.4 | 97.8 | 98.1 | 98.2 | 97.9 | 97.7 | 97.9
Solarmax | SM 15MT3A | Photovoltaic Inverter | 14.7 |  | 97 | Y | N |  | 0.46 |  |  | 325 | 400 | 500 | 1.47 | 2.94 | 4.41 | 7.35 | 11.03 | 14.71 | 94.6 | 96.1 | 96.7 | 96.7 | 96.5 | 96.1 | 96.4 | 95 | 96.6 | 96.8 | 97 | 97 | 96.7 | 96.9 | 95 | 96.7 | 96.9 | 97.3 | 97.2 | 96.9 | 97.1
Solarmax | SM 18MT3A | Photovoltaic Inverter | 17.7 |  | 97 | Y | N |  | 0.46 |  |  | 400 | 595 | 850 | 1.77 | 3.54 | 5.31 | 8.84 | 13.27 | 17.69 | 95.4 | 96.4 | 96.9 | 97.1 | 96.7 | 96.4 | 96.7 | 96.2 | 97.5 | 97.5 | 97.4 | 97.4 | 97 | 97.4 | 96.5 | 97.6 | 97.7 | 97.7 | 97.5 | 97.4 | 97.5
Solarmax | 75TS-A | Photovoltaic Inverter | 75.13 |  | 95 | Y | N |  | 11.24 |  |  | 325 | 450 | 600 | 7.51 | 15.03 | 22.54 | 37.57 | 56.35 | 75.13 | 93.9 | 95.8 | 95.9 | 95.6 | 95 | 94.3 | 95.2 | 93.5 | 95.7 | 95.7 | 95.5 | 94.8 | 93.8 | 95 | 92.2 | 94.2 | 94.8 | 94.8 | 94.3 | 93.6 | 94.3
SolaX Power Network Technology (Zhe jiang) Co., Ltd. | A1-Hybrid-7.6-US [240V] | 7.6 kW, 240 Vac, 1-phase, transformerless, bidirectional, hybrid PV and Battery Grid Support Utility Interactive Inverter with PV arc detector | 7.642 | 240 | 95.5 | N | N |  | 44 |  |  | 304 | 402 | 500 | 0.76415 | 1.5283 | 2.2925 | 3.8208 | 5.7311 | 7.6415 | 91.7074 | 94.5729 | 95.3432 | 95.7328 | 95.6501 | 95.3856 | 95.4058 | 90.5573 | 94.4837 | 95.2373 | 95.7522 | 95.7552 | 95.573 | 95.4118 | 93.4546 | 95.5643 | 96.1659 | 96.4887 | 96.3651 | 96.1449 | 96.1997 | 2019-06-03
SolaX Power Network Technology (Zhe jiang) Co., Ltd. | A1-Fit-7.6-US [240V] | 7.6 kW, 240 Vac, 1-phase, transformerless, bidirectional, battery Grid Support Utility Interactive Inverter | 7.832 | 240 | 95.5 | N | N |  | 49.5 |  |  | 320 | 375 | 430 | 0.78321 | 1.5664 | 2.3496 | 3.916 | 5.874 | 7.8321 | 91.4312 | 94.9622 | 95.6242 | 95.751 | 95.4401 | 94.9759 | 95.32 | 92.2952 | 94.8694 | 95.6095 | 95.9358 | 95.7414 | 95.332 | 95.5645 | 92.7618 | 95.0616 | 95.7149 | 95.9028 | 95.7632 | 95.4369 | 95.6153 | 2019-06-03
SolaX Power Network Technology (Zhe jiang) Co., Ltd. | A1-Hybrid-8.6-US [240V] | 8.6 kW, 240 Vac, 1-phase, transformerless, bidirectional, hybrid PV and Battery Grid Support Utility Interactive Inverter with PV arc detector | 8.604 | 240 | 96 | N | N |  | 40 |  |  | 258 | 379 | 500 | 0.86044 | 1.7209 | 2.5813 | 4.3022 | 6.4533 | 8.6044 | 92.6993 | 94.5399 | 95.2978 | 95.6136 | 95.4241 | 94.9404 | 95.2714 | 92.8441 | 95.2894 | 95.9701 | 96.1825 | 95.8716 | 95.5293 | 95.7814 | 93.6941 | 95.7768 | 96.2745 | 96.5194 | 96.2968 | 95.8922 | 96.1906 | 2019-06-03
SolaX Power Network Technology (Zhe jiang) Co., Ltd. | A1-Fit-8.6-US [240V] | 8.6 kW, 240 Vac, 1-phase, transformerless, bidirectional, battery Grid Support Utility Interactive Inverter | 8.613 | 240 | 95.5 | N | N |  | 42 |  |  | 363 | 396.5 | 430 | 0.8613 | 1.7226 | 2.5839 | 4.3065 | 6.4597 | 8.613 | 93.0135 | 95.2805 | 95.8088 | 95.9296 | 95.6312 | 95.1894 | 95.5709 | 92.8584 | 95.2474 | 95.8068 | 95.9989 | 95.7474 | 95.3227 | 95.6455 | 92.5757 | 95.1198 | 95.7234 | 95.9883 | 95.8346 | 95.4524 | 95.6683 | 2019-06-03
Sonnetek | Sonnetek 2000 [120V] | 2000 W, 120 Vac Utility Interactive Inverter | 2 | 120 | 91.5 | Y | N |  | 14.18 |  |  | 100 | 240 | 360 | 0.2 | 0.4 | 0.6 | 1 | 1.5 | 2 | 89 | 92.2 | 92.8 | 92.6 | 91.7 | 90.8 | 91.9 | 88.6 | 91.9 | 92.8 | 92.6 | 91.6 | 90.5 | 91.8 | 87.1 | 90.8 | 91.8 | 92.2 | 91.3 | 90.1 | 91.3
Sonnetek | Sonnetek 4000 [240V] | 4000 W, 240 Vac Utility Interactive Inverter | 4.03 | 240 | 95 | Y | N |  | 0.19 |  |  | 100 | 310 | 440 | 0.4 | 0.81 | 1.21 | 2.02 | 3.02 | 4.03 | 91.6 | 94.5 | 95.2 | 95.3 | 95 | 93.9 | 94.9 | 90.2 | 94.5 | 95.5 | 95.8 | 95.6 | 95 | 95.3 | 87.4 | 92.8 | 94 | 95 | 95.2 | 94.6 | 94.5
Sparq Systems | S215NA2240 [240V] | 207 W, 240 Vac Microinverter | 0.21 | 240 | 93 | N | Y |  | 0.03 |  |  | 22 | 27 | 40 | 0.02 | 0.04 | 0.06 | 0.1 | 0.16 | 0.21 | 84 | 91.2 | 92.8 | 94.3 | 94.7 | 94 | 93.7 | 83.8 | 91 | 91.5 | 93.9 | 94.1 | 93.8 | 93.2 | 81.5 | 89.3 | 92.1 | 93.3 | 93.6 | 93.4 | 92.6
Sparq Systems | Q1000-4101 [240V] | 960 W, 240 Vac Microinverter | 0.96 | 240 | 96 | N | Y |  | 0.1 |  |  | 28 | 29 | 31 | 0.1 | 0.19 | 0.29 | 0.48 | 0.72 | 0.96 | 91.5 | 95 | 95.5 | 96.1 | 96.6 | 96.7 | 96.1 | 91.4 | 94.9 | 95.4 | 95.8 | 96.4 | 96.5 | 95.9 | 91.3 | 94.9 | 95.1 | 95.8 | 96.3 | 96.4 | 95.8
Sparq Systems | Q1200-4101 [240V] | 1200 W, 240 Vac, 60Hz Utility Interactive Inverter | 1.165 | 240 | 96.5 | N | Y |  | 0.04 |  |  | 28 | 29 | 31 | 0.12 | 0.24 | 0.36 | 0.6 | 0.9 | 1.2 | 91.2693 | 95.4412 | 96.5736 | 97.1364 | 97.0548 | 96.7999 | 96.6893 | 90.983 | 95.514 | 96.5823 | 97.0419 | 96.9805 | 96.7573 | 96.6212 | 89.75 | 95.2351 | 96.4213 | 97.0117 | 96.9939 | 96.8163 | 96.5424 | 2018-08-01 | 2018-10-15
Sparq Systems | Q1200-4102 [240V] | 1200 W, 240 Vac, 60 Hz Utility Interactive Inverter | 1.203 | 240 | 96.5 | N | Y |  |  |  |  | 36 | 37 | 38 | 0.12032 | 0.24064 | 0.36096 | 0.6016 | 0.9024 | 1.2032 | 88.21 | 94.58 | 96.05 | 97.188 | 97.44 | 97.345 | 96.7033 | 87.2763 | 94.772 | 96.19 | 97.21 | 97.36 | 97.235 | 96.6491 | 87.1383 | 95.037 | 96.348 | 97.161 | 97.327 | 97.225 | 96.6475 | 2019-02-01
Sputnik Engineering | SM 12MT2A | Photovoltaic Inverter | 11.7 |  | 97.5 | Y | N |  | 0.45 |  |  | 340 | 500 | 850 | 1.17 | 2.33 | 3.5 | 5.83 | 8.75 | 11.67 | 95.2 | 96.6 | 96.6 | 97 | 96.7 | 96.5 | 96.7 | 95.8 | 97.1 | 97.6 | 97.5 | 97.5 | 97.2 | 97.4 | 97.4 | 97.8 | 98.1 | 98.2 | 97.9 | 97.7 | 97.9
Sputnik Engineering | SM 15MT3A | Photovoltaic Inverter | 14.7 |  | 97 | Y | N |  | 0.46 |  |  | 325 | 400 | 500 | 1.47 | 2.94 | 4.41 | 7.35 | 11.03 | 14.71 | 94.6 | 96.1 | 96.7 | 96.7 | 96.5 | 96.1 | 96.4 | 95 | 96.6 | 96.8 | 97 | 97 | 96.7 | 96.9 | 95 | 96.7 | 96.9 | 97.3 | 97.2 | 96.9 | 97.1
Sputnik Engineering | SM 18MT3A | Photovoltaic Inverter | 17.7 |  | 97 | Y | N |  | 0.46 |  |  | 400 | 595 | 850 | 1.77 | 3.54 | 5.31 | 8.84 | 13.27 | 17.69 | 95.4 | 96.4 | 96.9 | 97.1 | 96.7 | 96.4 | 96.7 | 96.2 | 97.5 | 97.5 | 97.4 | 97.4 | 97 | 97.4 | 96.5 | 97.6 | 97.7 | 97.7 | 97.5 | 97.4 | 97.5
Sputnik Engineering | 75TS | Photovoltaic Inverter | 75.13 |  | 95 | N | N |  | 11.24 |  |  | 325 | 450 | 600 | 7.51 | 15.03 | 22.54 | 37.57 | 56.35 | 75.13 | 93.9 | 95.8 | 95.9 | 95.6 | 95 | 94.3 | 95.2 | 93.5 | 95.7 | 95.7 | 95.5 | 94.8 | 93.8 | 95 | 92.2 | 94.2 | 94.8 | 94.8 | 94.3 | 93.6 | 94.3
Sungrow Power Supply Co., Ltd. | SG30KU | 30 kW, 3-phase, Utility Interactive Inverter | 30 |  | 98 | Y | N |  | 1.52 |  |  | 480 | 705 | 800 | 3 | 6 | 9 | 15 | 22.5 | 30 | 95.5 | 97 | 97.5 | 97.5 | 97.3 | 96.8 | 97.3 | 97.3 | 98.2 | 98.5 | 98.5 | 98.3 | 98.1 | 98.3 | 96.3 | 97.9 | 98.2 | 98.3 | 98.2 | 98 | 98.1 |  | 2019-02-01
Sungrow Power Supply Co., Ltd. | SG36KU | 36 kW, 3-phase Utility Interactive Inverter | 36 |  | 98 | Y | N |  | 1.51 |  |  | 580 | 700 | 800 | 3.6 | 7.2 | 10.8 | 18 | 27 | 36 | 96.6 | 97.7 | 97.8 | 97.8 | 97.5 | 97 | 97.5 | 97.6 | 98.2 | 98.5 | 98.4 | 98.2 | 97.9 | 98.2 | 97.1 | 98.1 | 98.3 | 98.3 | 98.1 | 97.8 | 98.1 |  | 2019-02-01
Sungrow Power Supply Co., Ltd. | SG60KU | 60 kW, transformerless Utility Interactive Inverter | 60 |  | 98.5 | Y | N |  | 0.84 |  |  | 550 | 700 | 850 | 6 | 12 | 18 | 30 | 45 | 60 | 97.8 | 98.5 | 98.6 | 98.5 | 98.4 | 98.5 | 98.5 | 97.8 | 98.6 | 98.8 | 99 | 98.8 | 98.6 | 98.8 | 97.2 | 98.3 | 98.6 | 98.7 | 98.4 | 98.3 | 98.4 |  | 2019-02-01
Sungrow Power Supply Co., Ltd. | SG60KU-M | 60 kW, transformerless Utility Interactive Inverter | 60 |  | 98.5 | Y | N |  | 0.88 |  |  | 550 | 700 | 850 | 6 | 12 | 18 | 30 | 45 | 60 | 97.8 | 98.2 | 98.2 | 98.4 | 98.4 | 98 | 98.3 | 97.8 | 98.6 | 98.8 | 98.9 | 98.7 | 98.5 | 98.7 | 97.5 | 98.6 | 98.5 | 98.8 | 98.5 | 98.4 | 98.5 |  | 2019-02-01
Sungrow Power Supply Co., Ltd. | SG100KU-outdoor [480V] | 100 kW, 480 Vac Utility Interactive Inverter | 100 | 480 | 96.5 | Y | N |  | 159.8 |  |  | 300 | 350 | 480 | 10 | 20 | 30 | 50 | 75 | 100 | 94.9 | 96.5 | 96.8 | 96.8 | 96.6 | 96 | 96.6 | 93.8 | 96.3 | 96.5 | 96.7 | 96.3 | 95.6 | 96.3 | 94.5 | 96.2 | 96.6 | 96.5 | 96 | 95.2 | 96.1 |  | 2019-02-01
Sungrow Power Supply Co., Ltd. | SG100KU [480V] | 100 kW, 480 Vac Utility Interactive Inverter | 101 | 480 | 96.5 | Y | N |  | 41.78 |  |  | 300 | 380 | 480 | 10.1 | 20.2 | 30.3 | 50.5 | 75.75 | 101 | 94.75 | 96.01 | 96.27 | 97.32 | 96.84 | 96.01 | 96.71 | 94.29 | 95.59 | 96.07 | 96.96 | 96.59 | 95.88 | 96.43 | 93.54 | 95.36 | 95.54 | 96.82 | 96.31 | 95.64 | 96.13 |  | 2019-02-01
Sungrow Power Supply Co., Ltd. | SG125HV [600V] | 125 kW, 600 Vac transformerless Grid Support Utility Interactive Inverter. | 125 | 600 | 98.5 | N | N |  | 5.59 |  |  | 860 | 945 | 1200 | 12.5 | 25 | 37.5 | 62.5 | 93.75 | 125 | 98.5862 | 98.8265 | 98.8829 | 98.6821 | 98.4462 | 98.2555 | 98.5632 | 98.2896 | 98.5839 | 98.589 | 98.4937 | 98.3596 | 98.1057 | 98.411 | 98.0848 | 98.4261 | 98.4778 | 98.3839 | 98.0971 | 97.6269 | 98.1955 | 2017-11-01 | 2019-06-03
Sungrow Power Supply Co., Ltd. | SG250KC [600V] | 250 kW, 600 Vac Utility Interactive Inverter (Canada) | 250 | 600 | 96.5 | Y | N |  | 71 | 250 | 71 | 320 | 360 | 480 | 25 | 50 | 75 | 125 | 187.5 | 250 | 95.8 | 97.4 | 97.1 | 97.2 | 96.8 | 96.2 | 96.9 | 95.3 | 96.9 | 97.1 | 97.1 | 96.7 | 96.1 | 96.7 | 94.5 | 95.9 | 96.7 | 96.6 | 96.4 | 95.9 | 96.4 |  | 2019-02-01
Sungrow Power Supply Co., Ltd. | SG250KU [480V] | 250 kW, 480 Vac Utility Interactive Inverter (United States) | 250 | 480 | 96.5 | Y | N |  | 50 | 250 | 50 | 320 | 360 | 480 | 25 | 50 | 75 | 125 | 187.5 | 250 | 95 | 96.6 | 97.1 | 97.1 | 96.5 | 96 | 96.6 | 95.3 | 96.8 | 97.4 | 96.9 | 96.3 | 95.8 | 96.5 | 93.7 | 95.8 | 96.6 | 96.5 | 96.3 | 95.8 | 96.3 |  | 2019-02-01
Sungrow Power Supply Co., Ltd. | SG500LV | 500 kW Utility Interactive Inverter to connect with medium voltage transformer | 500 |  | 96.5 | Y | N |  | 90 |  |  | 320 | 360 | 480 | 50 | 100 | 150 | 250 | 375 | 500 | 94.5 | 96.6 | 97 | 97 | 96.7 | 95.4 | 96.6 | 94.2 | 96.5 | 97 | 97 | 96.5 | 95.5 | 96.5 | 93.6 | 96.3 | 96.9 | 96.2 | 95.9 | 95.4 | 96 |  | 2019-02-01
Sungrow Power Supply Co., Ltd. | SG750MX | 750 kW, 3-phase, Utility Interactive Inverter with medium voltage NEMA NEMA TP1 transformer | 750 |  | 97 | Y | N |  | 87 |  |  | 500 | 580 | 800 | 75 | 150 | 225 | 375 | 562.5 | 750 | 95 | 97 | 97.5 | 97.5 | 97.2 | 96.6 | 97.2 | 94.4 | 96.9 | 97.5 | 97.5 | 97.2 | 96.5 | 97.1 | 93 | 96.1 | 96.9 | 97.1 | 96.7 | 96.1 | 96.6 |  | 2019-02-01
Sungrow Power Supply Co., Ltd. | SG800MX | 800 kW, 3-phase, Utility Interactive Inverter with medium voltage NEMA NEMA TP1 transformer | 800 |  | 97 | Y | N |  | 97 |  |  | 545 | 615 | 800 | 80 | 160 | 240 | 400 | 600 | 800 | 94 | 96.7 | 97.4 | 97.6 | 97.3 | 96.7 | 97.2 | 93.7 | 96.3 | 97.1 | 97.5 | 97.2 | 96.5 | 97.1 | 93.5 | 96.1 | 96.9 | 97.2 | 97 | 96.2 | 96.8 |  | 2019-02-01
Sungrow Power Supply Co., Ltd. | SG1000MX | 1000 kW, 3-phase, Utility Interactive Inverter with medium voltage NEMA NEMA TP1 transformer | 1000 |  | 97.5 | Y | N |  | 17 |  |  | 570 | 630 | 800 | 100 | 200 | 300 | 500 | 750 | 1000 | 94.3 | 96.9 | 97.5 | 97.8 | 97.5 | 96.9 | 97.4 | 93.9 | 96.6 | 97.4 | 97.8 | 97.5 | 96.8 | 97.3 | 93.6 | 96.3 | 97.2 | 97.5 | 97.4 | 96.4 | 97.2 |  | 2019-02-01
Sungrow Power Supply Co., Ltd. | SG2500U [550V] | 2500kW, 550Vac Utility Interactive Inverter connect to grid via a 2500kVA medium voltage transformer. | 2500 | 550 | 98 | N | N | Weighted Efficiency includes efficiency of ABB ZGSB-H-2500/35. | 651.36 |  |  | 800 | 900 | 1200 | 250 | 500 | 750 | 1250 | 1875 | 2500 | 98 | 98.6 | 98.8 | 98.8 | 98.6 | 98.4 | 97.9 | 97.8 | 98.5 | 98.6 | 98.6 | 98.5 | 98.3 | 97.7 | 97.4 | 98.2 | 98.4 | 98.5 | 98.3 | 98.2 | 97.7 | 2018-02-01 | 2018-10-15
Sunna Tech | SUNNA 2000TL-US-240 [240V] | 2110 W, 240 Vac Utility Interactive Inverter | 2.11 | 240 | 94.5 | Y | N |  | 0.25 |  |  | 100 | 375 | 400 | 0.21 | 0.42 | 0.63 | 1.06 | 1.58 | 2.11 | 85.3 | 91.6 | 92.9 | 94.3 | 94.6 | 94.5 | 93.8 | 82.1 | 91.9 | 94.2 | 95.6 | 96.1 | 96.4 | 95 | 82.2 | 91.5 | 93.8 | 95.6 | 96.1 | 96.3 | 95
Sunna Tech | SUNNA 3000TL-US-240 [240V] | 3180 W, 240 Vac Utility Interactive Inverter | 3.18 | 240 | 95 | Y | N |  | 0.25 |  |  | 100 | 375 | 400 | 0.32 | 0.64 | 0.95 | 1.59 | 2.39 | 3.18 | 88.8 | 92.9 | 94.1 | 94.6 | 94.3 | 94 | 94 | 88.8 | 94.4 | 95.3 | 96.2 | 96.3 | 95.9 | 95.7 | 89.5 | 93.7 | 95.3 | 96.2 | 96.3 | 96.1 | 95.7
Sunna Tech | SUNNA 4200TL-US-240 [240V] | 4100 W, 240 Vac Utility Interactive Inverter | 4.16 | 240 | 95.5 | Y | N |  | 0.2 |  |  | 100 | 380 | 400 | 0.42 | 0.83 | 1.25 | 2.08 | 3.12 | 4.16 | 90.6 | 93.8 | 94.5 | 94.8 | 94.6 | 94.2 | 94.4 | 91.4 | 95 | 95.7 | 96.1 | 96.2 | 95.9 | 95.9 | 90.7 | 94.7 | 95.5 | 96.1 | 96.1 | 95.9 | 95.7
Sunna Tech | SUNNA 5000TL-US-240 [240V] | 5000 W, 240 Vac Utility Interactive Inverter | 5.24 | 240 | 95.5 | Y | N |  | 0.2 |  |  | 100 | 380 | 400 | 0.52 | 1.05 | 1.57 | 2.62 | 3.93 | 5.24 | 91.8 | 94.1 | 94.6 | 94.7 | 94.3 | 93.5 | 94.3 | 92.5 | 95.1 | 96.1 | 96.2 | 95.9 | 95.6 | 95.8 | 92.3 | 95.3 | 95.8 | 96.1 | 95.9 | 95.5 | 95.8
SunPower | SPR-225E-BLK-U-ACPV [240V] | 225 W, 240 Vac Inverter | 0.225 | 240 | 94.5 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.03 | 0.225 | 0.03 | 30 | 43 | 50 | 0.02 | 0.05 | 0.07 | 0.11 | 0.2 | 0.2 | 86.6 | 91.6 | 93.3 | 94.6 | 94.7 | 94.5 | 94 | 85.9 | 91.3 | 93.2 | 94.9 | 95.3 | 95.3 | 94.4 | 87.3 | 90.7 | 93.3 | 95 | 95.5 | 95.4 | 94.5
SunPower | SPR-230NE-BLK-U-ACPV [240V] | 225 W, 240 Vac Inverter | 0.225 | 240 | 94.5 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.03 | 0.225 | 0.03 | 30 | 43 | 50 | 0.02 | 0.05 | 0.07 | 0.11 | 0.2 | 0.2 | 86.6 | 91.6 | 93.3 | 94.6 | 94.7 | 94.5 | 94 | 85.9 | 91.3 | 93.2 | 94.9 | 95.3 | 95.3 | 94.4 | 87.3 | 90.7 | 93.3 | 95 | 95.5 | 95.4 | 94.5
SunPower | SPR-240E-WHT-U-ACPV [240V] | 225 W, 240 Vac Inverter | 0.225 | 240 | 94.5 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.03 | 0.225 | 0.03 | 30 | 43 | 50 | 0.02 | 0.05 | 0.07 | 0.11 | 0.17 | 0.23 | 86.6 | 91.6 | 93.3 | 94.6 | 94.7 | 94.5 | 94 | 85.9 | 91.3 | 93.2 | 94.9 | 95.3 | 95.3 | 94.4 | 87.3 | 90.7 | 93.3 | 95 | 95.5 | 95.4 | 94.5
SunPower | SPR-245NE-WHT-U-240 ACPV [240V] | 225 W, 240 Vac Inverter | 0.225 | 240 | 94.5 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.03 | 0.225 | 0.03 | 30 | 43 | 50 | 0.02 | 0.05 | 0.07 | 0.11 | 0.2 | 0.2 | 86.6 | 91.6 | 93.3 | 94.6 | 94.7 | 94.5 | 94 | 85.9 | 91.3 | 93.2 | 94.9 | 95.3 | 95.3 | 94.4 | 87.3 | 90.7 | 93.3 | 95 | 95.5 | 95.4 | 94.5
SunPower | SPR-245NE-WHT-U-ACPV [240V] | 225 W, 240 Vac Inverter | 0.225 | 240 | 94.5 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.03 | 0.225 | 0.03 | 30 | 43 | 50 | 0.02 | 0.05 | 0.07 | 0.11 | 0.2 | 0.2 | 86.6 | 91.6 | 93.3 | 94.6 | 94.7 | 94.5 | 94 | 85.9 | 91.3 | 93.2 | 94.9 | 95.3 | 95.3 | 94.4 | 87.3 | 90.7 | 93.3 | 95 | 95.5 | 95.4 | 94.5
SunPower | SPR-E20-245-A-AC [240V] | 225 W, 240 Vac Inverter | 0.225 | 240 | 94.5 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.03 | 0.225 | 0.03 | 30 | 43 | 50 | 0.02 | 0.05 | 0.07 | 0.11 | 0.17 | 0.23 | 86.6 | 91.6 | 93.3 | 94.6 | 94.7 | 94.5 | 94 | 85.9 | 91.3 | 93.2 | 94.9 | 95.3 | 95.3 | 94.4 | 87.3 | 90.7 | 93.3 | 95 | 95.5 | 95.4 | 94.5
SunPower | SPR-X20-250-BLK-A-AC [240V] | 225 W, 240 Vac Inverter | 0.225 | 240 | 94.5 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.03 | 0.225 | 0.03 | 30 | 43 | 50 | 0.02 | 0.05 | 0.07 | 0.11 | 0.17 | 0.23 | 86.6 | 91.6 | 93.3 | 94.6 | 94.7 | 94.5 | 94 | 85.9 | 91.3 | 93.2 | 94.9 | 95.3 | 95.3 | 94.4 | 87.3 | 90.7 | 93.3 | 95 | 95.5 | 95.4 | 94.5
SunPower | SPR-E20-245-B-AC [208V] | 240 W, 208 Vac Inverter | 0.24 | 208 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 33.5 | 42.5 | 46 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.7 | 94.6 | 95.7 | 95 | 95 | 94.7 | 94.9 | 90 | 94.5 | 95.4 | 95.2 | 95.3 | 95.1 | 95 | 89.3 | 93.7 | 95.1 | 95 | 95.3 | 95.2 | 94.9
SunPower | SPR-E20-245-B-AC [240V] | 240 W, 240 Vac Inverter | 0.24 | 240 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 33.5 | 42.5 | 46 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.7 | 94.6 | 95.7 | 95 | 95 | 94.7 | 94.9 | 90 | 94.5 | 95.4 | 95.2 | 95.3 | 95.1 | 95 | 89.3 | 93.7 | 95.1 | 95 | 95.3 | 95.2 | 94.9
SunPower | SPR-X19-240-BLK-B-AC [208V] | 240 W, 208 Vac Inverter | 0.24 | 208 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 33.5 | 42.5 | 46 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.7 | 94.6 | 95.7 | 95 | 95 | 94.7 | 94.9 | 90 | 94.5 | 95.4 | 95.2 | 95.3 | 95.1 | 95 | 89.3 | 93.7 | 95.1 | 95 | 95.3 | 95.2 | 94.9
SunPower | SPR-X19-240-BLK-B-AC [240V] | 240 W, 240 Vac Inverter | 0.24 | 240 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 33.5 | 42.5 | 46 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.7 | 94.6 | 95.7 | 95 | 95 | 94.7 | 94.9 | 90 | 94.5 | 95.4 | 95.2 | 95.3 | 95.1 | 95 | 89.3 | 93.7 | 95.1 | 95 | 95.3 | 95.2 | 94.9
SunPower | SPR-X20-250-BLK-B-AC [208V] | 240 W, 208 Vac Inverter | 0.24 | 208 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 33.5 | 42.5 | 46 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.7 | 94.6 | 95.7 | 95 | 95 | 94.7 | 94.9 | 90 | 94.5 | 95.4 | 95.2 | 95.3 | 95.1 | 95 | 89.3 | 93.7 | 95.1 | 95 | 95.3 | 95.2 | 94.9
SunPower | SPR-X20-250-BLK-B-AC [240V] | 240 W, 240 Vac Inverter | 0.24 | 240 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 33.5 | 42.5 | 46 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.7 | 94.6 | 95.7 | 95 | 95 | 94.7 | 94.9 | 90 | 94.5 | 95.4 | 95.2 | 95.3 | 95.1 | 95 | 89.3 | 93.7 | 95.1 | 95 | 95.3 | 95.2 | 94.9 |  | 2018-03-15
SunPower | SPR-E19-320-E-AC [208V] | 320 W, 208 Vac, Utility Interactive, monocrystalline ACPV Module, white backsheet. DC Module: SPR-E19-320. Micro-inverter: IQ7XS-96-y-ACM-z [208V]. | 0.315 | 208 | 97 | N | Y | This component is specific to ACPV modules and is not available as an individual unit | 0.021 |  |  | 53 | 60 | 64 | 0.0315 | 0.063 | 0.0945 | 0.1575 | 0.23625 | 0.315 | 90.4836 | 96.6628 | 97.0999 | 97.6357 | 97.5242 | 97.1035 | 97.151 | 95.4142 | 96.4654 | 96.9008 | 97.542 | 97.4613 | 97.05 | 97.2587 | 95.2705 | 96.3335 | 96.8135 | 97.5025 | 97.4299 | 97.0197 | 97.2095 | 2019-01-02
SunPower | SPR-E19-320-E-AC [240V] | 320 W, 240 Vac, Utility Interactive, monocrystalline ACPV Module, white backsheet. DC Module: SPR-E19-320. Micro-inverter: IQ7XS-96-y-ACM-z [240V]. | 0.315 | 240 | 97.5 | N | Y | This component is specific to ACPV modules and is not available as an individual unit | 0.021 |  |  | 53 | 60 | 64 | 0.0315 | 0.063 | 0.0945 | 0.1575 | 0.23625 | 0.315 | 95.7348 | 96.8402 | 96.9962 | 97.7627 | 97.7558 | 97.4686 | 97.5251 | 95.6103 | 96.6782 | 96.7549 | 97.6667 | 97.7392 | 97.5137 | 97.4564 | 95.4365 | 96.4979 | 96.6571 | 97.6038 | 97.7001 | 97.4825 | 97.3932 | 2019-01-02
SunPower | SPR-E20-327-E-AC [208V] | 327 W, 208 Vac, Utility Interactive, monocrystalline ACPV Module, white backsheet. DC Module: SPR-E20-327. Micro-inverter: IQ7XS-96-y-ACM-z [208V]. | 0.315 | 208 | 97 | N | Y | This component is specific to ACPV modules and is not available as an individual unit | 0.021 |  |  | 53 | 60 | 64 | 0.0315 | 0.063 | 0.0945 | 0.1575 | 0.23625 | 0.315 | 90.4836 | 96.6628 | 97.0999 | 97.6357 | 97.5242 | 97.1035 | 97.151 | 95.4142 | 96.4654 | 96.9008 | 97.542 | 97.4613 | 97.05 | 97.2587 | 95.2705 | 96.3335 | 96.8135 | 97.5025 | 97.4299 | 97.0197 | 97.2095 | 2019-01-02
SunPower | SPR-E20-327-E-AC [240V] | 327 W, 240 Vac, Utility Interactive, monocrystalline ACPV Module, white backsheet. DC Module: SPR-E20-327. Micro-inverter: IQ7XS-96-y-ACM-z [240V]. | 0.315 | 240 | 97.5 | N | Y | This component is specific to ACPV modules and is not available as an individual unit | 0.021 |  |  | 53 | 60 | 64 | 0.0315 | 0.063 | 0.0945 | 0.1575 | 0.23625 | 0.315 | 95.7348 | 96.8402 | 96.9962 | 97.7627 | 97.7558 | 97.4686 | 97.5251 | 95.6103 | 96.6782 | 96.7549 | 97.6667 | 97.7392 | 97.5137 | 97.4564 | 95.4365 | 96.4979 | 96.6571 | 97.6038 | 97.7001 | 97.4825 | 97.3932 | 2019-01-02
SunPower | SPR-X20-327-BLK-E-AC [208V] | 327 W, 208 Vac, Utility Interactive, monocrystalline ACPV module, black backsheet. DC Module: SPR-X20-327-BLK. Micro-inverter: IQ7XS-96-y-ACM-z [208V]. | 0.315 | 208 | 97 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.021 |  |  | 53 | 60 | 64 | 0.0315 | 0.063 | 0.0945 | 0.1575 | 0.23625 | 0.315 | 90.4836 | 96.6628 | 97.0999 | 97.6357 | 97.5242 | 97.1035 | 97.151 | 95.4142 | 96.4654 | 96.9008 | 97.542 | 97.4613 | 97.05 | 97.2587 | 95.2705 | 96.3335 | 96.8135 | 97.5025 | 97.4299 | 97.0197 | 97.2095 | 2018-11-15
SunPower | SPR-X20-327-BLK-E-AC [240V] | 327 W, 240 Vac, Utility Interactive, monocrystalline ACPV module, black backsheet. DC Module: SPR-X20-327-BLK. Micro-inverter: IQ7XS-96-y-ACM-z [240V]. | 0.315 | 240 | 97.5 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.021 |  |  | 53 | 60 | 64 | 0.0315 | 0.063 | 0.0945 | 0.1575 | 0.23625 | 0.315 | 95.7348 | 96.8402 | 96.9962 | 97.7627 | 97.7558 | 97.4686 | 97.5251 | 95.6103 | 96.6782 | 96.7549 | 97.6667 | 97.7392 | 97.5137 | 97.4564 | 95.4365 | 96.4979 | 96.6571 | 97.6038 | 97.7001 | 97.4825 | 97.3932 | 2018-11-15
SunPower | SPR-X20-327-E-AC [208V] | 327 W, 208 Vac, Utility Interactive, monocrystalline ACPV module, white backsheet. DC Module: SPR-X20-327. Micro-inverter: IQ7XS-96-y-ACM-z [208V]. | 0.315 | 208 | 97 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.021 |  |  | 53 | 60 | 64 | 0.0315 | 0.063 | 0.0945 | 0.1575 | 0.23625 | 0.315 | 90.4836 | 96.6628 | 97.0999 | 97.6357 | 97.5242 | 97.1035 | 97.151 | 95.4142 | 96.4654 | 96.9008 | 97.542 | 97.4613 | 97.05 | 97.2587 | 95.2705 | 96.3335 | 96.8135 | 97.5025 | 97.4299 | 97.0197 | 97.2095 | 2018-11-15
SunPower | SPR-X20-327-E-AC [240V] | 327 W, 240 Vac, Utility Interactive, monocrystalline ACPV module, white backsheet. DC Module: SPR-X20-327. Micro-inverter: IQ7XS-96-y-ACM-z [240V]. | 0.315 | 240 | 97.5 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.021 |  |  | 53 | 60 | 64 | 0.0315 | 0.063 | 0.0945 | 0.1575 | 0.23625 | 0.315 | 95.7348 | 96.8402 | 96.9962 | 97.7627 | 97.7558 | 97.4686 | 97.5251 | 95.6103 | 96.6782 | 96.7549 | 97.6667 | 97.7392 | 97.5137 | 97.4564 | 95.4365 | 96.4979 | 96.6571 | 97.6038 | 97.7001 | 97.4825 | 97.3932 | 2018-11-15
SunPower | SPR-X21-335-BLK-E-AC [208V] | 335 W, 208 Vac, Utility Interactive, monocrystalline ACPV module, black backsheet. DC Module: SPR-X21-335-BLK. Micro-inverter: IQ7XS-96-y-ACM-z [208V]. | 0.315 | 208 | 97 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.021 |  |  | 53 | 60 | 64 | 0.0315 | 0.063 | 0.0945 | 0.1575 | 0.23625 | 0.315 | 90.4836 | 96.6628 | 97.0999 | 97.6357 | 97.5242 | 97.1035 | 97.151 | 95.4142 | 96.4654 | 96.9008 | 97.542 | 97.4613 | 97.05 | 97.2587 | 95.2705 | 96.3335 | 96.8135 | 97.5025 | 97.4299 | 97.0197 | 97.2095 | 2018-11-15
SunPower | SPR-X21-335-BLK-E-AC [240V] | 335 W, 240 Vac, Utility Interactive, monocrystalline ACPV module, black backsheet. DC Module: SPR-X21-335-BLK. Micro-inverter: IQ7XS-96-y-ACM-z [240V]. | 0.315 | 240 | 97.5 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.021 |  |  | 53 | 60 | 64 | 0.0315 | 0.063 | 0.0945 | 0.1575 | 0.23625 | 0.315 | 95.7348 | 96.8402 | 96.9962 | 97.7627 | 97.7558 | 97.4686 | 97.5251 | 95.6103 | 96.6782 | 96.7549 | 97.6667 | 97.7392 | 97.5137 | 97.4564 | 95.4365 | 96.4979 | 96.6571 | 97.6038 | 97.7001 | 97.4825 | 97.3932 | 2018-11-15
SunPower | SPR-X21-335-E-AC [208V] | 335 W, 208 Vac, Utility Interactive, monocrystalline ACPV module, white backsheet. DC Module: SPR-X21-335. Micro-inverter: IQ7XS-96-y-ACM-z [208V]. | 0.315 | 208 | 97 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.021 |  |  | 53 | 60 | 64 | 0.0315 | 0.063 | 0.0945 | 0.1575 | 0.23625 | 0.315 | 90.4836 | 96.6628 | 97.0999 | 97.6357 | 97.5242 | 97.1035 | 97.151 | 95.4142 | 96.4654 | 96.9008 | 97.542 | 97.4613 | 97.05 | 97.2587 | 95.2705 | 96.3335 | 96.8135 | 97.5025 | 97.4299 | 97.0197 | 97.2095 | 2018-11-15
SunPower | SPR-X21-335-E-AC [240V] | 335 W, 240 Vac, Utility Interactive, monocrystalline ACPV module, white backsheet. DC Module: SPR-X21-335. Micro-inverter: IQ7XS-96-y-ACM-z [240V]. | 0.315 | 240 | 97.5 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.021 |  |  | 53 | 60 | 64 | 0.0315 | 0.063 | 0.0945 | 0.1575 | 0.23625 | 0.315 | 95.7348 | 96.8402 | 96.9962 | 97.7627 | 97.7558 | 97.4686 | 97.5251 | 95.6103 | 96.6782 | 96.7549 | 97.6667 | 97.7392 | 97.5137 | 97.4564 | 95.4365 | 96.4979 | 96.6571 | 97.6038 | 97.7001 | 97.4825 | 97.3932 | 2018-11-15
SunPower | SPR-X21-345-E-AC [208V] | 345 W, 208 Vac, Utility Interactive, monocrystalline ACPV module, white backsheet. DC Module: SPR-X21-345. Micro-inverter: IQ7XS-96-y-ACM-z [208V]. | 0.315 | 208 | 97 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.021 |  |  | 53 | 60 | 64 | 0.0315 | 0.063 | 0.0945 | 0.1575 | 0.23625 | 0.315 | 90.4836 | 96.6628 | 97.0999 | 97.6357 | 97.5242 | 97.1035 | 97.151 | 95.4142 | 96.4654 | 96.9008 | 97.542 | 97.4613 | 97.05 | 97.2587 | 95.2705 | 96.3335 | 96.8135 | 97.5025 | 97.4299 | 97.0197 | 97.2095 | 2018-11-15
SunPower | SPR-X21-345-E-AC [240V] | 345 W, 240 Vac, Utility Interactive, monocrystalline ACPV module, white backsheet. DC Module: SPR-X21-345. Micro-inverter: IQ7XS-96-y-ACM-z [240V]. | 0.315 | 240 | 97.5 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.021 |  |  | 53 | 60 | 64 | 0.0315 | 0.063 | 0.0945 | 0.1575 | 0.23625 | 0.315 | 95.7348 | 96.8402 | 96.9962 | 97.7627 | 97.7558 | 97.4686 | 97.5251 | 95.6103 | 96.6782 | 96.7549 | 97.6667 | 97.7392 | 97.5137 | 97.4564 | 95.4365 | 96.4979 | 96.6571 | 97.6038 | 97.7001 | 97.4825 | 97.3932 | 2018-11-15
SunPower | SPR-X21-350-BLK-E-AC [208V] | 350 W, 208 Vac, Utility Interactive, monocrystalline ACPV module, black backsheet. DC Module: SPR-X21-350-BLK. Micro-inverter: IQ7XS-96-y-ACM-z [208V]. | 0.315 | 208 | 97 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.021 |  |  | 53 | 60 | 64 | 0.0315 | 0.063 | 0.0945 | 0.1575 | 0.23625 | 0.315 | 90.4836 | 96.6628 | 97.0999 | 97.6357 | 97.5242 | 97.1035 | 97.151 | 95.4142 | 96.4654 | 96.9008 | 97.542 | 97.4613 | 97.05 | 97.2587 | 95.2705 | 96.3335 | 96.8135 | 97.5025 | 97.4299 | 97.0197 | 97.2095 | 2018-11-15
SunPower | SPR-X21-350-BLK-E-AC [240V] | 350 W, 240 Vac, Utility Interactive, monocrystalline ACPV module, black backsheet. DC Module: SPR-X21-350-BLK. Micro-inverter: IQ7XS-96-y-ACM-z [240V]. | 0.315 | 240 | 97.5 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.021 |  |  | 53 | 60 | 64 | 0.0315 | 0.063 | 0.0945 | 0.1575 | 0.23625 | 0.315 | 95.7348 | 96.8402 | 96.9962 | 97.7627 | 97.7558 | 97.4686 | 97.5251 | 95.6103 | 96.6782 | 96.7549 | 97.6667 | 97.7392 | 97.5137 | 97.4564 | 95.4365 | 96.4979 | 96.6571 | 97.6038 | 97.7001 | 97.4825 | 97.3932 | 2018-11-15
SunPower | SPR-X22-360-E-AC [208V] | 360 W, 208 Vac, Utility Interactive, monocrystalline ACPV module, white backsheet. DC Module: SPR-X22-360. Micro-inverter: IQ7XS-96-y-ACM-z [208V]. | 0.315 | 208 | 97 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.021 |  |  | 53 | 60 | 64 | 0.0315 | 0.063 | 0.0945 | 0.1575 | 0.23625 | 0.315 | 90.4836 | 96.6628 | 97.0999 | 97.6357 | 97.5242 | 97.1035 | 97.151 | 95.4142 | 96.4654 | 96.9008 | 97.542 | 97.4613 | 97.05 | 97.2587 | 95.2705 | 96.3335 | 96.8135 | 97.5025 | 97.4299 | 97.0197 | 97.2095 | 2018-11-15
SunPower | SPR-X22-360-E-AC [240V] | 360 W, 240 Vac, Utility Interactive, monocrystalline ACPV module, white backsheet. DC Module: SPR-X22-360. Micro-inverter: IQ7XS-96-y-ACM-z [240V]. | 0.315 | 240 | 97.5 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.021 |  |  | 53 | 60 | 64 | 0.0315 | 0.063 | 0.0945 | 0.1575 | 0.23625 | 0.315 | 95.7348 | 96.8402 | 96.9962 | 97.7627 | 97.7558 | 97.4686 | 97.5251 | 95.6103 | 96.6782 | 96.7549 | 97.6667 | 97.7392 | 97.5137 | 97.4564 | 95.4365 | 96.4979 | 96.6571 | 97.6038 | 97.7001 | 97.4825 | 97.3932 | 2018-11-15
SunPower | SPR-X22-370-E-AC [208V] | 370 W, 208 Vac, Utility Interactive, monocrystalline ACPV module, white backsheet. DC Module: SPR-X22-370. Micro-inverter: IQ7XS-96-y-ACM-z [208V]. | 0.315 | 208 | 97 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.021 |  |  | 53 | 60 | 64 | 0.0315 | 0.063 | 0.0945 | 0.1575 | 0.23625 | 0.315 | 90.4836 | 96.6628 | 97.0999 | 97.6357 | 97.5242 | 97.1035 | 97.151 | 95.4142 | 96.4654 | 96.9008 | 97.542 | 97.4613 | 97.05 | 97.2587 | 95.2705 | 96.3335 | 96.8135 | 97.5025 | 97.4299 | 97.0197 | 97.2095 | 2018-11-15
SunPower | SPR-X22-370-E-AC [240V] | 370 W, 240 Vac, Utility Interactive, monocrystalline ACPV module, white backsheet. DC Module: SPR-X22-370. Micro-inverter: IQ7XS-96-y-ACM-z [240V]. | 0.315 | 240 | 97.5 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.021 |  |  | 53 | 60 | 64 | 0.0315 | 0.063 | 0.0945 | 0.1575 | 0.23625 | 0.315 | 95.7348 | 96.8402 | 96.9962 | 97.7627 | 97.7558 | 97.4686 | 97.5251 | 95.6103 | 96.6782 | 96.7549 | 97.6667 | 97.7392 | 97.5137 | 97.4564 | 95.4365 | 96.4979 | 96.6571 | 97.6038 | 97.7001 | 97.4825 | 97.3932 | 2018-11-15
SunPower | MI-C-320-US208/240-1X [208V] | 320 W, 208 Vac Utility Interactive Microinverter | 0.32 | 208 | 95.5 | Y | Y | This component is specific to ACPV modules and is not available as an individual unit. Previously listed as MI-C-320-US208-1X | 0.02 |  |  | 53 | 60 | 64 | 0.03 | 0.06 | 0.1 | 0.16 | 0.24 | 0.32 | 90.8 | 94.5 | 95.5 | 96.2 | 96.1 | 95.9 | 95.7 | 90.2 | 94.5 | 95.5 | 96.2 | 96.1 | 95.9 | 95.7 | 89.4 | 94.1 | 95.3 | 96.2 | 96.2 | 95.9 | 95.7 | 2017-07-01 | 2018-10-15
SunPower | MI-C-320-US208/240-1X [240V] | 320 W, 240 Vac Utility Interactive Microinverter | 0.32 | 240 | 96 | Y | Y | This component is specific to ACPV modules and is not available as an individual unit. Previously listed as MI-C-320-US240-1X | 0.1 |  |  | 53 | 60 | 64 | 0.03 | 0.06 | 0.1 | 0.16 | 0.24 | 0.32 | 89.7 | 94.1 | 95.3 | 96.2 | 96.1 | 95.9 | 95.7 | 90 | 94.3 | 95.4 | 96.3 | 96.3 | 96.2 | 95.8 | 89.6 | 94 | 95.2 | 96.3 | 96.4 | 96.2 | 95.8 | 2017-07-01 | 2018-10-15
SunPower | MI-C-320-US208-xx [208V] | 320 W, 208 Vac Utility Interactive Microinverter | 0.32 | 208 | 96 | N | Y |  | 0.04 |  |  | 53 | 60 | 64 | 0.03 | 0.06 | 0.1 | 0.16 | 0.24 | 0.32 | 92.7 | 95.6 | 96.3 | 96.2 | 96 | 95.4 | 95.9 | 91.4 | 95.1 | 95.9 | 96.1 | 95.9 | 95.5 | 95.7 | 90.6 | 94.8 | 95.7 | 96.1 | 96 | 95.7 | 95.7
SunPower | MI-C-320-US240-xx [240V] | 320 W, 240 Vac Utility Interactive Microinverter | 0.32 | 240 | 96 | N | Y |  | 0.07 |  |  | 53 | 60 | 64 | 0.03 | 0.06 | 0.1 | 0.16 | 0.24 | 0.32 | 92.9 | 95.8 | 96.5 | 96.4 | 96.3 | 95.8 | 96.1 | 92.9 | 95.7 | 96.5 | 96.5 | 96.4 | 96 | 96.2 | 91.7 | 95.4 | 96.2 | 96.5 | 96.5 | 96.2 | 96.2
SunPower | SPR-E19-320-C-AC [208V] | 320 W, 208 Vac Inverter | 0.32 | 208 | 96 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.07 |  |  | 53 | 60 | 64 | 0.03 | 0.06 | 0.1 | 0.16 | 0.24 | 0.32 | 92.9 | 95.8 | 96.5 | 96.4 | 96.3 | 95.8 | 96.1 | 92.9 | 95.7 | 96.5 | 96.5 | 96.4 | 96 | 96.2 | 91.7 | 95.4 | 96.2 | 96.5 | 96.5 | 96.2 | 96.2
SunPower | SPR-E19-320-C-AC [240V] | 320 W, 240 Vac Inverter | 0.32 | 240 | 96 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.07 |  |  | 53 | 60 | 64 | 0.03 | 0.06 | 0.1 | 0.16 | 0.24 | 0.32 | 92.9 | 95.8 | 96.5 | 96.4 | 96.3 | 95.8 | 96.1 | 92.9 | 95.7 | 96.5 | 96.5 | 96.4 | 96 | 96.2 | 91.7 | 95.4 | 96.2 | 96.5 | 96.5 | 96.2 | 96.2
SunPower | SPR-E19-320-D-AC [208V] | 320 W, 208 Vac, Utility Interactive, monocrystalline ACPV Module, white backsheet. DC Module: SPR-E19-320. Micro-inverter: MI-C-320-US208/240-1X [208V]. | 0.32 | 208 | 95.5 | Y | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.02 |  |  | 53 | 60 | 64 | 0.03 | 0.06 | 0.1 | 0.16 | 0.24 | 0.32 | 90.8 | 94.5 | 95.5 | 96.2 | 96.1 | 95.9 | 95.7 | 90.2 | 94.5 | 95.5 | 96.2 | 96.1 | 95.9 | 95.7 | 89.4 | 94.1 | 95.3 | 96.2 | 96.2 | 95.9 | 95.7 | 2017-09-01 | 2019-02-15
SunPower | SPR-E19-320-D-AC [240V] | 320 W, 240 Vac, Utility Interactive, monocrystalline ACPV Module, white backsheet. DC Module: SPR-E19-320. Micro-inverter: MI-C-320-US208/240-1X [240V]. | 0.32 | 240 | 96 | Y | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.1 |  |  | 53 | 60 | 64 | 0.03 | 0.06 | 0.1 | 0.16 | 0.24 | 0.32 | 89.7 | 94.1 | 95.3 | 96.2 | 96.1 | 95.9 | 95.7 | 90 | 94.3 | 95.4 | 96.3 | 96.3 | 96.2 | 95.8 | 89.6 | 94 | 95.2 | 96.3 | 96.4 | 96.2 | 95.8 | 2017-09-01 | 2019-02-15
SunPower | SPR-E20-327-C-AC [208V] | 320 W, 208 Vac Inverter | 0.32 | 208 | 96 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.07 |  |  | 53 | 60 | 64 | 0.03 | 0.06 | 0.1 | 0.16 | 0.24 | 0.32 | 92.9 | 95.8 | 96.5 | 96.4 | 96.3 | 95.8 | 96.1 | 92.9 | 95.7 | 96.5 | 96.5 | 96.4 | 96 | 96.2 | 91.7 | 95.4 | 96.2 | 96.5 | 96.5 | 96.2 | 96.2
SunPower | SPR-E20-327-C-AC [240V] | 320 W, 240 Vac Inverter | 0.32 | 240 | 96 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.07 |  |  | 53 | 60 | 64 | 0.03 | 0.06 | 0.1 | 0.16 | 0.24 | 0.32 | 92.9 | 95.8 | 96.5 | 96.4 | 96.3 | 95.8 | 96.1 | 92.9 | 95.7 | 96.5 | 96.5 | 96.4 | 96 | 96.2 | 91.7 | 95.4 | 96.2 | 96.5 | 96.5 | 96.2 | 96.2
SunPower | SPR-E20-327-D-AC [208V] | 327 W, 208 Vac, Utility Interactive, monocrystalline ACPV Module, white backsheet. DC Module: SPR-E20-327. Micro-inverter: MI-C-320-US208/240-1X [208V]. | 0.32 | 208 | 95.5 | Y | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.02 |  |  | 53 | 60 | 64 | 0.03 | 0.06 | 0.1 | 0.16 | 0.24 | 0.32 | 90.8 | 94.5 | 95.5 | 96.2 | 96.1 | 95.9 | 95.7 | 90.2 | 94.5 | 95.5 | 96.2 | 96.1 | 95.9 | 95.7 | 89.4 | 94.1 | 95.3 | 96.2 | 96.2 | 95.9 | 95.7 | 2017-09-01 | 2019-02-15
SunPower | SPR-E20-327-D-AC [240V] | 327 W, 240 Vac, Utility Interactive, monocrystalline ACPV Module, white backsheet. DC Module: SPR-E20-327. Micro-inverter: MI-C-320-US208/240-1X [240V]. | 0.32 | 240 | 96 | Y | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.1 |  |  | 53 | 60 | 64 | 0.03 | 0.06 | 0.1 | 0.16 | 0.24 | 0.32 | 89.7 | 94.1 | 95.3 | 96.2 | 96.1 | 95.9 | 95.7 | 90 | 94.3 | 95.4 | 96.3 | 96.3 | 96.2 | 95.8 | 89.6 | 94 | 95.2 | 96.3 | 96.4 | 96.2 | 95.8 | 2017-09-01 | 2019-02-15
SunPower | SPR-X20-327-BLK-C-AC [208V] | 320 W, 208 Vac Inverter | 0.32 | 208 | 96 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.07 |  |  | 53 | 60 | 64 | 0.03 | 0.06 | 0.1 | 0.16 | 0.24 | 0.32 | 92.9 | 95.8 | 96.5 | 96.4 | 96.3 | 95.8 | 96.1 | 92.9 | 95.7 | 96.5 | 96.5 | 96.4 | 96 | 96.2 | 91.7 | 95.4 | 96.2 | 96.5 | 96.5 | 96.2 | 96.2
SunPower | SPR-X20-327-BLK-C-AC [240V] | 320 W, 240 Vac Inverter | 0.32 | 240 | 96 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.07 |  |  | 53 | 60 | 64 | 0.03 | 0.06 | 0.1 | 0.16 | 0.24 | 0.32 | 92.9 | 95.8 | 96.5 | 96.4 | 96.3 | 95.8 | 96.1 | 92.9 | 95.7 | 96.5 | 96.5 | 96.4 | 96 | 96.2 | 91.7 | 95.4 | 96.2 | 96.5 | 96.5 | 96.2 | 96.2
SunPower | SPR-X20-327-BLK-D-AC [208V] | 327 W, 208 Vac, Utility Interactive, monocrystalline ACPV Module, black backsheet. DC Module: SPR-X20-327-BLK. Micro-inverter: MI-C-320-US208/240-1X [208V]. | 0.32 | 208 | 95.5 | Y | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.02 |  |  | 53 | 60 | 64 | 0.03 | 0.06 | 0.1 | 0.16 | 0.24 | 0.32 | 90.8 | 94.5 | 95.5 | 96.2 | 96.1 | 95.9 | 95.7 | 90.2 | 94.5 | 95.5 | 96.2 | 96.1 | 95.9 | 95.7 | 89.4 | 94.1 | 95.3 | 96.2 | 96.2 | 95.9 | 95.7 | 2017-09-01 | 2019-02-15
SunPower | SPR-X20-327-BLK-D-AC [240V] | 327 W, 240 Vac, Utility Interactive, monocrystalline ACPV Module, black backsheet. DC Module: SPR-X20-327-BLK. Micro-inverter: MI-C-320-US208/240-1X [240V]. | 0.32 | 240 | 96 | Y | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.1 |  |  | 53 | 60 | 64 | 0.03 | 0.06 | 0.1 | 0.16 | 0.24 | 0.32 | 89.7 | 94.1 | 95.3 | 96.2 | 96.1 | 95.9 | 95.7 | 90 | 94.3 | 95.4 | 96.3 | 96.3 | 96.2 | 95.8 | 89.6 | 94 | 95.2 | 96.3 | 96.4 | 96.2 | 95.8 | 2017-09-01 | 2019-02-15
SunPower | SPR-X20-327-C-AC [208V] | 320 W, 208 Vac Inverter | 0.32 | 208 | 96 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.07 |  |  | 53 | 60 | 64 | 0.03 | 0.06 | 0.1 | 0.16 | 0.24 | 0.32 | 92.9 | 95.8 | 96.5 | 96.4 | 96.3 | 95.8 | 96.1 | 92.9 | 95.7 | 96.5 | 96.5 | 96.4 | 96 | 96.2 | 91.7 | 95.4 | 96.2 | 96.5 | 96.5 | 96.2 | 96.2
SunPower | SPR-X20-327-C-AC [240V] | 320 W, 240 Vac Inverter | 0.32 | 240 | 96 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.07 |  |  | 53 | 60 | 64 | 0.03 | 0.06 | 0.1 | 0.16 | 0.24 | 0.32 | 92.9 | 95.8 | 96.5 | 96.4 | 96.3 | 95.8 | 96.1 | 92.9 | 95.7 | 96.5 | 96.5 | 96.4 | 96 | 96.2 | 91.7 | 95.4 | 96.2 | 96.5 | 96.5 | 96.2 | 96.2
SunPower | SPR-X20-327-D-AC [208V] | 320 W, 208 Vac Utility Interactive Microinverter for ACPV Module | 0.32 | 208 | 95.5 | Y | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.02 |  |  | 53 | 60 | 64 | 0.03 | 0.06 | 0.1 | 0.16 | 0.24 | 0.32 | 90.8 | 94.5 | 95.5 | 96.2 | 96.1 | 95.9 | 95.7 | 90.2 | 94.5 | 95.5 | 96.2 | 96.1 | 95.9 | 95.7 | 89.4 | 94.1 | 95.3 | 96.2 | 96.2 | 95.9 | 95.7 | 2017-09-01 | 2018-10-15
SunPower | SPR-X20-327-D-AC [240V] | 320 W, 240 Vac Utility Interactive Microinverter for ACPV Module | 0.32 | 240 | 96 | Y | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.1 |  |  | 53 | 60 | 64 | 0.03 | 0.06 | 0.1 | 0.16 | 0.24 | 0.32 | 89.7 | 94.1 | 95.3 | 96.2 | 96.1 | 95.9 | 95.7 | 90 | 94.3 | 95.4 | 96.3 | 96.3 | 96.2 | 95.8 | 89.6 | 94 | 95.2 | 96.3 | 96.4 | 96.2 | 95.8 | 2017-09-01 | 2018-10-15
SunPower | SPR-X21-335-BLK-C-AC [208V] | 320 W, 208 Vac Inverter | 0.32 | 208 | 96 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.07 |  |  | 53 | 60 | 64 | 0.03 | 0.06 | 0.1 | 0.16 | 0.24 | 0.32 | 92.9 | 95.8 | 96.5 | 96.4 | 96.3 | 95.8 | 96.1 | 92.9 | 95.7 | 96.5 | 96.5 | 96.4 | 96 | 96.2 | 91.7 | 95.4 | 96.2 | 96.5 | 96.5 | 96.2 | 96.2
SunPower | SPR-X21-335-BLK-C-AC [240V] | 320 W, 240 Vac Inverter | 0.32 | 240 | 96 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.07 |  |  | 53 | 60 | 64 | 0.03 | 0.06 | 0.1 | 0.16 | 0.24 | 0.32 | 92.9 | 95.8 | 96.5 | 96.4 | 96.3 | 95.8 | 96.1 | 92.9 | 95.7 | 96.5 | 96.5 | 96.4 | 96 | 96.2 | 91.7 | 95.4 | 96.2 | 96.5 | 96.5 | 96.2 | 96.2
SunPower | SPR-X21-335-BLK-D-AC [208V] | 335 W, 208 Vac, Utility Interactive, monocrystalline ACPV Module, black backsheet. DC Module: SPR-X21-335-BLK. Micro-inverter: MI-C-320-US208/240-1X [208V]. | 0.32 | 208 | 95.5 | Y | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.02 |  |  | 53 | 60 | 64 | 0.03 | 0.06 | 0.1 | 0.16 | 0.24 | 0.32 | 90.8 | 94.5 | 95.5 | 96.2 | 96.1 | 95.9 | 95.7 | 90.2 | 94.5 | 95.5 | 96.2 | 96.1 | 95.9 | 95.7 | 89.4 | 94.1 | 95.3 | 96.2 | 96.2 | 95.9 | 95.7 | 2017-09-01 | 2019-02-15
SunPower | SPR-X21-335-BLK-D-AC [240V] | 335 W, 240 Vac, Utility Interactive, monocrystalline ACPV Module, black backsheet. DC Module: SPR-X21-335-BLK. Micro-inverter: MI-C-320-US208/240-1X [240V]. | 0.32 | 240 | 96 | Y | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.1 |  |  | 53 | 60 | 64 | 0.03 | 0.06 | 0.1 | 0.16 | 0.24 | 0.32 | 89.7 | 94.1 | 95.3 | 96.2 | 96.1 | 95.9 | 95.7 | 90 | 94.3 | 95.4 | 96.3 | 96.3 | 96.2 | 95.8 | 89.6 | 94 | 95.2 | 96.3 | 96.4 | 96.2 | 95.8 | 2017-09-01 | 2019-02-15
SunPower | SPR-X21-335-C-AC [208V] | 320 W, 208 Vac Inverter | 0.32 | 208 | 96 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.07 |  |  | 53 | 60 | 64 | 0.03 | 0.06 | 0.1 | 0.16 | 0.24 | 0.32 | 92.9 | 95.8 | 96.5 | 96.4 | 96.3 | 95.8 | 96.1 | 92.9 | 95.7 | 96.5 | 96.5 | 96.4 | 96 | 96.2 | 91.7 | 95.4 | 96.2 | 96.5 | 96.5 | 96.2 | 96.2
SunPower | SPR-X21-335-C-AC [240V] | 320 W, 240 Vac Inverter | 0.32 | 240 | 96 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.07 |  |  | 53 | 60 | 64 | 0.03 | 0.06 | 0.1 | 0.16 | 0.24 | 0.32 | 92.9 | 95.8 | 96.5 | 96.4 | 96.3 | 95.8 | 96.1 | 92.9 | 95.7 | 96.5 | 96.5 | 96.4 | 96 | 96.2 | 91.7 | 95.4 | 96.2 | 96.5 | 96.5 | 96.2 | 96.2
SunPower | SPR-X21-335-D-AC [208V] | 335 W, 208 Vac, Utility Interactive, monocrystalline ACPV Module, white backsheet. DC Module: SPR-X21-335. Micro-inverter: MI-C-320-US208/240-1X [208V]. | 0.32 | 208 | 95.5 | Y | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.02 |  |  | 53 | 60 | 64 | 0.03 | 0.06 | 0.1 | 0.16 | 0.24 | 0.32 | 90.8 | 94.5 | 95.5 | 96.2 | 96.1 | 95.9 | 95.7 | 90.2 | 94.5 | 95.5 | 96.2 | 96.1 | 95.9 | 95.7 | 89.4 | 94.1 | 95.3 | 96.2 | 96.2 | 95.9 | 95.7 | 2017-09-01 | 2019-02-15
SunPower | SPR-X21-335-D-AC [240V] | 335 W, 240 Vac, Utility Interactive, monocrystalline ACPV Module, white backsheet. DC Module: SPR-X21-335. Micro-inverter: MI-C-320-US208/240-1X [240V]. | 0.32 | 240 | 96 | Y | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.1 |  |  | 53 | 60 | 64 | 0.03 | 0.06 | 0.1 | 0.16 | 0.24 | 0.32 | 89.7 | 94.1 | 95.3 | 96.2 | 96.1 | 95.9 | 95.7 | 90 | 94.3 | 95.4 | 96.3 | 96.3 | 96.2 | 95.8 | 89.6 | 94 | 95.2 | 96.3 | 96.4 | 96.2 | 95.8 | 2017-09-01 | 2019-02-15
SunPower | SPR-X21-345-C-AC [208V] | 320 W, 208 Vac Inverter | 0.32 | 208 | 96 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.07 |  |  | 53 | 60 | 64 | 0.03 | 0.06 | 0.1 | 0.16 | 0.24 | 0.32 | 92.9 | 95.8 | 96.5 | 96.4 | 96.3 | 95.8 | 96.1 | 92.9 | 95.7 | 96.5 | 96.5 | 96.4 | 96 | 96.2 | 91.7 | 95.4 | 96.2 | 96.5 | 96.5 | 96.2 | 96.2
SunPower | SPR-X21-345-C-AC [240V] | 320 W, 240 Vac Inverter | 0.32 | 240 | 96 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.07 |  |  | 53 | 60 | 64 | 0.03 | 0.06 | 0.1 | 0.16 | 0.24 | 0.32 | 92.9 | 95.8 | 96.5 | 96.4 | 96.3 | 95.8 | 96.1 | 92.9 | 95.7 | 96.5 | 96.5 | 96.4 | 96 | 96.2 | 91.7 | 95.4 | 96.2 | 96.5 | 96.5 | 96.2 | 96.2
SunPower | SPR-X21-345-D-AC [208V] | 345 W, 208 Vac, Utility Interactive, monocrystalline ACPV Module, white backsheet. DC Module: SPR-X21-345. Micro-inverter: MI-C-320-US208/240-1X [208V]. | 0.32 | 208 | 95.5 | Y | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.02 |  |  | 53 | 60 | 64 | 0.03 | 0.06 | 0.1 | 0.16 | 0.24 | 0.32 | 90.8 | 94.5 | 95.5 | 96.2 | 96.1 | 95.9 | 95.7 | 90.2 | 94.5 | 95.5 | 96.2 | 96.1 | 95.9 | 95.7 | 89.4 | 94.1 | 95.3 | 96.2 | 96.2 | 95.9 | 95.7 | 2017-09-01 | 2019-02-15
SunPower | SPR-X21-345-D-AC [240V] | 345 W, 240 Vac, Utility Interactive, monocrystalline ACPV Module, white backsheet. DC Module: SPR-X21-345. Micro-inverter: MI-C-320-US208/240-1X [240V]. | 0.32 | 240 | 96 | Y | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.1 |  |  | 53 | 60 | 64 | 0.03 | 0.06 | 0.1 | 0.16 | 0.24 | 0.32 | 89.7 | 94.1 | 95.3 | 96.2 | 96.1 | 95.9 | 95.7 | 90 | 94.3 | 95.4 | 96.3 | 96.3 | 96.2 | 95.8 | 89.6 | 94 | 95.2 | 96.3 | 96.4 | 96.2 | 95.8 | 2017-09-01 | 2019-02-15
SunPower | SPR-X21-350-BLK-D-AC [208V] | 350 W, 208 Vac, Utility Interactive, monocrystalline ACPV Module, black backsheet. DC Module: SPR-X21-350-BLK. Micro-inverter: MI-C-320-US208/240-1X [208V]. | 0.32 | 208 | 95.5 | Y | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.02 |  |  | 53 | 60 | 64 | 0.03 | 0.06 | 0.1 | 0.16 | 0.24 | 0.32 | 90.8 | 94.5 | 95.5 | 96.2 | 96.1 | 95.9 | 95.7 | 90.2 | 94.5 | 95.5 | 96.2 | 96.1 | 95.9 | 95.7 | 89.4 | 94.1 | 95.3 | 96.2 | 96.2 | 95.9 | 95.7 | 2018-01-16 | 2019-02-15
SunPower | SPR-X21-350-BLK-D-AC [240V] | 350 W, 240 Vac, Utility Interactive, monocrystalline ACPV Module, black backsheet. DC Module: SPR-X21-350-BLK. Micro-inverter: MI-C-320-US208/240-1X [240V]. | 0.32 | 240 | 96 | Y | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.1 |  |  | 53 | 60 | 64 | 0.03 | 0.06 | 0.1 | 0.16 | 0.24 | 0.32 | 89.7 | 94.1 | 95.3 | 96.2 | 96.1 | 95.9 | 95.7 | 90 | 94.3 | 95.4 | 96.3 | 96.3 | 96.2 | 95.8 | 89.6 | 94 | 95.2 | 96.3 | 96.4 | 96.2 | 95.8 | 2018-01-16 | 2019-02-15
SunPower | SPR-X22-360-C-AC [208V] | 320 W, 208 Vac Inverter | 0.32 | 208 | 96 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.04 |  |  | 53 | 60 | 64 | 0.03 | 0.06 | 0.1 | 0.16 | 0.24 | 0.32 | 92.7 | 95.6 | 96.3 | 96.2 | 96 | 95.4 | 95.9 | 91.4 | 95.1 | 95.9 | 96.1 | 95.9 | 95.5 | 95.7 | 90.6 | 94.8 | 95.7 | 96.1 | 96 | 95.7 | 95.7
SunPower | SPR-X22-360-C-AC [240V] | 320 W, 240 Vac Inverter | 0.32 | 240 | 96 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.04 |  |  | 53 | 60 | 64 | 0.03 | 0.06 | 0.1 | 0.16 | 0.24 | 0.32 | 92.7 | 95.6 | 96.3 | 96.2 | 96 | 95.4 | 95.9 | 91.4 | 95.1 | 95.9 | 96.1 | 95.9 | 95.5 | 95.7 | 90.6 | 94.8 | 95.7 | 96.1 | 96 | 95.7 | 95.7
SunPower | SPR-X22-360-D-AC [208V] | 360 W, 208 Vac, Utility Interactive, monocrystalline ACPV Module, white backsheet. DC Module: SPR-X22-360. Micro-inverter: MI-C-320-US208/240-1X [208V]. | 0.32 | 208 | 95.5 | Y | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.02 |  |  | 53 | 60 | 64 | 0.03 | 0.06 | 0.1 | 0.16 | 0.24 | 0.32 | 90.8 | 94.5 | 95.5 | 96.2 | 96.1 | 95.9 | 95.7 | 90.2 | 94.5 | 95.5 | 96.2 | 96.1 | 95.9 | 95.7 | 89.4 | 94.1 | 95.3 | 96.2 | 96.2 | 95.9 | 95.7 | 2017-09-01 | 2019-02-15
SunPower | SPR-X22-360-D-AC [240V] | 360 W, 240 Vac, Utility Interactive, monocrystalline ACPV Module, white backsheet. DC Module: SPR-X22-360. Micro-inverter: MI-C-320-US208/240-1X [240V]. | 0.32 | 240 | 96 | Y | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.1 |  |  | 53 | 60 | 64 | 0.03 | 0.06 | 0.1 | 0.16 | 0.24 | 0.32 | 89.7 | 94.1 | 95.3 | 96.2 | 96.1 | 95.9 | 95.7 | 90 | 94.3 | 95.4 | 96.3 | 96.3 | 96.2 | 95.8 | 89.6 | 94 | 95.2 | 96.3 | 96.4 | 96.2 | 95.8 | 2017-09-01 | 2019-02-15
SunPower | SPR-X22-370-D-AC [208V] | 370 W, 208 Vac, Utility Interactive, monocrystalline ACPV Module, white backsheet. DC Module: SPR-X22-370. Micro-inverter: MI-C-320-US208/240-1X [208V]. | 0.32 | 208 | 95.5 | Y | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.02 |  |  | 53 | 60 | 64 | 0.03 | 0.06 | 0.1 | 0.16 | 0.24 | 0.32 | 90.8 | 94.5 | 95.5 | 96.2 | 96.1 | 95.9 | 95.7 | 90.2 | 94.5 | 95.5 | 96.2 | 96.1 | 95.9 | 95.7 | 89.4 | 94.1 | 95.3 | 96.2 | 96.2 | 95.9 | 95.7 | 2018-01-16 | 2019-02-15
SunPower | SPR-X22-370-D-AC [240V] | 370 W, 240 Vac, Utility Interactive, monocrystalline ACPV Module, white backsheet. DC Module: SPR-X22-370. Micro-inverter: MI-C-320-US208/240-1X [240V]. | 0.32 | 240 | 96 | Y | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.1 |  |  | 53 | 60 | 64 | 0.03 | 0.06 | 0.1 | 0.16 | 0.24 | 0.32 | 89.7 | 94.1 | 95.3 | 96.2 | 96.1 | 95.9 | 95.7 | 90 | 94.3 | 95.4 | 96.3 | 96.3 | 96.2 | 95.8 | 89.6 | 94 | 95.2 | 96.3 | 96.4 | 96.2 | 95.8 | 2018-01-16 | 2019-02-15
SunPower | SPR-A390-G-AC [240V] | 390 W, 240 Vac, Utility Interactive, monocrystalline ACPV module, white backsheet, black frame. DC Module: SPR-A390. Microinverter: IQ7AS-66-ACM-US-x. | 0.349 | 240 | 97 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.349 |  |  | 38 | 40.5 | 43 | 0.03487 | 0.06974 | 0.10461 | 0.17435 | 0.26152 | 0.3487 | 95.1546 | 95.8056 | 96.6492 | 97.1481 | 96.9702 | 96.471 | 96.8132 | 95.0678 | 95.7094 | 96.5708 | 97.1127 | 96.977 | 96.4639 | 96.7913 | 95.0012 | 95.633 | 96.4691 | 97.072 | 96.9595 | 96.4604 | 96.7547 | 2019-07-15
SunPower | SPR-A395-G-AC [240V] | 395 W, 240 Vac Utility Interactive, monocrystalline ACPV Module, white backsheet. DC Module: SPR-A395. Micro-inverter: IQ7AS-66-ACM [240V]. | 0.349 | 240 | 97 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. |  |  |  | 38 | 40.5 | 43 | 0.03487 | 0.06974 | 0.10461 | 0.17435 | 0.26152 | 0.3487 | 95.1546 | 95.8056 | 96.6492 | 97.1481 | 96.9702 | 96.471 | 96.8132 | 95.0678 | 95.7094 | 96.5708 | 97.1127 | 96.977 | 96.4639 | 96.7913 | 95.0012 | 95.633 | 96.4691 | 97.072 | 96.9595 | 96.4604 | 96.7547 | 2019-04-02
SunPower | SPR-A400-G-AC [240V] | 400 W, 240 Vac Utility Interactive, monocrystalline ACPV Module, white backsheet. DC Module: SPR-A400. Micro-inverter: IQ7AS-66-ACM [240V]. | 0.349 | 240 | 97 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. |  |  |  | 38 | 40.5 | 43 | 0.03487 | 0.06974 | 0.10461 | 0.17435 | 0.26152 | 0.3487 | 95.1546 | 95.8056 | 96.6492 | 97.1481 | 96.9702 | 96.471 | 96.8132 | 95.0678 | 95.7094 | 96.5708 | 97.1127 | 96.977 | 96.4639 | 96.7913 | 95.0012 | 95.633 | 96.4691 | 97.072 | 96.9595 | 96.4604 | 96.7547 | 2019-04-02
SunPower | SPR-A405-G-AC [240V] | 405 W, 240 Vac Utility Interactive, monocrystalline ACPV Module, white backsheet. DC Module: SPR-A405. Micro-inverter: IQ7AS-66-ACM [240V]. | 0.349 | 240 | 97 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. |  |  |  | 38 | 40.5 | 43 | 0.03487 | 0.06974 | 0.10461 | 0.17435 | 0.26152 | 0.3487 | 95.1546 | 95.8056 | 96.6492 | 97.1481 | 96.9702 | 96.471 | 96.8132 | 95.0678 | 95.7094 | 96.5708 | 97.1127 | 96.977 | 96.4639 | 96.7913 | 95.0012 | 95.633 | 96.4691 | 97.072 | 96.9595 | 96.4604 | 96.7547 | 2019-04-02
SunPower | SPR-A410-G-AC [240V] | 410W, 240 Vac Utility Interactive, monocrystalline ACPV Module, white backsheet. DC Module: SPR-A410. Micro-inverter: IQ7AS-66-ACM [240V]. | 0.349 | 240 | 97 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. |  |  |  | 38 | 40.5 | 43 | 0.03487 | 0.06974 | 0.10461 | 0.17435 | 0.26152 | 0.3487 | 95.1546 | 95.8056 | 96.6492 | 97.1481 | 96.9702 | 96.471 | 96.8132 | 95.0678 | 95.7094 | 96.5708 | 97.1127 | 96.977 | 96.4639 | 96.7913 | 95.0012 | 95.633 | 96.4691 | 97.072 | 96.9595 | 96.4604 | 96.7547 | 2019-04-02
SunPower | SPR-A415-G-AC [240V] | 415 W, 240 Vac Utility Interactive, monocrystalline ACPV Module, white backsheet. DC Module: SPR-A415. Micro-inverter: IQ7AS-66-ACM [240V]. | 0.349 | 240 | 97 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. |  |  |  | 38 | 40.5 | 43 | 0.03487 | 0.06974 | 0.10461 | 0.17435 | 0.26152 | 0.3487 | 95.1546 | 95.8056 | 96.6492 | 97.1481 | 96.9702 | 96.471 | 96.8132 | 95.0678 | 95.7094 | 96.5708 | 97.1127 | 96.977 | 96.4639 | 96.7913 | 95.0012 | 95.633 | 96.4691 | 97.072 | 96.9595 | 96.4604 | 96.7547 | 2019-04-02
SunPower | SPR-A420-G-AC [240V] | 420 W, 240 Vac Utility Interactive, monocrystalline ACPV Module, white backsheet. DC Module: SPR-A420. Micro-inverter: IQ7AS-66-ACM [240V]. | 0.349 | 240 | 97 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. |  |  |  | 38 | 40.5 | 43 | 0.03487 | 0.06974 | 0.10461 | 0.17435 | 0.26152 | 0.3487 | 95.1546 | 95.8056 | 96.6492 | 97.1481 | 96.9702 | 96.471 | 96.8132 | 95.0678 | 95.7094 | 96.5708 | 97.1127 | 96.977 | 96.4639 | 96.7913 | 95.0012 | 95.633 | 96.4691 | 97.072 | 96.9595 | 96.4604 | 96.7547 | 2019-04-02
SunPower | SPR-A425-G-AC [240V] | 425 W, 240 Vac Utility Interactive, monocrystalline ACPV Module, white backsheet. DC Module: SPR-A425. Micro-inverter: IQ7AS-66-ACM [240V]. | 0.349 | 240 | 97 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. |  |  |  | 38 | 40.5 | 43 | 0.03487 | 0.06974 | 0.10461 | 0.17435 | 0.26152 | 0.3487 | 95.1546 | 95.8056 | 96.6492 | 97.1481 | 96.9702 | 96.471 | 96.8132 | 95.0678 | 95.7094 | 96.5708 | 97.1127 | 96.977 | 96.4639 | 96.7913 | 95.0012 | 95.633 | 96.4691 | 97.072 | 96.9595 | 96.4604 | 96.7547 | 2019-04-02
SunPower | SPR-2500 [240V] | 2500 W, 240 Vac Utility Interactive Inverter | 2.5 | 240 | 94.5 | Y | N |  | 3.9 |  |  | 100 | 218 | 400 | 0.25 | 0.5 | 0.75 | 1.25 | 1.88 | 2.5 | 87.1 | 93.3 | 94.9 | 95.8 | 95.8 | 95.6 | 95.2 | 85.2 | 92.4 | 93.8 | 95.2 | 95.4 | 95.1 | 94.6 | 80.4 | 90 | 91.7 | 93.7 | 94.5 | 93.8 | 93.2
SunPower | SPR-2500x [240V] | 2.5 kW, 240 Vac, 195-600 Vdc Grid Tie Inverter | 2.5 | 240 | 94 | Y | N |  | 1 | 2.5 | 1 | 100 | 266 | 480 | 0.25 | 0.5 | 0.75 | 1.25 | 1.88 | 2.5 | 88.5 | 92.7 | 94.1 | 94.8 | 94.8 | 94.5 | 94.4 | 87.7 | 92.3 | 93.7 | 94.5 | 94.6 | 94.4 | 94.1 | 86.3 | 90.9 | 92.6 | 93.8 | 94 | 93.8 | 93.3
SunPower | SPR-2800x [208V] | 2.7 kW, 208 Vac, 195-600 Vdc Grid Tie Inverter | 2.7 | 208 | 93.5 | Y | N |  | 1 | 2.7 | 1 | 100 | 266 | 480 | 0.27 | 0.54 | 0.81 | 1.35 | 2.025 | 2.7 | 88.7 | 93.1 | 94.1 | 94.6 | 94.5 | 94 | 94.1 | 88 | 92.8 | 93.8 | 94.4 | 94.3 | 93.8 | 93.9 | 84.6 | 90.6 | 92.3 | 93.4 | 93.4 | 92.5 | 92.7
SunPower | SPR-2800x [240V] | 2.8 kW, 240 Vac, 195-600 Vdc Grid Tie Inverter | 2.8 | 240 | 94 | Y | N |  | 1.3 | 2.8 | 1.3 | 100 | 266 | 480 | 0.28 | 0.56 | 0.84 | 1.4 | 2.1 | 2.8 | 89.3 | 93.5 | 94.4 | 95 | 94.8 | 94.4 | 94.5 | 88.6 | 93.1 | 94.2 | 94.7 | 94.6 | 94.2 | 94.3 | 85.3 | 91 | 92.7 | 93.8 | 93.7 | 92.7 | 93.1
SunPower | SPR-3000m [208V] | 3 kW, 208 Vac Utility Interactive Inverter with display | 3 | 208 | 95 | Y | N |  | 0.08 |  |  | 100 | 250 | 400 | 0.2 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 94 | 95.8 | 96 | 95.8 | 95.1 | 94.3 | 95.3 | 93.1 | 95.9 | 95.7 | 95.6 | 94.9 | 94 | 95.1 | 91.6 | 94.8 | 95.2 | 94.7 | 94.2 | 93.5 | 94.3
SunPower | SPR-3000m [240V] | 3 kW, 240 Vac Utility Interactive Inverter with display | 3 | 240 | 95.5 | Y | N |  | 0.07 |  |  | 100 | 250 | 400 | 0.2 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 93.4 | 95.9 | 96.3 | 96.5 | 96.1 | 95.6 | 96 | 92.5 | 95.8 | 96 | 96.1 | 95.8 | 95.1 | 95.7 | 90.5 | 94.6 | 95.4 | 95.3 | 95.2 | 94.6 | 95
SunPower | SPR-3300x [208V] | 3.1 kW, 208 Vac, 195-600 Vdc Grid Tie Inverter | 3.1 | 208 | 95 | Y | N |  | 1.24 | 3.1 | 1.24 | 100 | 250 | 400 | 0.31 | 0.62 | 0.93 | 1.55 | 2.325 | 3.1 | 91.4 | 94.7 | 95.4 | 95.6 | 95.5 | 95.1 | 95.3 | 90.9 | 94.4 | 95.2 | 95.6 | 95.4 | 95.1 | 95.2 | 89.3 | 93.4 | 94.5 | 95.2 | 95.2 | 94.9 | 94.7
SunPower | SPR-3300f [208V] | 3300 W, 208 Vac Utility Interactive Inverter | 3.3 | 208 | 95 | Y | N |  | 0.62 |  |  | 100 | 366 | 480 | 0.33 | 0.66 | 0.99 | 1.65 | 2.48 | 3.3 | 92 | 94.5 | 95.1 | 95.2 | 94.8 | 93.8 | 94.7 | 92 | 94.9 | 95.3 | 95.8 | 95.8 | 95.3 | 95.5 | 91.7 | 94.3 | 94.4 | 95.3 | 95.3 | 95.1 | 95
SunPower | SPR-3300f [240V] | 3300 W, 240 Vac Utility Interactive Inverter | 3.3 | 240 | 95.5 | Y | N |  | 0.83 |  |  | 100 | 390 | 480 | 0.33 | 0.66 | 0.99 | 1.65 | 2.48 | 3.3 | 91 | 94.5 | 95.3 | 95.6 | 95.5 | 94.8 | 95.3 | 91.9 | 95.1 | 95.3 | 96 | 96.1 | 95.9 | 95.8 | 91.4 | 94.7 | 94.9 | 95.6 | 95.7 | 95.6 | 95.3
SunPower | SPR-3300f [277V] | 3300 W, 277 Vac Utility Interactive Inverter | 3.3 | 277 | 95.5 | Y | N |  | 1.1 |  |  | 100 | 330 | 480 | 0.33 | 0.66 | 0.99 | 1.65 | 2.48 | 3.3 | 90.7 | 94.4 | 95.3 | 95.9 | 95.9 | 95.5 | 95.5 | 91 | 94.9 | 95.4 | 96.1 | 96.2 | 96.1 | 95.8 | 90.9 | 94.8 | 95.3 | 95.8 | 96 | 96.1 | 95.6
SunPower | SPR-3300x [240V] | 3.3 kW, 240 Vac, 195-600 Vdc Grid Tie Inverter | 3.3 | 240 | 95.5 | Y | N |  | 1.52 | 3.3 | 1.52 | 100 | 250 | 400 | 0.33 | 0.66 | 0.99 | 1.65 | 2.475 | 3.3 | 91.9 | 95 | 95.7 | 95.9 | 95.9 | 95.5 | 95.6 | 91.4 | 94.7 | 95.5 | 95.9 | 95.7 | 95.4 | 95.5 | 89.8 | 93.6 | 94.8 | 95.4 | 95.3 | 95.2 | 95
SunPower | SPR-3301f [208V] | 3300 W, 208 Vac Utility Interactive Inverter | 3.3 | 208 | 95.5 | Y | N |  | 0.53 | 3.3 | 0.53 | 100 | 366 | 480 | 0.33 | 0.66 | 0.99 | 1.65 | 2.475 | 3.3 | 92.9 | 94.67 | 95.24 | 95.4 | 95.13 | 94.37 | 95.05 | 93.04 | 95.01 | 95.5 | 95.98 | 95.85 | 95.37 | 95.66 | 92.51 | 93.92 | 94.7 | 95.44 | 95.49 | 95.23 | 95.17
SunPower | SPR-3301f [240V] | 3300 W, 240 Vac Utility Interactive Inverter | 3.3 | 240 | 95.5 | Y | N |  | 0.7 | 3.3 | 0.7 | 100 | 390 | 480 | 0.33 | 0.66 | 0.99 | 1.65 | 2.475 | 3.3 | 92.11 | 94.81 | 95.53 | 95.93 | 95.77 | 95.28 | 95.55 | 93.02 | 95.3 | 95.52 | 96.23 | 96.3 | 96.07 | 96 | 92.63 | 94.64 | 94.83 | 95.73 | 95.97 | 95.91 | 95.58
SunPower | SPR-3301f [277V] | 3300 W, 277 Vac Utility Interactive Inverter | 3.3 | 277 | 96 | Y | N |  | 0.94 | 3.3 | 0.94 | 100 | 330 | 480 | 0.33 | 0.66 | 0.99 | 1.65 | 2.475 | 3.3 | 91.26 | 94.76 | 95.6 | 96.2 | 96.24 | 95.93 | 95.87 | 91.44 | 95.25 | 95.55 | 96.39 | 96.49 | 96.34 | 96.09 | 92.25 | 94.89 | 95.24 | 95.96 | 96.29 | 96.37 | 95.87
SunPower | SPR-3500 [240V] | 3500 W, 240 Vac Utility Interactive Inverter | 3.5 | 240 | 95.5 | Y | N |  | 3.9 |  |  | 100 | 263 | 400 | 0.35 | 0.7 | 1.05 | 1.75 | 2.63 | 3.5 | 87.2 | 93.1 | 95.4 | 96.5 | 96.7 | 96.6 | 95.9 | 85.7 | 92.2 | 94.9 | 96.2 | 96.4 | 96.3 | 95.5 | 82.1 | 90.2 | 93.6 | 95.4 | 95.7 | 95.6 | 94.5
SunPower | SPR-4000m [208V] | 4 kW, 208 Vac Utility Interactive Inverter with display | 3.5 | 208 | 95.5 | Y | N |  | 0.14 |  |  | 100 | 310 | 480 | 0.35 | 0.7 | 1.05 | 1.75 | 2.63 | 3.5 | 94.3 | 96.3 | 96.5 | 96.4 | 95.8 | 94.9 | 95.9 | 93.5 | 96.2 | 96.1 | 96.1 | 95.5 | 94.8 | 95.6 | 91.5 | 94.9 | 95.4 | 95.1 | 94.8 | 94 | 94.7
SunPower | SPR-3801f [208V] | 3800 W, 208 Vac Utility Interactive Inverter | 3.8 | 208 | 95 | Y | N |  | 0.53 | 3.8 | 0.53 | 100 | 366 | 480 | 0.38 | 0.76 | 1.14 | 1.9 | 2.85 | 3.8 | 92.98 | 94.93 | 95.38 | 95.33 | 94.78 | 93.76 | 94.85 | 93.52 | 95.04 | 95.62 | 95.96 | 95.65 | 95.02 | 95.56 | 92.96 | 93.88 | 94.78 | 95.48 | 95.41 | 94.93 | 95.15
SunPower | SPR-3801f [240V] | 3800 W, 240 Vac Utility Interactive Inverter | 3.8 | 240 | 95.5 | Y | N |  | 0.7 | 3.8 | 0.7 | 100 | 390 | 480 | 0.38 | 0.76 | 1.14 | 1.9 | 2.85 | 3.8 | 92.7 | 95.04 | 95.67 | 95.88 | 95.57 | 94.87 | 95.47 | 93.31 | 95.3 | 95.74 | 96.28 | 96.2 | 95.81 | 95.98 | 93.05 | 94.61 | 95.08 | 95.85 | 95.93 | 95.71 | 95.62
SunPower | SPR-3801f [277V] | 3800 W, 277 Vac Utility Interactive Inverter | 3.8 | 277 | 96 | Y | N |  | 0.94 | 3.8 | 0.94 | 100 | 330 | 480 | 0.38 | 0.76 | 1.14 | 1.9 | 2.85 | 3.8 | 92.08 | 95.02 | 95.77 | 96.22 | 96.12 | 95.68 | 95.86 | 92.56 | 95.38 | 95.82 | 96.46 | 96.42 | 96.14 | 96.14 | 92.98 | 95.16 | 95.31 | 96.1 | 96.35 | 96.27 | 95.97
SunPower | SPR-4000f [208V] | 4000 W, 208 Vac Utility Interactive Inverter | 3.8 | 208 | 95 | Y | N |  | 0.62 |  |  | 100 | 366 | 480 | 0.38 | 0.76 | 1.14 | 1.9 | 2.85 | 3.8 | 93 | 94.9 | 95.3 | 95.1 | 94.4 | 93 | 94.6 | 93.6 | 95.1 | 95.7 | 95.9 | 95.6 | 94.9 | 95.6 | 92.7 | 94.4 | 95 | 95.4 | 95.2 | 94.7 | 95
SunPower | SPR-4000x [208V] | 3.8 kW, 208 Vac, 195-600 Vdc Grid Tie Inverter | 3.8 | 208 | 95 | Y | N |  | 0.99 | 3.8 | 0.99 | 100 | 300 | 480 | 0.38 | 0.76 | 1.14 | 1.9 | 2.85 | 3.8 | 91.7 | 94.8 | 95.5 | 95.7 | 95.4 | 95.1 | 95.3 | 91 | 94.6 | 95.3 | 95.6 | 95.4 | 94.9 | 95.2 | 90.2 | 93.6 | 94.7 | 95.1 | 95.1 | 94.7 | 94.7
SunPower | SPR-4000f [240V] | 4000 W, 240 Vac Utility Interactive Inverter | 4 | 240 | 95.5 | Y | N |  | 0.83 |  |  | 100 | 390 | 480 | 0.4 | 0.8 | 1.2 | 2 | 3 | 4 | 92.3 | 94.9 | 95.5 | 95.6 | 95.1 | 94.1 | 95.1 | 93 | 95.2 | 95.7 | 96.1 | 96 | 95.6 | 95.8 | 92.9 | 94.9 | 95.2 | 95.6 | 95.7 | 95.4 | 95.4
SunPower | SPR-4000f [277V] | 4000 W, 277 Vac Utility Interactive Inverter | 4 | 277 | 95.5 | Y | N |  | 1.1 |  |  | 100 | 330 | 480 | 0.4 | 0.8 | 1.2 | 2 | 3 | 4 | 92.1 | 94.9 | 95.6 | 95.9 | 95.7 | 94.9 | 95.5 | 92 | 95.2 | 95.7 | 96.2 | 96.2 | 95.8 | 95.9 | 92.6 | 95.1 | 95.3 | 95.9 | 96.1 | 96 | 95.7
SunPower | SPR-4000m [240V] | 4 kW, 240 Vac Utility Interactive Inverter with display | 4 | 240 | 96 | Y | N |  | 0.17 |  |  | 100 | 310 | 480 | 0.25 | 0.8 | 1.2 | 2 | 3 | 4 | 92.5 | 96.4 | 96.8 | 96.7 | 96.4 | 96 | 96.3 | 91.9 | 96.2 | 96.3 | 96.5 | 96 | 95.5 | 96 | 89.1 | 94.7 | 95.6 | 95.5 | 95.3 | 94.9 | 95.1
SunPower | SPR-4000x [240V] | 4.0 kW, 240 Vac, 195-600 Vdc Grid Tie Inverter | 4 | 240 | 95.5 | Y | N |  | 1.1 | 4 | 1.1 | 100 | 300 | 480 | 0.4 | 0.8 | 1.2 | 2 | 3 | 4 | 92.2 | 95.1 | 95.8 | 96 | 95.8 | 95.5 | 95.7 | 91.6 | 94.9 | 95.7 | 95.9 | 95.8 | 95.3 | 95.5 | 90.7 | 94.2 | 95 | 95.5 | 95.4 | 95.1 | 95.1
SunPower | SPR-5000x [208V] | 4.5 kW, 208 Vac, 195-600 Vdc Grid Tie Inverter | 4.5 | 208 | 95 | Y | N |  | 1 | 4.5 | 1 | 100 | 300 | 480 | 0.45 | 0.9 | 1.35 | 2.25 | 3.375 | 4.5 | 92.1 | 94.9 | 95.5 | 95.5 | 94.9 | 94.3 | 95 | 91.8 | 94.7 | 95.3 | 95.4 | 94.9 | 94.3 | 94.9 | 90.5 | 93.9 | 94.6 | 95 | 94.7 | 94.2 | 94.5
SunPower | SPR-4600 [208V] | 4600 W, 208 Vac Utility Interactive Inverter | 4.6 | 208 | 95.5 | Y | N |  | 4 | 4.6 | 4 | 100 | 254 | 400 | 0.46 | 0.92 | 1.38 | 2.3 | 3.45 | 4.6 | 90.3 | 94.8 | 95.9 | 96.5 | 96.5 | 96.2 | 96.1 | 89.2 | 94.3 | 95.6 | 96.3 | 96.4 | 96.1 | 95.9 | 86.5 | 92.9 | 94.7 | 95.6 | 95.7 | 95.4 | 95
SunPower | SPR-5000m [208V] | 5 kW, 208 Vac Utility Interactive Inverter with display | 5 | 208 | 95.5 | Y | N |  | 0.46 |  |  | 100 | 310 | 480 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 91.5 | 95.7 | 96.2 | 96.7 | 96.7 | 96.3 | 96.4 | 89.9 | 95 | 95.7 | 96.2 | 96.4 | 96 | 95.9 | 86.3 | 92.5 | 94.3 | 95 | 95.1 | 95 | 94.5
SunPower | SPR-5000m [240V] | 5 kW, 240 Vac Utility Interactive Inverter with display | 5 | 240 | 95.5 | Y | N |  | 0.72 |  |  | 100 | 310 | 480 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 91 | 95.7 | 96.2 | 96.8 | 96.8 | 96.5 | 96.4 | 89.7 | 94.9 | 95.7 | 96.2 | 96.4 | 96.2 | 95.9 | 86.2 | 92.5 | 94.3 | 95.2 | 95.2 | 95.1 | 94.6
SunPower | SPR-5000m [277V] | 5 kW, 277 Vac Utility Interactive Inverter with display | 5 | 277 | 95.5 | Y | N |  | 1.41 |  |  | 100 | 310 | 480 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 91.5 | 95.8 | 96.5 | 96.8 | 96.5 | 96.6 | 96.3 | 90 | 95 | 95.8 | 96.2 | 96.5 | 96.2 | 96 | 86.3 | 92.3 | 94.4 | 95.2 | 95.2 | 95.2 | 94.6
SunPower | SPR-5000x [240V] | 5.0 kW, 240 Vac, 195-600 Vdc Grid Tie Inverter | 5 | 240 | 95.5 | Y | N |  | 1 | 5 | 1 | 100 | 300 | 480 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 93.2 | 95.5 | 95.9 | 95.9 | 95.5 | 94.8 | 95.5 | 92.7 | 95.3 | 95.8 | 95.8 | 95.4 | 94.8 | 95.4 | 91.5 | 94.6 | 95.3 | 95.4 | 95.1 | 94.5 | 95
SunPower | SPR-5200 [240V] | 5200 W, 240 Vac Utility Interactive Inverter | 5.2 | 240 | 96 | Y | N |  | 4 | 5.2 | 4 | 100 | 280 | 400 | 0.52 | 1.04 | 1.56 | 2.6 | 3.9 | 5.2 | 89.4 | 94.8 | 96 | 96.8 | 97 | 96.8 | 96.4 | 88.6 | 94.4 | 95.7 | 96.7 | 96.8 | 96.6 | 96.2 | 87.7 | 93.1 | 94.8 | 96.1 | 96.3 | 96.1 | 95.5
SunPower | SPR-6000m [208V] | 6 kW, 208 Vac Utility Interactive Inverter with display | 6 | 208 | 95.5 | Y | N |  | 0.46 |  |  | 100 | 310 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 92.5 | 95.8 | 96.5 | 96.9 | 96.5 | 95.9 | 96.3 | 91.2 | 95.6 | 95.9 | 96.3 | 96.1 | 95.6 | 95.9 | 88 | 93.5 | 94.8 | 94.6 | 94.9 | 94.6 | 94.5
SunPower | SPR-6000m [240V] | 6 kW, 240 Vac Utility Interactive Inverter with display | 6 | 240 | 95.5 | Y | N |  | 0.72 |  |  | 100 | 310 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 92.6 | 96.1 | 96.5 | 96.8 | 96.7 | 96 | 96.4 | 91.3 | 95.6 | 96 | 96.3 | 96.3 | 95.9 | 96 | 87.9 | 93.6 | 94.8 | 95.1 | 95 | 94.8 | 94.7
SunPower | SPR-6000m [277V] | 6 kW, 277 Vac Utility Interactive Inverter with display | 6 | 277 | 96 | Y | N |  | 1.41 |  |  | 100 | 310 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 92.3 | 96 | 96.7 | 97 | 96.7 | 96.5 | 96.5 | 91.3 | 95.6 | 96.2 | 96.4 | 96.4 | 96 | 96.1 | 87.8 | 93.6 | 94.9 | 95.2 | 95.1 | 94.9 | 94.7
SunPower | SPR-6500f [208V] | 6500 W, 208 Vac Utility Interactive Inverter | 6.5 | 208 | 95 | Y | N |  | 0.71 |  |  | 100 | 366 | 480 | 0.65 | 1.3 | 1.95 | 3.25 | 4.88 | 6.5 | 92.8 | 94.7 | 94.6 | 95.2 | 94.7 | 93.7 | 94.6 | 93 | 94.9 | 95.2 | 95.7 | 95.6 | 95.2 | 95.4 | 91.8 | 93.8 | 94.6 | 94.9 | 95 | 94.9 | 94.7
SunPower | SPR-6500f [240V] | 6500 W, 240 Vac Utility Interactive Inverter | 6.5 | 240 | 95.5 | Y | N |  | 0.76 |  |  | 100 | 390 | 480 | 0.65 | 1.3 | 1.95 | 3.25 | 4.88 | 6.5 | 92.7 | 95 | 95.1 | 95.6 | 95.4 | 94.8 | 95.3 | 93 | 94.9 | 95.5 | 95.8 | 96 | 95.8 | 95.7 | 91.8 | 94.1 | 94.8 | 95.2 | 95.5 | 95.4 | 95.1
SunPower | SPR-6500f [277V] | 6500 W, 277 Vac Utility Interactive Inverter | 6.5 | 277 | 96 | Y | N |  | 1.02 |  |  | 100 | 330 | 480 | 0.65 | 1.3 | 1.95 | 3.25 | 4.88 | 6.5 | 93.5 | 95.4 | 95.7 | 96 | 96 | 95.5 | 95.8 | 93.9 | 95.5 | 96 | 96.2 | 96.3 | 96.2 | 96.1 | 93.8 | 95 | 95.6 | 95.8 | 96.1 | 96.1 | 95.8
SunPower | SPR-6501f [208V] | 6500 W, 208 Vac Utility Interactive Inverter | 6.5 | 208 | 95 | Y | N |  | 0.6 | 6.5 | 0.6 | 100 | 366 | 480 | 0.65 | 1.3 | 1.95 | 3.25 | 4.875 | 6.5 | 93.55 | 95.01 | 94.97 | 95.27 | 94.94 | 94.12 | 94.92 | 93.97 | 95.36 | 95.54 | 95.84 | 95.71 | 95.26 | 95.61 | 92.88 | 94.56 | 95.06 | 95.27 | 95.35 | 95.11 | 95.15
SunPower | SPR-6501f [240V] | 6500 W, 240 Vac Utility Interactive Inverter | 6.5 | 240 | 95.5 | Y | N |  | 0.8 | 6.5 | 0.8 | 100 | 390 | 480 | 0.65 | 1.3 | 1.95 | 3.25 | 4.875 | 6.5 | 93.66 | 95.4 | 95.56 | 95.81 | 95.62 | 95.09 | 95.53 | 94.19 | 95.48 | 95.86 | 96.09 | 96.16 | 95.91 | 95.98 | 93.3 | 94.9 | 95.53 | 95.56 | 95.81 | 95.74 | 95.57
SunPower | SPR-6501f [277V] | 6500 W, 277 Vac Utility Interactive Inverter | 6.5 | 277 | 96 | Y | N |  | 1.1 | 6.5 | 1.1 | 100 | 330 | 480 | 0.65 | 1.3 | 1.95 | 3.25 | 4.875 | 6.5 | 93.95 | 95.72 | 96.02 | 96.18 | 96.13 | 95.81 | 96 | 94.26 | 95.79 | 96.3 | 96.38 | 96.43 | 96.26 | 96.28 | 94.08 | 95.4 | 95.87 | 95.9 | 96.18 | 96.28 | 95.97
SunPower | SPR-7000m [208V] | 7 kW, 208 Vac Utility Interactive Inverter with display | 7 | 208 | 95.5 | Y | N |  | 0.46 |  |  | 100 | 310 | 480 | 0.7 | 1.4 | 2.1 | 3.5 | 5.25 | 7 | 94 | 96.3 | 97.1 | 96.7 | 96.2 | 95.4 | 96.3 | 92.7 | 96.1 | 96.1 | 96.2 | 95.9 | 95.3 | 95.9 | 89.7 | 94.2 | 95 | 94.9 | 94.8 | 94.1 | 94.6
SunPower | SPR-7000m [240V] | 7 kW, 240 Vac Utility Interactive Inverter with display | 7 | 240 | 96 | Y | N |  | 0.72 |  |  | 100 | 310 | 480 | 0.7 | 1.4 | 2.1 | 3.5 | 5.25 | 7 | 93.7 | 96.2 | 96.8 | 96.9 | 96.5 | 95.8 | 96.5 | 92.3 | 96.1 | 96.1 | 96.4 | 96.1 | 95.6 | 96 | 89.3 | 94.3 | 95.1 | 95.6 | 95 | 94.7 | 94.8
SunPower | SPR-7000m [277V] | 7 kW, 277 Vac Utility Interactive Inverter with display | 7 | 277 | 96 | Y | N |  | 1.41 |  |  | 100 | 310 | 480 | 0.7 | 1.4 | 2.1 | 3.5 | 5.25 | 7 | 93.7 | 96.3 | 96.8 | 97 | 96.5 | 95.9 | 96.5 | 92.5 | 96.1 | 96.3 | 96.5 | 96.2 | 95.6 | 96.1 | 89.3 | 94.2 | 95.2 | 95 | 95.1 | 94.6 | 94.8
SunPower | SPR-7501f [208V] | 7500 W, 208 Vac Utility Interactive Inverter | 7.5 | 208 | 95 | Y | N |  | 0.6 | 7.5 | 0.6 | 100 | 366 | 480 | 0.75 | 1.5 | 2.25 | 3.75 | 5.625 | 7.5 | 94.23 | 95.18 | 95 | 95.19 | 94.68 | 93.6 | 94.78 | 94.47 | 95.69 | 95.69 | 95.89 | 95.6 | 94.94 | 95.6 | 93.01 | 95.11 | 95.35 | 95.4 | 95.31 | 94.87 | 95.21
SunPower | SPR-7501f [240V] | 7500 W, 240 Vac Utility Interactive Inverter | 7.5 | 240 | 95.5 | Y | N |  | 0.8 | 7.5 | 0.8 | 100 | 390 | 480 | 0.75 | 1.5 | 2.25 | 3.75 | 5.625 | 7.5 | 94.37 | 95.6 | 95.61 | 95.78 | 95.46 | 94.73 | 95.47 | 94.49 | 95.9 | 96.06 | 96.22 | 96.16 | 95.73 | 96.06 | 93.98 | 95.29 | 95.68 | 95.83 | 95.86 | 95.61 | 95.71
SunPower | SPR-7501f [277V] | 7500 W, 277 Vac Utility Interactive Inverter | 7.5 | 277 | 96 | Y | N |  | 1.1 | 7.5 | 1.1 | 100 | 330 | 480 | 0.75 | 1.5 | 2.25 | 3.75 | 5.625 | 7.5 | 94.05 | 95.73 | 95.93 | 96.15 | 95.95 | 95.45 | 95.88 | 94.27 | 95.84 | 96.09 | 96.36 | 96.26 | 95.96 | 96.14 | 93.86 | 95.28 | 95.81 | 95.97 | 96.16 | 96.11 | 95.94
SunPower | SPR-8000f [208V] | 7600 W 208 Vac Utility Interactive Inverter | 7.6 | 208 | 95 | Y | N |  | 0.71 |  |  | 100 | 366 | 480 | 0.76 | 1.52 | 2.28 | 3.8 | 5.7 | 7.6 | 93.4 | 94.8 | 94.4 | 95 | 94.3 | 92.9 | 94.4 | 93.3 | 95.1 | 95.4 | 95.7 | 95.5 | 94.7 | 95.4 | 92.3 | 94.4 | 94.5 | 95.1 | 95 | 94.5 | 94.8
SunPower | SPR-8000m [240V] | 8 kW, 240 Vac Sunny Boy Utility Interactive Inverter with display | 7.6 | 240 | 96 | Y | N |  | 0.17 |  |  | 100 | 345 | 480 | 0.76 | 1.52 | 2.28 | 3.8 | 5.7 | 7.6 | 95.04 | 96.48 | 96.84 | 96.82 | 96.5 | 96.01 | 96.53 | 94.59 | 96.19 | 96.61 | 96.63 | 96.3 | 96.29 | 96.33 | 93.13 | 95.28 | 95.83 | 95.98 | 95.72 | 95.94 | 95.67
SunPower | SPR-8000f [240V] | 8000 W, 240 Vac Utility Interactive Inverter | 8 | 240 | 95.5 | Y | N |  | 0.76 |  |  | 100 | 390 | 480 | 0.8 | 1.6 | 2.4 | 4 | 6 | 8 | 94 | 95.3 | 95.2 | 95.6 | 95.1 | 94 | 95.1 | 93.9 | 95.5 | 95.6 | 96 | 96 | 95.5 | 95.8 | 93.4 | 94.9 | 95.4 | 95.5 | 95.5 | 95.3 | 95.4
SunPower | SPR-8000f [277V] | 8000 W, 277 Vac Utility Interactive Inverter | 8 | 277 | 96 | Y | N |  | 1.02 |  |  | 100 | 330 | 480 | 0.8 | 1.6 | 2.4 | 4 | 6 | 8 | 94.3 | 95.8 | 95.7 | 96.1 | 95.7 | 95 | 95.7 | 95 | 96 | 96.2 | 96.4 | 96.3 | 95.8 | 96.2 | 94.8 | 95.8 | 95.6 | 96.1 | 96.2 | 96 | 96
SunPower | SPR-8000m [277V] | 8kW, 277 Vac Sunny Boy Utility Interactive Inverter with display | 8 | 277 | 96 | Y | N |  | 0.15 |  |  | 100 | 345 | 480 | 0.8 | 1.6 | 2.4 | 4 | 6 | 8 | 95.12 | 96.22 | 96.48 | 96.46 | 96.17 | 95.56 | 96.2 | 94.85 | 95.86 | 96.28 | 96.25 | 95.89 | 95.28 | 95.93 | 93.45 | 95.01 | 95.41 | 95.51 | 95.24 | 94.7 | 95.21
SunPower | SPR-10001f [208V] | 10000 W, 208 Vac Utility Interactive Inverter | 9.995 | 208 | 95 | Y | N |  | 0.77 | 10 | 0.77 | 100 | 366 | 480 | 0.9995 | 1.999 | 2.999 | 4.998 | 7.496 | 9.995 | 93.96 | 94.59 | 95.13 | 95.15 | 94.79 | 93.95 | 94.82 | 93.94 | 95.27 | 95.61 | 95.79 | 95.64 | 95.11 | 95.55 | 92.8 | 94.78 | 94.89 | 95.27 | 95.3 | 95 | 95.1
SunPower | SPR-10001f [240V] | 10000 W, 240 Vac Utility Interactive Inverter | 9.995 | 240 | 95.5 | Y | N |  | 1 | 10 | 1 | 100 | 390 | 480 | 0.9995 | 1.999 | 2.999 | 4.998 | 7.496 | 9.995 | 94.18 | 95.24 | 95.61 | 95.7 | 95.51 | 94.94 | 95.47 | 93.77 | 95.61 | 95.8 | 96.04 | 96.12 | 95.86 | 95.93 | 93.16 | 95.13 | 95.2 | 95.55 | 95.79 | 95.7 | 95.52
SunPower | SPR-10001f [277V] | 10000 W, 277 Vac Utility Interactive Inverter | 9.995 | 277 | 96 | Y | N |  | 1.36 | 10 | 1.36 | 100 | 330 | 480 | 0.9995 | 1.999 | 2.999 | 4.998 | 7.496 | 9.995 | 94.28 | 95.67 | 95.87 | 96.05 | 95.98 | 95.59 | 95.88 | 94.07 | 95.87 | 96.02 | 96.23 | 96.3 | 96.08 | 96.13 | 93.68 | 95.46 | 95.44 | 95.8 | 96.12 | 96.16 | 95.84
SunPower | SPR-10000f [208V] | 10000 W, 208 Vac Utility Interactive Inverter | 10 | 208 | 95 | Y | N |  | 0.64 |  |  | 100 | 366 | 480 | 1 | 2 | 3 | 5 | 7.5 | 10 | 93.8 | 94.5 | 95.2 | 95.3 | 94.9 | 93.8 | 94.9 | 93.5 | 95.2 | 95.6 | 95.9 | 95.8 | 95.3 | 95.6 | 92.5 | 94.4 | 94.8 | 95.2 | 95.2 | 95 | 95
SunPower | SPR-10000f [240V] | 10000 W, 240 Vac Utility Interactive Inverter | 10 | 240 | 95.5 | Y | N |  | 0.85 |  |  | 100 | 390 | 480 | 1 | 2 | 3 | 5 | 7.5 | 10 | 94.1 | 95.1 | 95.7 | 95.8 | 95.5 | 94.9 | 95.5 | 93.7 | 95.5 | 95.9 | 96.2 | 96.2 | 96 | 96 | 93.2 | 95 | 95.3 | 95.6 | 95.7 | 95.6 | 95.5
SunPower | SPR-10000f [277V] | 10000 W, 277 Vac Utility Interactive Inverter | 10 | 277 | 96 | Y | N |  | 1.13 |  |  | 100 | 330 | 480 | 1 | 2 | 3 | 5 | 7.5 | 10 | 94.2 | 95.7 | 95.9 | 96.1 | 96 | 95.6 | 95.9 | 94.5 | 96 | 96.1 | 96.3 | 96.4 | 96.3 | 96.3 | 94.5 | 95.6 | 95.7 | 96 | 96.1 | 96.2 | 96
SunPower | SPR 11401f [208V] | 11400 W, 208 Vac, 3-phase Utility Interactive Inverter | 11.4 | 208 | 95 | Y | N |  | 0.77 | 11.4 | 0.77 | 230 | 366 | 480 | 1.14 | 2.28 | 3.42 | 5.7 | 8.55 | 11.4 | 94.38 | 94.56 | 95.11 | 95.08 | 94.48 | 93.34 | 94.63 | 94.57 | 95.31 | 95.74 | 95.78 | 95.43 | 94.8 | 95.47 | 93.33 | 94.99 | 95.17 | 95.33 | 95.22 | 94.66 | 95.12
SunPower | SPR 11401f [240V] | 11400 W, 240 Vac, 3-phase Utility Interactive Inverter | 11.4 | 240 | 95.5 | Y | N |  | 1 | 11.4 | 1 | 230 | 390 | 480 | 1.14 | 2.28 | 3.42 | 5.7 | 8.55 | 11.4 | 94.59 | 95.19 | 95.62 | 95.67 | 95.28 | 94.5 | 95.33 | 94.33 | 95.72 | 95.9 | 96.12 | 96.01 | 95.61 | 95.92 | 93.56 | 95.36 | 95.49 | 95.7 | 95.77 | 95.51 | 95.6
SunPower | SPR 11401f [277V] | 12000 W, 240 Vac, 3-phase Utility Interactive Inverter | 11.4 | 277 | 96 | Y | N |  | 1.36 | 11.4 | 1.36 | 240 | 330 | 480 | 1.14 | 2.28 | 3.42 | 5.7 | 8.55 | 11.4 | 94.66 | 95.65 | 95.94 | 96.03 | 95.84 | 95.31 | 95.81 | 94.49 | 95.89 | 96.13 | 96.27 | 96.21 | 95.88 | 96.11 | 93.86 | 95.69 | 95.65 | 95.97 | 96.14 | 96.05 | 95.93
SunPower | SPR-11400f-3 [208V] | 11400 W, 208 Vac, 3-phase Utility Interactive Inverter | 11.4 | 208 | 95 | Y | N |  | 0.9 |  |  | 230 | 365 | 480 | 1.14 | 2.28 | 3.42 | 5.7 | 8.55 | 11.4 | 94.2 | 94.3 | 95.1 | 95.1 | 94.4 | 93 | 94.55 | 94.4 | 95.3 | 95.8 | 95.9 | 95.6 | 94.9 | 95.59 | 93.4 | 94.6 | 95 | 95.3 | 95.2 | 94.7 | 95.05
SunPower | SPR-11400f-3 [240V] | 11400 W, 240 Vac, 3-phase Utility Interactive Inverter | 11.4 | 240 | 95.5 | Y | N |  | 1 |  |  | 230 | 390 | 480 | 1.14 | 2.28 | 3.42 | 5.7 | 8.55 | 11.4 | 94.3 | 95 | 95.6 | 95.7 | 95.2 | 94.2 | 95.25 | 94.1 | 95.7 | 96 | 96.2 | 96.1 | 95.7 | 95.99 | 93.4 | 95.1 | 95.4 | 95.7 | 95.7 | 95.6 | 95.54
SunPower | SPR-11401f-3 Delta [208V] | 11400 W, 208 Vac, 3-phase Utility Interactive Inverter | 11.4 | 208 | 95 | Y | N |  | 0.9 | 11.4 | 0.9 | 230 | 366 | 480 | 1.14 | 2.28 | 3.42 | 5.7 | 8.55 | 11.4 | 94.57 | 94.79 | 95.21 | 95.21 | 94.63 | 93.51 | 94.77 | 94.66 | 95.45 | 95.78 | 95.89 | 95.55 | 94.88 | 95.57 | 93.71 | 94.96 | 95.25 | 95.43 | 95.29 | 94.8 | 95.21
SunPower | SPR-11401f-3 Delta [240V] | 11400 W, 240 Vac, 3-phase Utility Interactive Inverter | 11.4 | 240 | 96 | Y | N |  | 1.2 | 11.4 | 1.2 | 230 | 390 | 480 | 1.14 | 2.28 | 3.42 | 5.7 | 8.55 | 11.4 | 94.67 | 95.44 | 95.75 | 95.82 | 95.47 | 94.68 | 95.5 | 94.49 | 95.79 | 96.03 | 96.25 | 96.15 | 95.75 | 96.05 | 94.01 | 95.42 | 95.54 | 95.83 | 95.87 | 95.65 | 95.71
SunPower | SPR-12000f [208V] | 11400 W, 208 Vac, 3-phase Utility Interactive Inverter | 11.4 | 208 | 95 | Y | N |  | 0.9 |  |  | 230 | 365 | 480 | 1.14 | 2.28 | 3.42 | 5.7 | 8.55 | 11.4 | 94.2 | 94.3 | 95.1 | 95.1 | 94.4 | 93 | 94.55 | 94.4 | 95.3 | 95.8 | 95.9 | 95.6 | 94.9 | 95.59 | 93.4 | 94.6 | 95 | 95.3 | 95.2 | 94.7 | 95.05
SunPower | SPR-12000f [240V] | 12000 W, 240 Vac, 3-Phase Utility Interactive Inverter | 12 | 240 | 95.5 | Y | N |  | 1 |  |  | 230 | 390 | 480 | 1.2 | 2.4 | 3.6 | 6 | 9 | 12 | 94.4 | 94.8 | 95.5 | 95.7 | 95.1 | 94 | 95.17 | 94.2 | 95.5 | 95.9 | 96.2 | 96 | 95.5 | 95.93 | 93.4 | 95.1 | 95.4 | 95.6 | 95.7 | 95.4 | 95.49
SunPower | SPR-12000f-3 [277V] | 12000 W, 277 Vac, 3-phase Utility Interactive Inverter | 12 | 277 | 96 | Y | N |  | 1 |  |  | 240 | 330 | 480 | 1.2 | 2.4 | 3.6 | 6 | 9 | 12 | 94.7 | 95.5 | 95.9 | 96 | 95.8 | 95.1 | 95.8 | 94.7 | 95.9 | 96.1 | 96.3 | 96.3 | 95.8 | 96.2 | 94.3 | 95.7 | 95.8 | 96 | 96.2 | 96 | 96
SunPower | SPR-12000m-3 [480V] | Sunny Tripower TL-US 12 kW, 480 Vac 3-phase, Utility Interactive Inverter | 12 | 480 | 97.5 | Y | N | Multiple Listing of SMA America | 1.79 |  |  | 300 | 675 | 800 | 1.2 | 2.4 | 3.6 | 6 | 9 | 12 | 92.8947 | 95.8254 | 96.4946 | 96.6907 | 96.6273 | 96.507 | 96.4293 | 94.8857 | 96.883 | 97.4944 | 97.777 | 97.8321 | 97.8114 | 97.6137 | 94.1548 | 97.204 | 97.7008 | 98.014 | 98.1838 | 98.1898 | 97.8803 | 2017-09-01 | 2018-10-15
SunPower | SPR-12000m-3-H [480V] | Sunny Tripower TL-US 12 kW, 480 Vac, 3-phase, transformerless Utility Interactive Inverter | 12 | 480 | 97.5 | Y | N | Multiple Listing of SMA America | 1.79 |  |  | 300 | 675 | 800 | 1.2 | 2.4 | 3.6 | 6 | 9 | 12 | 92.8947 | 95.8254 | 96.4946 | 96.6907 | 96.6273 | 96.507 | 96.4293 | 94.8857 | 96.883 | 97.4944 | 97.777 | 97.8321 | 97.8114 | 97.6137 | 94.1548 | 97.204 | 97.7008 | 98.014 | 98.1838 | 98.1898 | 97.8803 | 2017-09-01 | 2018-10-15
SunPower | SPR-12001f-3 WYE [277V] | 12000 W, 277 Vac, 3-phase Utility Interactive Inverter | 12 | 277 | 96 | Y | N |  | 0.5 | 12 | 0.5 | 240 | 330 | 480 | 1.2 | 2.4 | 3.6 | 6 | 9 | 12 | 92.62 | 95.2 | 96.16 | 96.32 | 96.05 | 95.44 | 95.91 | 92.45 | 95.69 | 96.17 | 96.56 | 96.45 | 96.06 | 96.22 | 94.43 | 95.61 | 95.78 | 96.24 | 96.43 | 96.29 | 96.19
SunPower | SPR-15000m-3 [480V] | Sunny Tripower TL-US 15 kW, 480 Vac, 3-phase, transformerless Utility Interactive Inverter | 15 | 480 | 97.5 | Y | N | Multiple Listing of SMA America | 1.79 |  |  | 300 | 675 | 800 | 1.5 | 3 | 4.5 | 7.5 | 11.25 | 15 | 93.8557 | 96.2201 | 96.7314 | 96.6627 | 96.5254 | 96.3471 | 96.448 | 95.4959 | 97.1929 | 97.7963 | 97.8029 | 97.833 | 97.7774 | 97.694 | 95.5529 | 97.5151 | 97.9236 | 98.173 | 98.2148 | 98.1572 | 98.0267 | 2017-09-01 | 2018-10-15
SunPower | SPR-15000m-3-H [480V] | Sunny Tripower TL-US 15 kW, 480 Vac, 3-phase, transformerless Utility Interactive Inverter | 15 | 480 | 97.5 | Y | N | Multiple Listing of SMA America | 1.79 |  |  | 300 | 675 | 800 | 1.5 | 3 | 4.5 | 7.5 | 11.25 | 15 | 93.8557 | 96.2201 | 96.7314 | 96.6627 | 96.5254 | 96.3471 | 96.448 | 95.4959 | 97.1929 | 97.7963 | 97.8029 | 97.833 | 97.7774 | 97.694 | 95.5529 | 97.5151 | 97.9236 | 98.173 | 98.2148 | 98.1572 | 98.0267 | 2017-09-01 | 2018-10-15
SunPower | SPR-20000m-3 [480V] | Sunny Tripower TL-US 20 kW, 480 Vac, 3-phase, transformerless Utility Interactive Inverter | 20 | 480 | 97.5 | Y | N | Multiple Listing of SMA America | 1.79 |  |  | 380 | 695 | 800 | 2 | 4 | 6 | 10 | 15 | 20 | 95.166 | 96.9605 | 97.2062 | 97.0835 | 96.9341 | 96.7051 | 96.9173 | 97.2288 | 98.2895 | 98.5099 | 98.5485 | 97.8368 | 97.7051 | 98.0588 | 96.4929 | 97.8688 | 98.1306 | 98.2198 | 98.1746 | 98.0422 | 98.0897 | 2017-09-01 | 2018-10-15
SunPower | SPR-20000m-3-H [480V] | Sunny Tripower TL-US 20 kW, 480 Vac, 3-phase, transformerless Utility Interactive Inverter | 20 | 480 | 97.5 | Y | N | Multiple Listing of SMA America | 1.79 |  |  | 380 | 695 | 800 | 2 | 4 | 6 | 10 | 15 | 20 | 95.166 | 96.9605 | 97.2062 | 97.0835 | 96.9341 | 96.7051 | 96.9173 | 97.2288 | 98.2895 | 98.5099 | 98.5485 | 97.8368 | 97.7051 | 98.0588 | 96.4929 | 97.8688 | 98.1306 | 98.2198 | 98.1746 | 98.0422 | 98.0897 | 2017-09-01 | 2018-10-15
SunPower | SPR-24000m-3 [480V] | Sunny Tripower TL-US 24 kW, 480 Vac, 3-phase, transformerless Utility Interactive Inverter | 24.06 | 480 | 98 | Y | N | Multiple Listing of SMA America | 1.79 |  |  | 450 | 712 | 800 | 2.406 | 4.812 | 7.218 | 12.03 | 18.045 | 24.06 | 96.0825 | 97.4242 | 97.4447 | 97.3151 | 97.1222 | 96.8659 | 97.1621 | 97.4599 | 98.348 | 98.5031 | 98.5314 | 98.4351 | 98.2665 | 98.4117 | 96.9099 | 98.0049 | 98.1886 | 98.2041 | 98.0766 | 97.8823 | 98.0569 | 2017-09-01 | 2018-10-15
SunPower | SPR-24000m-3-H [480V] | Sunny Tripower TL-US 24 kW, 480 Vac, 3-phase, transformerless Utility Interactive Inverter | 24.06 | 480 | 98 | Y | N | Multiple Listing of SMA America | 1.79 |  |  | 450 | 712 | 800 | 2.406 | 4.812 | 7.218 | 12.03 | 18.045 | 24.06 | 96.0825 | 97.4242 | 97.4447 | 97.3151 | 97.1222 | 96.8659 | 97.1621 | 97.4599 | 98.348 | 98.5031 | 98.5314 | 98.4351 | 98.2665 | 98.4117 | 96.9099 | 98.0049 | 98.1886 | 98.2041 | 98.0766 | 97.8823 | 98.0569 | 2017-09-01 | 2018-10-15
SunPower | SPR-30000m-3 [480V] | Sunny Tripower TL-US, 30kW, 480Vac 3-phase, Transformerless, Utility Interactive Inverter | 30.01 | 480 | 98 | Y | N | Multiple Listing of SMA America | 1.22 |  |  | 500 | 720 | 800 | 3.001 | 6.002 | 9.003 | 15.005 | 22.5075 | 30.01 | 96.588 | 97.716 | 97.926 | 97.98 | 97.838 | 97.622 | 97.8115 | 97.588 | 98.448 | 98.69 | 98.602 | 98.538 | 98.328 | 98.5167 | 97.026 | 98.06 | 98.452 | 98.386 | 98.282 | 98.08 | 98.2528 | 2017-09-01 | 2018-10-15
Sunset | SUNstring 4000 [240V] | 2.9 kW, 240 Vac, 125-400 Vdc Utility Interactive Inverter | 2.86 | 240 | 94 | Y | N |  | 2.77 |  |  | 100 | 175 | 300 | 0.29 | 0.57 | 0.86 | 1.43 | 2.15 | 2.86 | 91.1 | 94.1 | 94.5 | 94.7 | 94.1 | 93.3 | 94.1 | 90.5 | 93.7 | 94.3 | 94.5 | 93.8 | 93 | 93.8 | 90.6 | 93.2 | 94.3 | 93.9 | 93.2 | 92.5 | 93.4
Sunset | SUNstring 5000 [240V] | 3.6 kW, 240 Vac, 125-400 Vdc Utility Interactive Inverter | 3.6 | 240 | 93.5 | Y | N |  | 3.11 |  |  | 100 | 175 | 300 | 0.36 | 0.72 | 1.08 | 1.8 | 2.7 | 3.6 | 89.9 | 93.3 | 94.2 | 94.3 | 94 | 93.3 | 93.8 | 89.7 | 93.1 | 94.1 | 94.2 | 93.9 | 93.2 | 93.7 | 89 | 92.4 | 93.5 | 93.8 | 93.6 | 92.9 | 93.3
Sustainable Energy Technologies | SUNERGY ELV 208 [208V] | 5000 W, 208 Vac, Grid-Direct Solar PV Inverter | 5 | 208 | 94 | Y | N |  | 0.27 |  |  | 54 | 65 | 95 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 90.38 | 95.05 | 95.76 | 95.79 | 94.96 | 93.79 | 94.99 | 88.56 | 94 | 94.95 | 95.14 | 94.48 | 93.59 | 94.37 | 83.41 | 91.15 | 92.88 | 93.5 | 93.29 | 92.63 | 92.75
Sustainable Energy Technologies | SUNERGY LV 208 [208V] | 5000 W, 208 Vac, Grid-Direct Solar PV Inverter | 5 | 208 | 94.5 | Y | N |  | 0.25 | 5 | 0.03 | 70 | 85 | 130 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 90.4 | 94.7 | 95.6 | 95.8 | 95.2 | 94.4 | 95.1 | 88.8 | 93.9 | 95 | 95.3 | 94.9 | 94.2 | 94.7 | 84.4 | 91.4 | 93.2 | 93.9 | 94.1 | 93.4 | 93.4
Sustainable Energy Technologies | SUNERGY TENK 240D [240V] | 5000 W, 240 Vac, Grid-Direct Solar PV Inverter | 5 | 240 | 94.5 | Y | N |  | 0.19 |  |  | 50 | 63 | 95 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 92.29 | 95.48 | 96 | 95.96 | 95.21 | 94.16 | 95.31 | 90.15 | 94.4 | 95.25 | 95.3 | 94.9 | 93.89 | 94.76 | 85.05 | 91.96 | 93.38 | 93.99 | 93.89 | 93.13 | 93.36
Sustainable Energy Technologies | Sunergy 5000-70/240 [240V] | 5000 W, 240 Vac, Grid-Direct Solar PV Inverter | 5.009 | 240 | 95 | Y | N |  | 0.52 |  |  | 70 | 78 | 100 | 0.5 | 1 | 1.5 | 2.5 | 3.76 | 5.01 | 90.2 | 94.6 | 95.4 | 95.7 | 95.3 | 94.6 | 95.1 | 88.8 | 93.9 | 95 | 95.4 | 95.1 | 94.5 | 94.8 | 87.8 | 93.2 | 94.6 | 95 | 94.9 | 94.2 | 94.5
Sysgration | Soleil 2000-120 [120V] | 2000 W, 120Vac Utility Interactive Inverter | 2 | 120 | 91.5 | Y | N |  | 14.18 |  |  | 100 | 240 | 360 | 0.2 | 0.4 | 0.6 | 1 | 1.5 | 2 | 89 | 92.2 | 92.8 | 92.6 | 91.7 | 90.8 | 91.9 | 88.6 | 91.9 | 92.8 | 92.6 | 91.6 | 90.5 | 91.8 | 87.1 | 90.8 | 91.8 | 92.2 | 91.3 | 90.1 | 91.3
Sysgration | SG-4000 [240V] | 4000 W, 240 Vac, Utility Interactive Inverter | 4.03 | 240 | 95 | Y | N |  | 0.19 |  |  | 100 | 310 | 440 | 0.4 | 0.81 | 1.21 | 2.02 | 3.02 | 4.03 | 91.6 | 94.5 | 95.2 | 95.3 | 95 | 93.9 | 94.9 | 90.2 | 94.5 | 95.5 | 95.8 | 95.6 | 95 | 95.3 | 87.4 | 92.8 | 94 | 95 | 95.2 | 94.6 | 94.5
Tabuchi Electric Co., Ltd. | EHW-S55P3B-PNUS [240V] | 5346 W, 240 Vac, Utility Interactive Inverter | 5.346 | 240 | 91.5 | Y | N |  | 0.017 |  |  | 100 | 300 | 450 | 0.53 | 1.07 | 1.6 | 2.67 | 4.01 | 5.35 | 77.2 | 87 | 90 | 92.4 | 92.8 | 92.2 | 91.4 | 80.3 | 88.8 | 91.2 | 93 | 93.4 | 93.3 | 92.3 | 81.5 | 88.6 | 90.5 | 91.7 | 92.1 | 92.2 | 91.2 |  | 2017-12-15
Tabuchi Electric Co., Ltd. | EPW-T250P6-US [480V] | 24 kW, 480 Vac, transformerless Utility Interactive Inverter | 24.13 | 480 | 97.5 | Y | N |  | 7.127 |  |  | 500 | 700 | 800 | 2.41 | 4.83 | 7.24 | 12.07 | 18.1 | 24.13 | 93.8 | 96.9 | 97.7 | 97.2 | 97.2 | 97.1 | 97.1 | 94.3 | 96.6 | 98.1 | 98.5 | 98 | 97.4 | 97.9 | 94.1 | 96.5 | 97.9 | 97.4 | 97.6 | 98 | 97.4 |  | 2017-12-15
Tabuchi Electric Co., Ltd. | TPD-T250P6-US [480V] | 25 kW, 480 Vac, transformerless Utility Interactive Inverter | 24.895 | 480 | 97.5 | N | N |  | 7.129 |  |  | 500 | 700 | 800 | 2.49 | 4.98 | 7.47 | 12.45 | 18.67 | 24.9 | 93.9956 | 96.6194 | 98.2385 | 96.7456 | 98.0242 | 97.2681 | 97.5122 | 93.2322 | 96.6486 | 98.7005 | 97.6598 | 97.8204 | 97.7219 | 97.6452 | 92.8068 | 96.3838 | 98.097 | 96.976 | 97.4662 | 97.4504 | 97.1977 |  | 2017-12-15
Talesun Solar | TP660AM225 [240V] | 225 W, 240 Vac Inverter | 0.23 | 240 | 94.5 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.02 |  |  | 21 | 31.5 | 35 | 0.02 | 0.05 | 0.07 | 0.11 | 0.17 | 0.23 | 87 | 92 | 93.4 | 94.5 | 94.5 | 94.1 | 93.9 | 85.8 | 91.5 | 93.5 | 95.1 | 96.1 | 95.3 | 94.9 | 85.4 | 91.3 | 93.3 | 94.9 | 95.3 | 95.5 | 94.4
Talesun Solar | TP660AM240 [240V] | 240 W, 240 Vac Inverter | 0.24 | 240 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 33.5 | 42.5 | 46 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 89.1 | 93.6 | 94.7 | 95 | 95.1 | 94.8 | 94.7 | 88.6 | 93.5 | 94.7 | 95.3 | 95.6 | 94.8 | 95 | 88.1 | 93.3 | 94.7 | 95.3 | 95.7 | 95.7 | 95.1
Talesun Solar | TP660AM255 [240V] | 225 W, 240 Vac Inverter | 0.25 | 240 | 95.5 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.28 |  |  | 46 | 53.5 | 57 | 0.02 | 0.05 | 0.07 | 0.13 | 0.19 | 0.25 | 91.2 | 95.2 | 96 | 95.5 | 95.7 | 95.5 | 95.5 | 91.4 | 95.5 | 95.9 | 95.5 | 95.1 | 94.3 | 95.1 | 90.8 | 95.3 | 96.1 | 95.7 | 96.1 | 95.9 | 95.8
Talesun Solar | TP660AM270 [240V] | 241 W, 240 Vac Inverter | 0.26 | 240 | 96 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.41 |  |  | 58.5 | 64.5 | 68 | 0.02 | 0.05 | 0.07 | 0.14 | 0.2 | 0.26 | 93.3 | 96.8 | 97.3 | 96 | 96.3 | 96.2 | 96.3 | 94.2 | 97.5 | 97.1 | 95.7 | 94.6 | 93.8 | 95.2 | 93.5 | 97.3 | 97.5 | 96.1 | 96.5 | 96.1 | 96.5
TMEIC | PVL-L0500U | 500 kW Utility Interactive Inverter for medium voltage transformer | 500 |  | 95.5 | Y | N |  | 60 |  |  | 320 | 360 | 480 | 50 | 100 | 150 | 250 | 375 | 500 | 91.4 | 95.1 | 96 | 96.4 | 96 | 95.4 | 95.8 | 91 | 94.8 | 95.8 | 96.2 | 95.9 | 95.2 | 95.7 | 89.7 | 94.2 | 95.7 | 95.8 | 95.5 | 94.9 | 95.3
TMEIC | PVL-L0630U-S | 630 kW Utility Interactive Inverter for medium voltage transformer | 630 |  | 97 | Y | N |  | 53 |  |  | 550 | 615 | 800 | 63 | 126 | 189 | 315 | 472.5 | 630 | 94.2 | 96.9 | 97.3 | 97.8 | 97.4 | 96.9 | 97.3 | 94 | 96.8 | 97.2 | 97.7 | 97.3 | 96.8 | 97.2 | 93.2 | 96.5 | 96.9 | 97.6 | 97.2 | 96.6 | 97
TMEIC | PVL-L0833GR | 1.35 MW Utility Interactive Inverter for medium voltage transformer | 833 |  | 97.5 | Y | N |  | 78 |  |  | 605 | 655 | 800 | 83.3 | 166.6 | 249.9 | 416.5 | 624.75 | 833 | 95.4 | 97.4 | 97.9 | 98 | 97.8 | 97.5 | 97.7 | 95.1 | 97.3 | 97.8 | 97.9 | 97.7 | 97.3 | 97.6 | 94.6 | 97 | 97.5 | 97.7 | 97.5 | 97.1 | 97.4
TMEIC | PVH-L1350GR | 1.35 MW Utility Interactive Inverter for medium voltage transformer | 1350 |  | 97.5 | N | N |  | 106 |  |  | 875 | 960 | 1200 | 135 | 270 | 405 | 675 | 1012.5 | 1350 | 95.4133 | 97.4401 | 97.9838 | 98.1254 | 97.9325 | 97.5613 | 97.8352 | 95.0511 | 97.3945 | 97.881 | 98.0214 | 97.8127 | 97.4201 | 97.7137 | 94.5754 | 97.0141 | 97.6434 | 97.8014 | 97.6385 | 97.2585 | 97.5006
TMEIC | PVH-L1350GR-EG | 1.35 MW Utility Interactive Inverter for medium voltage transformer | 1350 |  | 97.5 | N | N |  | 106 |  |  | 875 | 960 | 1200 | 135 | 270 | 405 | 675 | 1012.5 | 1350 | 95.4133 | 97.4401 | 97.9838 | 98.1254 | 97.9325 | 97.5613 | 97.8352 | 95.0511 | 97.3945 | 97.881 | 98.0214 | 97.8127 | 97.4201 | 97.7137 | 94.5754 | 97.0141 | 97.6434 | 97.8014 | 97.6385 | 97.2585 | 97.5006
TMEIC | PVL-L1833GRQ | 1667 kW Utility Interactive Inverter for medium voltage transformer | 1667 |  | 97.5 | N | N |  | 100 |  |  | 605 | 655 | 800 | 166.7 | 333.4 | 500.1 | 833.5 | 1250 | 1667 | 96.2 | 97.8 | 98.1 | 98.1 | 97.9 | 97.3 | 97.8 | 96.1 | 97.7 | 98.1 | 98 | 97.7 | 97.2 | 97.7 | 96 | 97.6 | 97.9 | 97.9 | 97.5 | 97 | 97.6
TMEIC | PVL-L1833GRM | 1.833 MW Utility Interactive Inverter for medium voltage transformer | 1833 |  | 98 | N | N |  | 110 |  |  | 605 | 655 | 800 | 183.3 | 366.6 | 549.9 | 916.5 | 1374.75 | 1833 | 95.9 | 97.7 | 98.2 | 98.2 | 98 | 97.5 | 97.9 | 95.6 | 97.6 | 98 | 98.1 | 97.8 | 97.4 | 97.8 | 95.3 | 97.4 | 97.9 | 97.9 | 97.7 | 97.3 | 97.6
TMEIC | PVH-L2500GR | 2.5 MW Utility Interactive Inverter | 2500 |  | 97.5 | N | N |  | 235 |  |  | 800 | 900 | 1200 | 250 | 500 | 750 | 1250 | 1875 | 2500 | 95.9 | 97.6 | 97.9 | 98 | 97.8 | 97.4 | 97.8 | 95.6 | 97.5 | 97.8 | 97.9 | 97.7 | 97.2 | 97.6 | 95.2 | 97.2 | 97.6 | 97.7 | 97.5 | 97.1 | 97.4 |  | 2017-12-15
TMEIC | PVH-L2500GR-EG | 2.5 MW Utility Interactive Inverter | 2500 |  | 97.5 | N | N |  | 235 |  |  | 800 | 900 | 1200 | 250 | 500 | 750 | 1250 | 1875 | 2500 | 95.9 | 97.6 | 97.9 | 98 | 97.8 | 97.4 | 97.8 | 95.6 | 97.5 | 97.8 | 97.9 | 97.7 | 97.2 | 97.6 | 95.2 | 97.2 | 97.6 | 97.7 | 97.5 | 97.1 | 97.4 |  | 2017-12-15
TMEIC | PVH-L2700GR | 2.7 MW Utility Interactive Inverter | 2700 |  | 97.5 | N | N |  | 265 |  |  | 875 | 960 | 1200 | 270 | 540 | 810 | 1350 | 2025 | 2700 | 95.8 | 97.6 | 98 | 98 | 97.9 | 97.5 | 97.8 | 95.6 | 97.5 | 97.9 | 97.9 | 97.8 | 97.3 | 97.7 | 95.3 | 97.3 | 97.7 | 97.8 | 97.6 | 97.1 | 97.5 |  | 2017-12-15
TMEIC | PVH-L2700GR-EG | 2.7 MW Utility Interactive Inverter | 2700 |  | 97.5 | N | N |  | 265 |  |  | 875 | 960 | 1200 | 270 | 540 | 810 | 1350 | 2025 | 2700 | 95.8 | 97.6 | 98 | 98 | 97.9 | 97.5 | 97.8 | 95.6 | 97.5 | 97.9 | 97.9 | 97.8 | 97.3 | 97.7 | 95.3 | 97.3 | 97.7 | 97.8 | 97.6 | 97.1 | 97.5 |  | 2017-12-15
TMEIC | PVH-L3200GR [600V] | 3200 kW, rated 1500Vdc (Negative Ground), 600Vac Utility Interactive PV Inverter | 3127.43 | 600 | 98.5 | N | N | Efficiency data inclusive of transformer effect based on 3.2 MVA DOE 2016 Transformer Efficiency. | 49 |  |  | 875 | 1100 | 1200 | 312.74 | 625.49 | 938.23 | 1563.72 | 2345.57 | 3127.43 | 96.15 | 98.02 | 98.44 | 98.46 | 98.72 | 98.76 | 98.5 | 95.52 | 97.68 | 98.19 | 98.24 | 98.48 | 98.55 | 98.24 | 95.41 | 97.54 | 98.09 | 98.18 | 98.46 | 98.5 | 98.19 | 2018-04-16
TMEIC | PVH-L3200GR-E7 [600V] | 3200 kW, rated 1500Vdc (Negative Ground), 600Vac, 3.2MW output, compliant with NEC 2017 Utility Interactive PV Inverter | 3127.43 | 600 | 98.5 | N | N | Efficiency data inclusive of transformer effect based on 3.2 MVA DOE 2016 Transformer Efficiency. | 49 |  |  | 875 | 1100 | 1200 | 312.74 | 625.49 | 938.23 | 1563.72 | 2345.57 | 3127.43 | 96.15 | 98.02 | 98.44 | 98.46 | 98.72 | 98.76 | 98.5 | 95.52 | 97.68 | 98.19 | 98.24 | 98.48 | 98.55 | 98.24 | 95.41 | 97.54 | 98.09 | 98.18 | 98.46 | 98.5 | 98.19 | 2018-04-16
TMEIC | PVH-L3200GR-EG [600V] | 3200 kW, rated 1500Vdc (Negative Externally Grounded), 600Vac Utility Interactive PV Inverter | 3127.43 | 600 | 98.5 | N | N | Efficiency data inclusive of transformer effect based on 3.2 MVA DOE 2016 Transformer Efficiency. | 49 |  |  | 875 | 1100 | 1200 | 312.74 | 625.49 | 938.23 | 1563.72 | 2345.57 | 3127.43 | 96.15 | 98.02 | 98.44 | 98.46 | 98.72 | 98.76 | 98.5 | 95.52 | 97.68 | 98.19 | 98.24 | 98.48 | 98.55 | 98.24 | 95.41 | 97.54 | 98.09 | 98.18 | 98.46 | 98.5 | 98.19 | 2018-04-16
Topper Sun Energy Technology | TS-S1500 [208V] | 1.5 kW, 208 Vac Utility Interactive Inverter | 1.55 | 208 | 94.5 | Y | N |  | 0.21 |  |  | 100 | 325 | 360 | 0.155 | 0.31 | 0.465 | 0.775 | 1.163 | 1.55 | 84.46 | 90.49 | 92.52 | 94.25 | 94.92 | 95.02 | 93.86 | 85.04 | 91.04 | 93.19 | 94.79 | 95.41 | 95.53 | 94.38 | 85.31 | 91.19 | 93.54 | 95.02 | 95.55 | 95.76 | 94.58
Topper Sun Energy Technology | TS-S1500 [240V] | 1.5 kW, 240 Vac Utility Interactive Inverter | 1.55 | 240 | 94.5 | Y | N |  | 0.32 |  |  | 100 | 325 | 360 | 0.155 | 0.31 | 0.465 | 0.775 | 1.163 | 1.55 | 84.62 | 90.46 | 92.57 | 94.42 | 95.07 | 95.25 | 93.99 | 84.89 | 90.97 | 93.04 | 94.81 | 95.51 | 95.73 | 94.42 | 85.22 | 91.38 | 93.44 | 95.12 | 95.65 | 95.93 | 94.66
Topper Sun Energy Technology | TS-S2000 [208V] | 2 kW, 208 Vac Utility Interactive Inverter | 2.06 | 208 | 95.5 | Y | N |  | 0.29 |  |  | 100 | 325 | 360 | 0.206 | 0.412 | 0.618 | 1.03 | 1.545 | 2.06 | 88.28 | 93.12 | 94.41 | 95.27 | 95.43 | 95.37 | 94.87 | 89.63 | 93.68 | 94.91 | 95.73 | 95.84 | 95.8 | 95.34 | 89.74 | 94.01 | 95.11 | 96.13 | 96.38 | 96.07 | 95.77
Topper Sun Energy Technology | TS-S2000 [240V] | 2 kW, 240 Vac Utility Interactive Inverter | 2.06 | 240 | 95 | Y | N |  | 0.36 |  |  | 100 | 325 | 360 | 0.206 | 0.412 | 0.618 | 1.03 | 1.545 | 2.06 | 86.91 | 92.14 | 93.78 | 94.94 | 95.3 | 95.37 | 94.55 | 87.84 | 92.87 | 94.26 | 95.56 | 95.79 | 95.73 | 95.09 | 88.1 | 93.05 | 94.37 | 95.71 | 96 | 95.94 | 95.28
Topper Sun Energy Technology | TS-S3000 [208V] | 3 kW, 208 Vac Utility Interactive Inverter | 3 | 208 | 95.5 | Y | N |  | 0.18 |  |  | 100 | 325 | 360 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 91.57 | 94.41 | 95.16 | 95.47 | 95.31 | 94.62 | 95.1 | 92.05 | 94.92 | 95.58 | 95.89 | 95.76 | 95.37 | 95.56 | 92.22 | 95.17 | 95.79 | 96.25 | 95.93 | 95.8 | 95.78
Topper Sun Energy Technology | TS-S3000 [240V] | 3 kW, 240 Vac Utility Interactive Inverter | 3.01 | 240 | 95.5 | Y | N |  | 0.25 |  |  | 100 | 325 | 360 | 0.301 | 0.602 | 0.903 | 1.505 | 2.258 | 3.01 | 90 | 93.9 | 94.85 | 95.4 | 95.31 | 94.83 | 94.97 | 90.64 | 94.34 | 95.34 | 95.79 | 95.87 | 95.6 | 95.49 | 91 | 94.59 | 95.44 | 95.97 | 96.01 | 95.77 | 95.65
Topper Sun Energy Technology | TS-S4000 [208V] | 4 kW, 208 Vac Utility Interactive Inverter | 3.98 | 208 | 95.5 | Y | N |  | 0.18 |  |  | 100 | 325 | 360 | 0.398 | 0.796 | 1.194 | 1.99 | 2.985 | 3.98 | 90.53 | 94.32 | 95.17 | 95.44 | 95.41 | 95.16 | 95.13 | 91.58 | 94.87 | 95.63 | 96.05 | 96 | 95.45 | 95.7 | 91.82 | 95.03 | 95.8 | 96.45 | 96.31 | 95.76 | 96.01
Topper Sun Energy Technology | TS-S4000 [240V] | 4 kW, 240 Vac Utility Interactive Inverter | 3.99 | 240 | 96 | Y | N |  | 0.25 |  |  | 100 | 325 | 360 | 0.399 | 0.798 | 1.197 | 1.995 | 2.993 | 3.99 | 90.55 | 94.3 | 95.24 | 95.69 | 95.74 | 95.56 | 95.38 | 91.53 | 94.95 | 95.81 | 96.33 | 96.33 | 96.05 | 95.99 | 91.95 | 95.23 | 95.96 | 96.4 | 96.48 | 96.25 | 96.15
Toshiba International | PVT-AAA50K6U | 500 kW Utility Interactive Inverter for medium voltage transformer | 500 |  | 95.5 | Y | N |  | 60 |  |  | 320 | 360 | 480 | 50 | 100 | 150 | 250 | 375 | 500 | 91.4 | 95.1 | 96 | 96.4 | 96 | 95.4 | 95.8 | 91 | 94.8 | 95.8 | 96.2 | 95.9 | 95.2 | 95.7 | 89.7 | 94.2 | 95.7 | 95.8 | 95.5 | 94.9 | 95.3
Toshiba International | PVL-L0630U-S | 630 kW Utility Interactive Inverter for medium voltage transformer | 630 |  | 97 | Y | N |  | 53 |  |  | 550 | 615 | 800 | 63 | 126 | 189 | 315 | 472.5 | 630 | 94.2 | 96.9 | 97.3 | 97.8 | 97.4 | 96.9 | 97.3 | 94 | 96.8 | 97.2 | 97.7 | 97.3 | 96.8 | 97.2 | 93.2 | 96.5 | 96.9 | 97.6 | 97.2 | 96.6 | 97
Ubiquiti Networks International | SM-MI-250 [240V] | 250 W, 240 Vac Utility Interactive Inverter | 0.25 | 240 | 95.5 | N | Y |  | 0.12 |  |  | 28.7 | 30 | 31 | 0.03 | 0.05 | 0.13 | 0.13 | 0.19 | 0.25 | 94.8 | 95.7 | 95.8 | 95.7 | 95.4 | 95 | 95.5 | 94.8 | 95.7 | 95.8 | 95.7 | 95.4 | 95.2 | 95.5 | 94.7 | 95.6 | 95.8 | 95.7 | 95.4 | 95.2 | 95.5
Westinghouse Solar | WLW-230-1-AC1-A-B [240V] | 190 W, 240 Vac Inverter | 0.19 | 240 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.03 | 0.19 | 0.03 | 22 | 32.5 | 40 | 0.02 | 0.04 | 0.1 | 0.1 | 0.1 | 0.2 | 93.3 | 94.4 | 94.7 | 95.1 | 94.9 | 94.2 | 94.8 | 93.3 | 94.4 | 94.6 | 95.2 | 95.4 | 95.1 | 95.1 | 93.5 | 94.4 | 94.6 | 94.9 | 95.4 | 95.4 | 95.1
Westinghouse Solar | WLW-235-1-AC1-A-B [240V] | 190 W, 240 Vac Inverter | 0.19 | 240 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.03 | 0.19 | 0.03 | 22 | 32.5 | 40 | 0.02 | 0.04 | 0.1 | 0.1 | 0.1 | 0.2 | 93.3 | 94.4 | 94.7 | 95.1 | 94.9 | 94.2 | 94.8 | 93.3 | 94.4 | 94.6 | 95.2 | 95.4 | 95.1 | 95.1 | 93.5 | 94.4 | 94.6 | 94.9 | 95.4 | 95.4 | 95.1
Westinghouse Solar | WLW-235-1-AC3-B-B [240V] | 190 W, 240 Vac Inverter | 0.19 | 240 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.01 | 0.19 | 0.01 | 22 | 32 | 40 | 0.019 | 0.038 | 0.057 | 0.095 | 0.1425 | 0.19 | 93.6 | 94.6 | 94.9 | 95 | 94.6 | 93.7 | 94.6 | 93.4 | 94.6 | 94.7 | 95.2 | 95.2 | 94.8 | 95 | 93.4 | 94.4 | 94.8 | 95.1 | 95.3 | 95.1 | 95.1
Westinghouse Solar | WLW-240-1-AC1-A-B [240V] | 190 W, 240 Vac Inverter | 0.19 | 240 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.03 | 0.19 | 0.03 | 22 | 32.5 | 40 | 0.02 | 0.04 | 0.1 | 0.1 | 0.1 | 0.2 | 93.3 | 94.4 | 94.7 | 95.1 | 94.9 | 94.2 | 94.8 | 93.3 | 94.4 | 94.6 | 95.2 | 95.4 | 95.1 | 95.1 | 93.5 | 94.4 | 94.6 | 94.9 | 95.4 | 95.4 | 95.1
Westinghouse Solar | WLW-240-1-AC3-B-B [240V] | 190 W, 240 Vac Inverter | 0.19 | 240 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.01 | 0.19 | 0.01 | 22 | 32 | 40 | 0.019 | 0.038 | 0.057 | 0.095 | 0.1425 | 0.19 | 93.6 | 94.6 | 94.9 | 95 | 94.6 | 93.7 | 94.6 | 93.4 | 94.6 | 94.7 | 95.2 | 95.2 | 94.8 | 95 | 93.4 | 94.4 | 94.8 | 95.1 | 95.3 | 95.1 | 95.1
Westinghouse Solar | WS-175-1AC1-A-A [240V] | 190 W, 240 Vac Inverter | 0.19 | 240 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.03 | 0.19 | 0.03 | 22 | 32.5 | 40 | 0.02 | 0.04 | 0.1 | 0.1 | 0.1 | 0.2 | 93.3 | 94.4 | 94.7 | 95.1 | 94.9 | 94.2 | 94.8 | 93.3 | 94.4 | 94.6 | 95.2 | 95.4 | 95.1 | 95.1 | 93.5 | 94.4 | 94.6 | 94.9 | 95.4 | 95.4 | 95.1
Westinghouse Solar | WS-175-1AC3-B-A [240V] | 190 W, 240 Vac Inverter | 0.19 | 240 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.01 | 0.19 | 0.01 | 22 | 32 | 40 | 0.02 | 0.04 | 0.06 | 0.1 | 0.1 | 0.2 | 93.6 | 94.6 | 94.9 | 95 | 94.6 | 93.7 | 94.6 | 93.4 | 94.6 | 94.7 | 95.2 | 95.2 | 94.8 | 95 | 93.4 | 94.4 | 94.8 | 95.1 | 95.3 | 95.1 | 95.1
Westinghouse Solar | WS-185-1AC1-A-A [240V] | 190 W, 240 Vac Inverter | 0.19 | 240 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.03 | 0.19 | 0.03 | 22 | 32.5 | 40 | 0.02 | 0.04 | 0.1 | 0.1 | 0.1 | 0.2 | 93.3 | 94.4 | 94.7 | 95.1 | 94.9 | 94.2 | 94.8 | 93.3 | 94.4 | 94.6 | 95.2 | 95.4 | 95.1 | 95.1 | 93.5 | 94.4 | 94.6 | 94.9 | 95.4 | 95.4 | 95.1
Westinghouse Solar | WS-185-1AC1-A-B [240V] | 190 W, 240 Vac Inverter | 0.19 | 240 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.03 | 0.19 | 0.03 | 22 | 32.5 | 40 | 0.02 | 0.04 | 0.1 | 0.1 | 0.1 | 0.2 | 93.3 | 94.4 | 94.7 | 95.1 | 94.9 | 94.2 | 94.8 | 93.3 | 94.4 | 94.6 | 95.2 | 95.4 | 95.1 | 95.1 | 93.5 | 94.4 | 94.6 | 94.9 | 95.4 | 95.4 | 95.1
Westinghouse Solar | WS-185-1AC3-B-A [208V] | 190 W, 208 Vac Inverter | 0.19 | 208 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.01 | 0.19 | 0.01 | 22 | 32 | 40 | 0.02 | 0.04 | 0.06 | 0.1 | 0.1 | 0.2 | 93.6 | 94.6 | 94.9 | 95 | 94.6 | 93.7 | 94.6 | 93.4 | 94.6 | 94.7 | 95.2 | 95.2 | 94.8 | 95 | 93.4 | 94.4 | 94.8 | 95.1 | 95.3 | 95.1 | 95.1
Westinghouse Solar | WS-185-1AC3-B-B [208V] | 190 W, 208 Vac Inverter | 0.19 | 208 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.01 | 0.19 | 0.01 | 22 | 32 | 40 | 0.02 | 0.04 | 0.06 | 0.1 | 0.1 | 0.2 | 93.6 | 94.6 | 94.9 | 95 | 94.6 | 93.7 | 94.6 | 93.4 | 94.6 | 94.7 | 95.2 | 95.2 | 94.8 | 95 | 93.4 | 94.4 | 94.8 | 95.1 | 95.3 | 95.1 | 95.1
Westinghouse Solar | WS-190-1AC1-A-B [240V] | 190 W, 240 Vac Inverter | 0.19 | 240 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.03 | 0.19 | 0.03 | 22 | 32.5 | 40 | 0.02 | 0.04 | 0.1 | 0.1 | 0.1 | 0.2 | 93.3 | 94.4 | 94.7 | 95.1 | 94.9 | 94.2 | 94.8 | 93.3 | 94.4 | 94.6 | 95.2 | 95.4 | 95.1 | 95.1 | 93.5 | 94.4 | 94.6 | 94.9 | 95.4 | 95.4 | 95.1
Westinghouse Solar | WS-190-1AC3-B-B [240V] | 190 W, 240 Vac Inverter | 0.19 | 240 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.01 | 0.19 | 0.01 | 22 | 32 | 40 | 0.019 | 0.038 | 0.057 | 0.095 | 0.1425 | 0.19 | 93.6 | 94.6 | 94.9 | 95 | 94.6 | 93.7 | 94.6 | 93.4 | 94.6 | 94.7 | 95.2 | 95.2 | 94.8 | 95 | 93.4 | 94.4 | 94.8 | 95.1 | 95.3 | 95.1 | 95.1
Westinghouse Solar | WS-195-1AC1-A-B [240V] | 190 W, 240 Vac Inverter | 0.19 | 240 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.03 | 0.19 | 0.03 | 22 | 32.5 | 40 | 0.02 | 0.04 | 0.1 | 0.1 | 0.1 | 0.2 | 93.3 | 94.4 | 94.7 | 95.1 | 94.9 | 94.2 | 94.8 | 93.3 | 94.4 | 94.6 | 95.2 | 95.4 | 95.1 | 95.1 | 93.5 | 94.4 | 94.6 | 94.9 | 95.4 | 95.4 | 95.1
Westinghouse Solar | WS-195-1AC3-B-B [208V] | 190 W, 208 Vac Inverter | 0.19 | 208 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.01 | 0.19 | 0.01 | 22 | 32 | 40 | 0.019 | 0.038 | 0.057 | 0.095 | 0.1425 | 0.19 | 93.6 | 94.6 | 94.9 | 95 | 94.6 | 93.7 | 94.6 | 93.4 | 94.6 | 94.7 | 95.2 | 95.2 | 94.8 | 95 | 93.4 | 94.4 | 94.8 | 95.1 | 95.3 | 95.1 | 95.1
Westinghouse Solar | WLW-230-1-AC0-D-B [208V] | 215 W, 208 Vac Inverter | 0.215 | 208 | 96 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.04 | 0.215 | 0.04 | 22 | 29 | 36 | 0.02 | 0.04 | 0.06 | 0.11 | 0.16 | 0.22 | 94.5 | 95.5 | 95.9 | 96 | 95.5 | 94.7 | 95.6 | 94.5 | 95.5 | 95.9 | 96.1 | 96 | 95.5 | 95.9 | 94.4 | 95.4 | 95.7 | 96.1 | 96.1 | 95.8 | 95.9
Westinghouse Solar | WLW-230-1-AC0-D-B [240V] | 215 W, 240 Vac Inverter | 0.215 | 240 | 96 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.04 | 0.215 | 0.04 | 22 | 29 | 36 | 0.02 | 0.04 | 0.06 | 0.11 | 0.16 | 0.22 | 94.5 | 95.5 | 95.9 | 96 | 95.5 | 94.7 | 95.6 | 94.5 | 95.5 | 95.9 | 96.1 | 96 | 95.5 | 95.9 | 94.4 | 95.4 | 95.7 | 96.1 | 96.1 | 95.8 | 95.9
Westinghouse Solar | WLW-230-1-AC2-D-B [208V] | 215 W, 208 Vac Inverter | 0.215 | 208 | 96 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.04 | 0.215 | 0.04 | 22 | 29 | 36 | 0.02 | 0.04 | 0.06 | 0.11 | 0.16 | 0.22 | 94.5 | 95.5 | 95.9 | 96 | 95.5 | 94.7 | 95.6 | 94.5 | 95.5 | 95.9 | 96.1 | 96 | 95.5 | 95.9 | 94.4 | 95.4 | 95.7 | 96.1 | 96.1 | 95.8 | 95.9
Westinghouse Solar | WLW-230-1-AC2-D-B [240V] | 215 W, 240 Vac Inverter | 0.215 | 240 | 96 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.04 | 0.215 | 0.04 | 22 | 29 | 36 | 0.02 | 0.04 | 0.06 | 0.11 | 0.16 | 0.22 | 94.5 | 95.5 | 95.9 | 96 | 95.5 | 94.7 | 95.6 | 94.5 | 95.5 | 95.9 | 96.1 | 96 | 95.5 | 95.9 | 94.4 | 95.4 | 95.7 | 96.1 | 96.1 | 95.8 | 95.9
Westinghouse Solar | WLW-235-1-AC0-D-B [208V] | 215 W, 208 Vac Inverter | 0.215 | 208 | 96 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.04 | 0.215 | 0.04 | 22 | 29 | 36 | 0.02 | 0.04 | 0.06 | 0.11 | 0.16 | 0.22 | 94.5 | 95.5 | 95.9 | 96 | 95.5 | 94.7 | 95.6 | 94.5 | 95.5 | 95.9 | 96.1 | 96 | 95.5 | 95.9 | 94.4 | 95.4 | 95.7 | 96.1 | 96.1 | 95.8 | 95.9
Westinghouse Solar | WLW-235-1-AC0-D-B [240V] | 215 W, 240 Vac Inverter | 0.215 | 240 | 96 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.04 | 0.215 | 0.04 | 22 | 29 | 36 | 0.02 | 0.04 | 0.06 | 0.11 | 0.16 | 0.22 | 94.5 | 95.5 | 95.9 | 96 | 95.5 | 94.7 | 95.6 | 94.5 | 95.5 | 95.9 | 96.1 | 96 | 95.5 | 95.9 | 94.4 | 95.4 | 95.7 | 96.1 | 96.1 | 95.8 | 95.9
Westinghouse Solar | WLW-235-1-AC2-D-B [208V] | 215 W, 208 Vac Inverter | 0.215 | 208 | 96 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.04 | 0.215 | 0.04 | 22 | 29 | 36 | 0.02 | 0.04 | 0.06 | 0.11 | 0.16 | 0.22 | 94.5 | 95.5 | 95.9 | 96 | 95.5 | 94.7 | 95.6 | 94.5 | 95.5 | 95.9 | 96.1 | 96 | 95.5 | 95.9 | 94.4 | 95.4 | 95.7 | 96.1 | 96.1 | 95.8 | 95.9
Westinghouse Solar | WLW-235-1-AC2-D-B [240V] | 215 W, 240 Vac Inverter | 0.215 | 240 | 96 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.04 | 0.215 | 0.04 | 22 | 29 | 36 | 0.02 | 0.04 | 0.06 | 0.11 | 0.16 | 0.22 | 94.5 | 95.5 | 95.9 | 96 | 95.5 | 94.7 | 95.6 | 94.5 | 95.5 | 95.9 | 96.1 | 96 | 95.5 | 95.9 | 94.4 | 95.4 | 95.7 | 96.1 | 96.1 | 95.8 | 95.9
Westinghouse Solar | WLW-240-1-AC0-D-B [208V] | 215 W, 208 Vac Inverter | 0.215 | 208 | 96 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.04 | 0.215 | 0.04 | 22 | 29 | 36 | 0.02 | 0.04 | 0.06 | 0.11 | 0.16 | 0.22 | 94.5 | 95.5 | 95.9 | 96 | 95.5 | 94.7 | 95.6 | 94.5 | 95.5 | 95.9 | 96.1 | 96 | 95.5 | 95.9 | 94.4 | 95.4 | 95.7 | 96.1 | 96.1 | 95.8 | 95.9
Westinghouse Solar | WLW-240-1-AC0-D-B [240V] | 215 W, 240 Vac Inverter | 0.215 | 240 | 96 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.04 | 0.215 | 0.04 | 22 | 29 | 36 | 0.02 | 0.04 | 0.06 | 0.11 | 0.16 | 0.22 | 94.5 | 95.5 | 95.9 | 96 | 95.5 | 94.7 | 95.6 | 94.5 | 95.5 | 95.9 | 96.1 | 96 | 95.5 | 95.9 | 94.4 | 95.4 | 95.7 | 96.1 | 96.1 | 95.8 | 95.9
Westinghouse Solar | WLW-240-1-AC2-D-B [208V] | 215 W, 208 Vac Inverter | 0.215 | 208 | 96 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.04 | 0.215 | 0.04 | 22 | 29 | 36 | 0.02 | 0.04 | 0.06 | 0.11 | 0.16 | 0.22 | 94.5 | 95.5 | 95.9 | 96 | 95.5 | 94.7 | 95.6 | 94.5 | 95.5 | 95.9 | 96.1 | 96 | 95.5 | 95.9 | 94.4 | 95.4 | 95.7 | 96.1 | 96.1 | 95.8 | 95.9
Westinghouse Solar | WLW-240-1-AC2-D-B [240V] | 215 W, 240 Vac Inverter | 0.215 | 240 | 96 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.04 | 0.215 | 0.04 | 22 | 29 | 36 | 0.02 | 0.04 | 0.06 | 0.11 | 0.16 | 0.22 | 94.5 | 95.5 | 95.9 | 96 | 95.5 | 94.7 | 95.6 | 94.5 | 95.5 | 95.9 | 96.1 | 96 | 95.5 | 95.9 | 94.4 | 95.4 | 95.7 | 96.1 | 96.1 | 95.8 | 95.9
Westinghouse Solar | WTW-240-1-AC2-D-B [208V] | 215 W, 208 Vac Inverter | 0.215 | 208 | 96 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.04 |  |  | 22 | 29 | 36 | 0.02 | 0.04 | 0.06 | 0.11 | 0.16 | 0.22 | 94.5 | 95.5 | 95.9 | 96 | 95.5 | 94.7 | 95.6 | 94.5 | 95.5 | 95.9 | 96.1 | 96 | 95.5 | 95.9 | 94.4 | 95.4 | 95.7 | 96.1 | 96.1 | 95.8 | 95.9
Westinghouse Solar | WTW-240-1-AC2-D-B [240V] | 215 W, 240 Vac Inverter | 0.215 | 240 | 96 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.04 |  |  | 22 | 29 | 36 | 0.02 | 0.04 | 0.06 | 0.11 | 0.16 | 0.22 | 94.5 | 95.5 | 95.9 | 96 | 95.5 | 94.7 | 95.6 | 94.5 | 95.5 | 95.9 | 96.1 | 96 | 95.5 | 95.9 | 94.4 | 95.4 | 95.7 | 96.1 | 96.1 | 95.8 | 95.9
Westinghouse Solar | WTW-245-1-AC2-D-B [208V] | 215 W, 208 Vac Inverter | 0.215 | 208 | 96 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.04 |  |  | 22 | 29 | 36 | 0.02 | 0.04 | 0.06 | 0.11 | 0.16 | 0.22 | 94.5 | 95.5 | 95.9 | 96 | 95.5 | 94.7 | 95.6 | 94.5 | 95.5 | 95.9 | 96.1 | 96 | 95.5 | 95.9 | 94.4 | 95.4 | 95.7 | 96.1 | 96.1 | 95.8 | 95.9
Westinghouse Solar | WTW-245-1-AC2-D-B [240V] | 215 W, 240 Vac Inverter | 0.215 | 240 | 96 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.04 |  |  | 22 | 29 | 36 | 0.02 | 0.04 | 0.06 | 0.11 | 0.16 | 0.22 | 94.5 | 95.5 | 95.9 | 96 | 95.5 | 94.7 | 95.6 | 94.5 | 95.5 | 95.9 | 96.1 | 96 | 95.5 | 95.9 | 94.4 | 95.4 | 95.7 | 96.1 | 96.1 | 95.8 | 95.9
Westinghouse Solar | WTW-250-1-AC2-D-B [208V] | 215 W, 208 Vac Inverter | 0.215 | 208 | 96 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.04 |  |  | 22 | 29 | 36 | 0.02 | 0.04 | 0.06 | 0.11 | 0.16 | 0.22 | 94.5 | 95.5 | 95.9 | 96 | 95.5 | 94.7 | 95.6 | 94.5 | 95.5 | 95.9 | 96.1 | 96 | 95.5 | 95.9 | 94.4 | 95.4 | 95.7 | 96.1 | 96.1 | 95.8 | 95.9
Westinghouse Solar | WTW-250-1-AC2-D-B [240V] | 215 W, 240 Vac Inverter | 0.215 | 240 | 96 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.04 |  |  | 22 | 29 | 36 | 0.02 | 0.04 | 0.06 | 0.11 | 0.16 | 0.22 | 94.5 | 95.5 | 95.9 | 96 | 95.5 | 94.7 | 95.6 | 94.5 | 95.5 | 95.9 | 96.1 | 96 | 95.5 | 95.9 | 94.4 | 95.4 | 95.7 | 96.1 | 96.1 | 95.8 | 95.9
Xantrex Technology | GT2.5-NA-DS-240 [240V] | 2.5 kW, 240 Vac, 195-600 Vdc Grid Tie Inverter | 2.5 | 240 | 94 | Y | N |  | 1 | 2.5 | 1 | 100 | 266 | 480 | 0.25 | 0.5 | 0.75 | 1.25 | 1.88 | 2.5 | 88.5 | 92.7 | 94.1 | 94.8 | 94.8 | 94.5 | 94.4 | 87.7 | 92.3 | 93.7 | 94.5 | 94.6 | 94.4 | 94.1 | 86.3 | 90.9 | 92.6 | 93.8 | 94 | 93.8 | 93.3
Xantrex Technology | GT2.5-NA-DS-240-POS [240V] | 2.5 kW, 240 Vac, 195-600 Vdc Grid Tie Inverter (positive ground) | 2.5 | 240 | 94 | Y | N |  | 1 | 2.5 | 1 | 100 | 266 | 480 | 0.25 | 0.5 | 0.75 | 1.25 | 1.88 | 2.5 | 88.5 | 92.7 | 94.1 | 94.8 | 94.8 | 94.5 | 94.4 | 87.7 | 92.3 | 93.7 | 94.5 | 94.6 | 94.4 | 94.1 | 86.3 | 90.9 | 92.6 | 93.8 | 94 | 93.8 | 93.3
Xantrex Technology | GT2.8-NA-240/208 [208V] | 2.7 kW, 208 Vac, 195-600 Vdc Grid Tie Inverter | 2.7 | 208 | 93.5 | Y | N |  | 1 | 2.7 | 1 | 100 | 266 | 480 | 0.27 | 0.54 | 0.81 | 1.35 | 2.025 | 2.7 | 88.7 | 93.1 | 94.1 | 94.6 | 94.5 | 94 | 94.1 | 88 | 92.8 | 93.8 | 94.4 | 94.3 | 93.8 | 93.9 | 84.6 | 90.6 | 92.3 | 93.4 | 93.4 | 92.5 | 92.7
Xantrex Technology | GT2.8-NA-240/208 [240V] | 2.8 kW, 240 Vac, 195-600 Vdc Grid Tie Inverter | 2.8 | 240 | 94 | Y | N |  | 1.3 | 2.8 | 1.3 | 100 | 266 | 480 | 0.28 | 0.56 | 0.84 | 1.4 | 2.1 | 2.8 | 89.3 | 93.5 | 94.4 | 95 | 94.8 | 94.4 | 94.5 | 88.6 | 93.1 | 94.2 | 94.7 | 94.6 | 94.2 | 94.3 | 85.3 | 91 | 92.7 | 93.8 | 93.7 | 92.7 | 93.1
Xantrex Technology | GT3.0-NA-DS-240 [240V] | 3.0 kW, 240 Vac, 195-600 Vdc Grid Tie Inverter | 3 | 240 | 94.5 | Y | N |  | 1 | 3 | 1 | 100 | 266 | 480 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 90.2 | 93.7 | 94.6 | 95 | 95 | 94.6 | 94.7 | 89.5 | 93.7 | 94.5 | 95 | 95 | 94.6 | 94.6 | 88.7 | 92.6 | 94 | 94.6 | 94.6 | 94.3 | 94.2
Xantrex Technology | GT3.0-NA-DS-240-POS [240V] | 3.0 kW, 240 Vac, 195-600 Vdc Grid Tie Inverter (positive ground) | 3 | 240 | 94.5 | Y | N |  | 1 | 3 | 1 | 100 | 266 | 480 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 90.2 | 93.7 | 94.6 | 95 | 95 | 94.6 | 94.7 | 89.5 | 93.7 | 94.5 | 95 | 95 | 94.6 | 94.6 | 88.7 | 92.6 | 94 | 94.6 | 94.6 | 94.3 | 94.2
Xantrex Technology | GT3.3N-NA-240/208 [208V] | 3.1 kW, 208 Vac, 195-600 Vdc Grid Tie Inverter | 3.1 | 208 | 95 | Y | N |  | 1.24 | 3.1 | 1.24 | 100 | 250 | 400 | 0.31 | 0.62 | 0.93 | 1.55 | 2.325 | 3.1 | 91.4 | 94.7 | 95.4 | 95.6 | 95.5 | 95.1 | 95.3 | 90.9 | 94.4 | 95.2 | 95.6 | 95.4 | 95.1 | 95.2 | 89.3 | 93.4 | 94.5 | 95.2 | 95.2 | 94.9 | 94.7
Xantrex Technology | SW4048 [120V] | 4.0 kVA, 48 Vdc, 120 Vac, Trace Engr. batt bkp, sine wave Inverter (with GTI) | 3.211 | 120 | 90.5 | Y | N |  | 26.2 |  |  | 100 | 53.2 | 60 | 0.3211 | 0.6423 | 0.9634 | 1.606 | 2.408 | 3.211 | 92.7 | 94.3 | 94.1 | 92.2 | 88.5 | 85.5 | 90.3 | 92.8 | 93.7 | 93.6 | 91.8 | 89.1 | 84.8 | 90.4 | 91.1 | 92.9 | 93.1 | 91.2 | 89.3 | 85 | 90.2
Xantrex Technology | SW4024 [120V] | 4.0 kVA, 24 Vdc, 120 Vac, Trace Engr. batt bkp, sine wave Inverter (with GTI) | 3.297 | 120 | 89 | Y | N |  | 27.7 |  |  | 100 | 26.8 | 30 | 0.3297 | 0.6594 | 0.9891 | 1.649 | 2.473 | 3.297 | 92 | 93.6 | 93.3 | 90.9 | 88.4 | 83.7 | 89.7 | 91.3 | 93.1 | 93 | 91 | 87.5 | 83.1 | 89.1 | 88.9 | 92.3 | 92.4 | 90.7 | 87.1 | 83 | 88.6
Xantrex Technology | GT3.3-NA-DS-208 [208V] | 3.3 kW, 208 Vac, 195-600 Vdc Grid Tie Inverter | 3.3 | 208 | 94 | Y | N |  | 1 | 3.3 | 1 | 100 | 266 | 480 | 0.33 | 0.66 | 0.99 | 1.65 | 2.48 | 3.3 | 90.1 | 93.3 | 94.2 | 94.6 | 94.3 | 93.6 | 94.1 | 89.5 | 93.2 | 94.1 | 94.6 | 94.3 | 93.6 | 94.1 | 87.2 | 91.7 | 93.2 | 93.9 | 93.7 | 93.1 | 93.3
Xantrex Technology | GT3.3-NA-DS-208-POS [208V] | 3.3 kW, 208 Vac, 195-600 Vdc Grid Tie Inverter | 3.3 | 208 | 94 | Y | N |  | 1 | 3.3 | 1 | 100 | 266 | 480 | 0.33 | 0.66 | 0.99 | 1.65 | 2.48 | 3.3 | 90.1 | 93.3 | 94.2 | 94.6 | 94.3 | 93.6 | 94.1 | 89.5 | 93.2 | 94.1 | 94.6 | 94.3 | 93.6 | 94.1 | 87.2 | 91.7 | 93.2 | 93.9 | 93.7 | 93.1 | 93.3
Xantrex Technology | GT3.3-NA-DS-240 [240V] | 3.3 kW, 240 Vac, 195-600 Vdc Grid Tie Inverter | 3.3 | 240 | 94.5 | Y | N |  | 1 | 3.3 | 1 | 100 | 266 | 480 | 0.33 | 0.66 | 0.99 | 1.65 | 2.48 | 3.3 | 90.6 | 93.8 | 94.9 | 95.3 | 95.1 | 94.6 | 94.9 | 90.1 | 93.7 | 94.6 | 95.1 | 95 | 94.4 | 94.7 | 87.2 | 91.9 | 93.4 | 94.4 | 94.3 | 93.8 | 93.8
Xantrex Technology | GT3.3-NA-DS-240-POS [240V] | 3.3 kW, 240 Vac, 195-600 Vdc Grid Tie Inverter | 3.3 | 240 | 94.5 | Y | N |  | 1 | 3.3 | 1 | 100 | 266 | 480 | 0.33 | 0.66 | 0.99 | 1.65 | 2.48 | 3.3 | 90.6 | 93.8 | 94.9 | 95.3 | 95.1 | 94.6 | 94.9 | 90.1 | 93.7 | 94.6 | 95.1 | 95 | 94.4 | 94.7 | 87.2 | 91.9 | 93.4 | 94.4 | 94.3 | 93.8 | 93.8
Xantrex Technology | GT3.3N-NA-240/208 [240V] | 3.3 kW, 240 Vac, 195-600 Vdc Grid Tie Inverter | 3.3 | 240 | 95.5 | Y | N |  | 1.52 | 3.3 | 1.52 | 100 | 250 | 400 | 0.33 | 0.66 | 0.99 | 1.65 | 2.475 | 3.3 | 91.9 | 95 | 95.7 | 95.9 | 95.9 | 95.5 | 95.6 | 91.4 | 94.7 | 95.5 | 95.9 | 95.7 | 95.4 | 95.5 | 89.8 | 93.6 | 94.8 | 95.4 | 95.3 | 95.2 | 95
Xantrex Technology | GT3.8-NA-240/208 UL-05 [208V] | 3.5 kW, 208 Vac, 195-600 Vdc Grid Tie Inverter | 3.5 | 208 | 95 | Y | N |  | 1 | 3.5 | 1 | 100 | 266 | 480 | 0.35 | 0.7 | 1.05 | 1.75 | 2.63 | 3.5 | 91.8 | 94.9 | 95.5 | 95.6 | 95.2 | 94.7 | 95.15 | 91.3 | 94.6 | 95.3 | 95.5 | 95.1 | 94.6 | 94.98 | 90 | 93.6 | 94.6 | 95.1 | 94.7 | 94.3 | 94.49
Xantrex Technology | GT3.8-NA-240/208 UL-05 [240V] | 3.8 kW, 240 Vac, 195-600 Vdc Grid Tie Inverter | 3.8 | 240 | 95 | Y | N |  | 1 | 3.8 | 1 | 100 | 266 | 480 | 0.38 | 0.76 | 1.14 | 1.9 | 2.85 | 3.8 | 92.5 | 95.2 | 95.8 | 95.9 | 95.6 | 95 | 95.51 | 92 | 95 | 95.6 | 95.7 | 95.5 | 94.9 | 95.37 | 90.8 | 94.1 | 95 | 95.3 | 95 | 94.6 | 94.85
Xantrex Technology | GT3.8-NA-DS-240 [240V] | 3.8 kW, 240 Vac, 195-600 Vdc Grid Tie Inverter | 3.8 | 240 | 95 | Y | N |  | 1 | 3.8 | 1 | 100 | 266 | 480 | 0.38 | 0.76 | 1.14 | 1.9 | 2.85 | 3.8 | 93 | 95.2 | 95.7 | 95.7 | 95.4 | 94.5 | 95.3 | 92.3 | 95 | 95.5 | 95.6 | 95.3 | 94.6 | 95.2 | 91.2 | 94.2 | 94.8 | 95.1 | 95 | 94.3 | 94.7
Xantrex Technology | GT3.8-NA-DS-240-POS [240V] | 3.8 kW, 240 Vac, 195-600 Vdc Grid Tie Inverter (positive ground) | 3.8 | 240 | 95 | Y | N |  | 1 | 3.8 | 1 | 100 | 266 | 480 | 0.38 | 0.76 | 1.14 | 1.9 | 2.85 | 3.8 | 93 | 95.2 | 95.7 | 95.7 | 95.4 | 94.5 | 95.3 | 92.3 | 95 | 95.5 | 95.6 | 95.3 | 94.6 | 95.2 | 91.2 | 94.2 | 94.8 | 95.1 | 95 | 94.3 | 94.7
Xantrex Technology | GT4.0N-NA-240/208 [208V] | 3.8 kW, 208 Vac, 195-600 Vdc Grid Tie Inverter | 3.8 | 208 | 95 | Y | N |  | 0.99 | 3.8 | 0.99 | 100 | 300 | 480 | 0.38 | 0.76 | 1.14 | 1.9 | 2.85 | 3.8 | 91.7 | 94.8 | 95.5 | 95.7 | 95.4 | 95.1 | 95.3 | 91 | 94.6 | 95.3 | 95.6 | 95.4 | 94.9 | 95.2 | 90.2 | 93.6 | 94.7 | 95.1 | 95.1 | 94.7 | 94.7
Xantrex Technology | GT4.0N-NA-240/208 [240V] | 4.0 kW, 240 Vac, 195-600 Vdc Grid Tie Inverter | 4 | 240 | 95.5 | Y | N |  | 1.1 | 4 | 1.1 | 100 | 300 | 480 | 0.4 | 0.8 | 1.2 | 2 | 3 | 4 | 92.2 | 95.1 | 95.8 | 96 | 95.8 | 95.5 | 95.7 | 91.6 | 94.9 | 95.7 | 95.9 | 95.8 | 95.3 | 95.5 | 90.7 | 94.2 | 95 | 95.5 | 95.4 | 95.1 | 95.1
Xantrex Technology | SW5548 [120V] | 5.5 kVA, 48Vdc, 120Vac, Trace Engr. batt bkp, sine wave Inverter (with GTI) | 4.265 | 120 | 91 | Y | N |  | 34.1 |  |  | 100 | 53.2 | 60 | 0.4265 | 0.8529 | 1.279 | 2.132 | 3.198 | 4.265 | 92.9 | 94.7 | 94.4 | 92.2 | 90 | 87.1 | 91.2 | 92.1 | 94.2 | 94.2 | 92.3 | 89.6 | 86.2 | 90.9 | 90.1 | 93.4 | 93.6 | 92 | 89 | 86.4 | 90.3
Xantrex Technology | GT5.0-NA-240/208 [208V] | 5.0 kW, 208 Vac, 195-600 Vdc Grid Tie Inverter | 4.5 | 208 | 95 | Y | N |  | 1 | 4.5 | 1 | 100 | 300 | 480 | 0.45 | 0.9 | 1.35 | 2.25 | 3.375 | 4.5 | 92.1 | 94.9 | 95.5 | 95.5 | 94.9 | 94.3 | 95 | 91.8 | 94.7 | 95.3 | 95.4 | 94.9 | 94.3 | 94.9 | 90.5 | 93.9 | 94.6 | 95 | 94.7 | 94.2 | 94.5
Xantrex Technology | GT5.0-NA-240/208 [240V] | 5.0 kW, 240 Vac, 195-600 Vdc Grid Tie Inverter | 5 | 240 | 95.5 | Y | N |  | 1 | 5 | 1 | 100 | 300 | 480 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 93.2 | 95.5 | 95.9 | 95.9 | 95.5 | 94.8 | 95.5 | 92.7 | 95.3 | 95.8 | 95.8 | 95.4 | 94.8 | 95.4 | 91.5 | 94.6 | 95.3 | 95.4 | 95.1 | 94.5 | 95
Xantrex Technology | GT5.0-NA-DS-240 [240V] | 5.0 kW, 240 Vac, 195-600 Vdc Grid Tie Inverter | 5 | 240 | 95.5 | Y | N |  | 1 | 5 | 1 | 100 | 300 | 480 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 93.6 | 95.7 | 96 | 96.1 | 95.5 | 94.8 | 95.6 | 93.2 | 95.6 | 95.9 | 95.9 | 95.5 | 94.8 | 95.5 | 92.3 | 94.8 | 95.5 | 95.6 | 95.2 | 94.6 | 95.2
Xantrex Technology | PV10-208 [208V] | 10 kW, 208 Vac, 3-phase Utility Interactive Inverter with 208 Vac Transformer | 10.19 | 208 | 90 | Y | N |  | 203.3 |  |  | 330 | 368 | 480 | 1.02 | 2.04 | 3.06 | 5.1 | 7.64 | 10.19 | 78.5 | 86.5 | 89.2 | 91.8 | 92.8 | 92.9 | 91.3 | 77 | 84.7 | 88.3 | 91.1 | 91.7 | 92.3 | 90.3 | 73 | 82.9 | 86.8 | 89.4 | 90.7 | 90.7 | 88.9
Xantrex Technology | PV10-480 [208V] | 10 kW, 208 Vac, 3-phase Utility Interactive Inverter with 480 Vac Transformer | 10.24 | 208 | 92 | Y | N |  | 114.2 |  |  | 330 | 368 | 480 | 1.02 | 2.05 | 3.07 | 5.12 | 7.68 | 10.24 | 83.3 | 89.6 | 91.9 | 93.5 | 94 | 93.9 | 93 | 82 | 88.8 | 91.2 | 92.8 | 93.4 | 93.3 | 92.3 | 79.4 | 86.1 | 89.1 | 91.1 | 91.9 | 91.7 | 90.6
Xantrex Technology | PV15-480 [208V] | 15 kW, 208 Vac, 3-phase Utility Interactive Inverter with 480 Vac Transformer | 15.28 | 208 | 91.5 | Y | N |  | 171.6 |  |  | 330 | 368 | 480 | 1.53 | 3.06 | 4.58 | 7.64 | 11.46 | 15.28 | 79.3 | 89.3 | 91.5 | 93.2 | 93.7 | 93.6 | 92.5 | 78 | 88 | 90.6 | 92.3 | 92.9 | 92.7 | 91.6 | 74.1 | 85.6 | 88.7 | 90.6 | 91.6 | 90.7 | 90
Xantrex Technology | PV15-208 [208V] | 15 kW, 208 Vac, 3-phase Utility Interactive Inverter with 208 Vac Transformer | 15.31 | 208 | 91.5 | Y | N |  | 165.2 |  |  | 330 | 368 | 480 | 1.53 | 3.06 | 4.59 | 7.66 | 11.49 | 15.31 | 83.3 | 89.7 | 91.6 | 93.4 | 93.8 | 93.8 | 92.8 | 81.7 | 88 | 90.8 | 92.4 | 93.2 | 92.9 | 92 | 78.3 | 85.5 | 88.7 | 90.6 | 91.7 | 90.9 | 90.2
Xantrex Technology | PV20-480 [208V] | 20 kW, 208 Vac, 3-phase Utility Interactive Inverter with 480 Vac Transformer | 20.32 | 208 | 92 | Y | N |  | 203.3 |  |  | 330 | 368 | 480 | 2.03 | 4.06 | 6.1 | 10.16 | 15.24 | 20.32 | 85.1 | 90.7 | 92.6 | 93.5 | 93.8 | 93.7 | 93.1 | 84.4 | 89.6 | 91.7 | 93.4 | 93.5 | 92.9 | 92.7 | 81.9 | 87.6 | 90 | 91.3 | 91.7 | 90.5 | 90.8
Xantrex Technology | PV20-208 [208V] | 20 kW, 208 Vac, 3-phase Utility Interactive Inverter with 208 Vac Transformer | 20.49 | 208 | 92 | Y | N |  | 210.6 |  |  | 330 | 368 | 480 | 2.05 | 4.1 | 6.15 | 10.25 | 15.37 | 20.49 | 84.7 | 90.3 | 92.3 | 93.8 | 94 | 93.8 | 93.2 | 83.9 | 89.7 | 91.6 | 93.1 | 93.4 | 93 | 92.5 | 81.3 | 87.1 | 89.9 | 91.3 | 91.7 | 90.7 | 90.7
Xantrex Technology | PV30-480 [208V] | 30 kW, 208 Vac, 3-phase Utility Interactive Inverter with 480 Vac Transformer | 29.97 | 208 | 92 | Y | N |  | 454.8 |  |  | 330 | 368 | 480 | 3 | 5.99 | 8.99 | 14.99 | 22.48 | 29.97 | 83.1 | 89.8 | 91.9 | 93.3 | 93.5 | 93.5 | 92.7 | 82.1 | 89.6 | 91.2 | 92.9 | 93.3 | 93.1 | 92.3 | 80 | 87.2 | 89.9 | 91.2 | 92.3 | 91.8 | 91
Xantrex Technology | PV30-208 [208V] | 30 kW, 208 Vac, 3-phase Utility Interactive Inverter with 208 Vac Transformer | 30.29 | 208 | 92 | Y | N |  | 415 |  |  | 330 | 368 | 480 | 3.03 | 6.06 | 9.09 | 15.15 | 22.72 | 30.29 | 83.9 | 89.9 | 91.8 | 93.3 | 93.9 | 93.8 | 92.9 | 83 | 88.8 | 91 | 92.5 | 93.5 | 93.2 | 92.3 | 79.9 | 86.4 | 89.2 | 91.1 | 92.5 | 92 | 91
Xantrex Technology | PV45-480 [208V] | 45 kW, 208 Vac, 3-phase Utility Interactive Inverter with 480 Vac Transformer | 45.21 | 208 | 92 | Y | N |  | 595.6 |  |  | 330 | 368 | 480 | 4.52 | 9.04 | 13.56 | 22.6 | 33.91 | 45.21 | 83.3 | 89.6 | 91.7 | 93.1 | 93.4 | 93.1 | 92.5 | 83.1 | 89.2 | 91.2 | 92.6 | 92.8 | 92.6 | 92 | 81.2 | 87.8 | 90 | 91.6 | 92 | 91.2 | 91
Xantrex Technology | PV45-208 [208V] | 45 kW, 208 Vac, 3-phase Utility Interactive Inverter with 208 Vac Transformer | 45.35 | 208 | 92.5 | Y | N |  | 489 |  |  | 330 | 368 | 480 | 4.53 | 9.07 | 13.6 | 22.67 | 34.01 | 45.35 | 85 | 90.7 | 92.5 | 93.8 | 94.1 | 93.8 | 93.3 | 84.4 | 90.3 | 91.9 | 93.3 | 93.6 | 93.6 | 92.8 | 83.1 | 88.9 | 91 | 92.3 | 92.6 | 92.1 | 91.7
Xantrex Technology | PV100S-480 [480V] | 100 kW 480 Vac, 330-600 Vdc Inverter System with Automatic Transformer Disconnect | 100.3 | 480 | 93 | Y | N |  | 94.6 |  |  | 330 | 368 | 480 | 10.03 | 20.06 | 30.09 | 50.15 | 75.22 | 100.3 | 85.1 | 90.6 | 92.6 | 93.9 | 94.1 | 93.7 | 93.3 | 84.9 | 90.3 | 92.4 | 93.8 | 93.8 | 93.4 | 93.1 | 83.4 | 89 | 91.2 | 92.6 | 92.8 | 92.3 | 92
Xantrex Technology | PV100S-208 [208V] | 100 kW 208 Vac, 330-600 Vdc Inverter System with Automatic Transformer Disconnect | 101 | 208 | 92.5 | Y | N |  | 86.6 |  |  | 330 | 368 | 480 | 10.1 | 20.21 | 30.31 | 50.52 | 75.78 | 101 | 84.3 | 90.4 | 92.6 | 93.8 | 94 | 93.8 | 93.2 | 84.5 | 90.3 | 92.4 | 93.6 | 93.8 | 93.6 | 93 | 83 | 88.9 | 91.2 | 92.4 | 92.7 | 92.3 | 91.9
Xantrex Technology | PV100S-480-HE [480V] | 100 kW 480 Vac, 330-600 Vdc Inverter System with Automatic Transformer Disconnect | 101.1 | 480 | 95 | Y | N |  | 96 |  |  | 300 | 345 | 480 | 10.11 | 20.22 | 30.33 | 50.56 | 75.83 | 101.1 | 89.4 | 93.4 | 94.8 | 95.7 | 95.8 | 95.6 | 95.3 | 88.7 | 93 | 94.4 | 95.3 | 95.5 | 95.3 | 94.9 | 87.3 | 91.9 | 93.5 | 94.5 | 94.8 | 94.6 | 94.1
Xantrex Technology | PV100S-208-HE [208V] | 100 kW 208 Vac, 330-600 Vdc Inverter System with Automatic Transformer Disconnect | 101.3 | 208 | 94.5 | Y | N |  | 100 |  |  | 300 | 345 | 480 | 10.13 | 20.26 | 30.39 | 50.65 | 75.97 | 101.3 | 89.6 | 93.4 | 94.8 | 95.6 | 95.7 | 95.2 | 95.2 | 88 | 93 | 94.4 | 95.2 | 95.3 | 95.1 | 94.8 | 87.4 | 91.8 | 93.4 | 94.5 | 94.7 | 94.4 | 94
Xantrex Technology | PV225S-480-P [480V] | 225 kW 480 Vac, 330-600 Vdc Inverter System with Automatic Transformer Disconnect | 225.3 | 480 | 94.5 | Y | N |  | 107 |  |  | 300 | 345 | 480 | 22.53 | 45.05 | 67.58 | 112.6 | 169 | 225.3 | 89.4 | 93.7 | 94.8 | 95.4 | 95.3 | 95.1 | 94.9 | 88.5 | 93.2 | 94.4 | 95 | 95 | 94.8 | 94.6 | 87.2 | 92.1 | 93.4 | 94.3 | 94.3 | 93.9 | 93.8
Xantrex Technology | PV225S-480 [480V] | 225 kW 480 Vac, 330-600 Vdc Inverter System with Automatic Transformer Disconnect | 227.3 | 480 | 93.5 | Y | N |  | 103.8 |  |  | 330 | 368 | 480 | 22.73 | 45.46 | 68.19 | 113.7 | 170.5 | 227.3 | 88.5 | 92.7 | 94.1 | 94.9 | 94.9 | 94.6 | 94.4 | 87.4 | 92.1 | 93.6 | 94.7 | 94.5 | 94 | 94 | 84.5 | 89.7 | 91.5 | 92.6 | 92.6 | 92.5 | 92
Xslent Energy Technologies | XPX A1000 [120V] | 180 W, 120 Vac, 1-phase Utility Interactive Smart Grid Inverter | 0.18 | 120 | 89 | N | Y |  | 0.32 |  |  | 21 | 28 | 35 | 0.018 | 0.036 | 0.054 | 0.09 | 0.135 | 0.18 | 75.77 | 83.35 | 87.45 | 90.25 | 90.79 | 90.95 | 89.31 | 76.24 | 84.34 | 86.22 | 89.87 | 91.11 | 91.23 | 89.34 | 71.27 | 81.84 | 86.44 | 89.15 | 90.88 | 91.27 | 88.77
Yaskawa Solectria Solar | PVI 1800-208 [208V] | 1800 W, 208 Vac Grid-Tied Solar PV Inverter | 1.8 | 208 | 92.5 | Y | N | Formerly "Solectria Renewables, LLC" | 0.26 | 1.8 | 0.26 | 100 | 290 | 320 | 0.18 | 0.36 | 0.54 | 0.9 | 1.35 | 1.8 | 83.5 | 90 | 91.6 | 92.5 | 92.8 | 92.4 | 92 | 84 | 91.4 | 91.6 | 93.1 | 93.4 | 93.5 | 92.6 | 84.8 | 90.4 | 92.1 | 93.4 | 93.6 | 93.5 | 92.8 |  | 2018-02-15
Yaskawa Solectria Solar | PVI 1800-240 [240V] | 1800 W, 240 Vac Grid-Tied Solar PV Inverter | 1.8 | 240 | 92.5 | Y | N | Formerly "Solectria Renewables, LLC" | 0.14 | 1.8 | 0.14 | 100 | 290 | 320 | 0.18 | 0.36 | 0.54 | 0.9 | 1.35 | 1.8 | 83.6 | 89.6 | 91.2 | 92.3 | 92.6 | 92.3 | 91.8 | 84.1 | 90.1 | 91.8 | 93.2 | 93.4 | 93.2 | 92.6 | 85 | 90.1 | 92.2 | 93.3 | 93.5 | 93.3 | 92.8 |  | 2018-02-15
Yaskawa Solectria Solar | PVI 2500-208 [208V] | 2500 W, 208 Vac Grid-Tied Solar PV Inverter | 2.5 | 208 | 92 | Y | N | Formerly "Solectria Renewables, LLC" | 0.1 | 2.5 | 0.1 | 100 | 290 | 320 | 0.25 | 0.5 | 0.75 | 1.25 | 1.88 | 2.5 | 85.3 | 90.2 | 91.6 | 92.1 | 91.8 | 90.8 | 91.4 | 86.7 | 90.7 | 92.3 | 92.7 | 92.6 | 92.1 | 92.2 | 86.6 | 91 | 92.4 | 93 | 92.5 | 92 | 92.3 |  | 2018-02-15
Yaskawa Solectria Solar | PVI 2500-240 [240V] | 2500 W, 240 Vac Grid-Tied Solar PV Inverter | 2.5 | 240 | 93 | Y | N | Formerly "Solectria Renewables, LLC" | 0.32 | 2.5 | 0.32 | 100 | 290 | 320 | 0.25 | 0.5 | 0.75 | 1.25 | 1.88 | 2.5 | 86.5 | 91.2 | 92.7 | 93.1 | 92.6 | 91.7 | 92.4 | 86.8 | 91.7 | 93.1 | 93.7 | 93.6 | 92.9 | 93.2 | 87.6 | 92.1 | 93.3 | 93.8 | 93.6 | 93 | 93.3 |  | 2018-02-15
Yaskawa Solectria Solar | PVI 3000-208 [208V] | 2.7 kW, 208 Vac Utility Interactive Inverter | 2.7 | 208 | 95.5 | Y | N | Formerly "Solectria Renewables, LLC" | 0.5 |  |  | 100 | 250 | 400 | 0.27 | 0.54 | 0.81 | 1.35 | 2.03 | 2.7 | 90.7 | 94.5 | 95.8 | 96.4 | 96.3 | 95.9 | 95.9 | 89.8 | 94.1 | 95.5 | 96.2 | 96.2 | 95.8 | 95.7 | 88.2 | 92.5 | 94.3 | 95.5 | 95.6 | 95.3 | 94.9 |  | 2018-02-15
Yaskawa Solectria Solar | PVI 3000-POS-208 [208V] | 2.7 kW, 208 Vac Utility Interactive Inverter | 2.7 | 208 | 95.5 | Y | N | Formerly "Solectria Renewables, LLC" | 0.5 |  |  | 100 | 250 | 400 | 0.27 | 0.54 | 0.81 | 1.35 | 2.03 | 2.7 | 90.7 | 94.5 | 95.8 | 96.4 | 96.3 | 95.9 | 95.9 | 89.8 | 94.1 | 95.5 | 96.2 | 96.2 | 95.8 | 95.7 | 88.2 | 92.5 | 94.3 | 95.5 | 95.6 | 95.3 | 94.9 |  | 2018-02-15
Yaskawa Solectria Solar | PVI 3000S [208V] | 2.8 kW, 208 Vac Utility Interactive Inverter | 2.81 | 208 | 95.5 | Y | N | Formerly "Solectria Renewables, LLC" | 0.35 |  |  | 100 | 275 | 400 | 0.28 | 0.56 | 0.84 | 1.41 | 2.11 | 2.81 | 89.4 | 94.4 | 95.5 | 96.2 | 96.2 | 95.9 | 95.8 | 88.7 | 93.8 | 95.2 | 95.9 | 96 | 95.7 | 95.5 | 86.5 | 92.1 | 94 | 95.1 | 95.3 | 95.2 | 94.6 |  | 2018-02-15
Yaskawa Solectria Solar | PVI 3000S-P [208V] | 2.8 kW, 208 Vac Utility Interactive Inverter | 2.81 | 208 | 95.5 | Y | N | Formerly "Solectria Renewables, LLC" | 0.35 |  |  | 100 | 275 | 400 | 0.28 | 0.56 | 0.84 | 1.41 | 2.11 | 2.81 | 89.4 | 94.4 | 95.5 | 96.2 | 96.2 | 95.9 | 95.8 | 88.7 | 93.8 | 95.2 | 95.9 | 96 | 95.7 | 95.5 | 86.5 | 92.1 | 94 | 95.1 | 95.3 | 95.2 | 94.6 |  | 2018-02-15
Yaskawa Solectria Solar | PVI 3000-240 [240V] | 3 kW, 240 Vac Utility Interactive Inverter | 2.9 | 240 | 96 | Y | N | Formerly "Solectria Renewables, LLC" | 0.5 |  |  | 100 | 250 | 400 | 0.29 | 0.58 | 0.87 | 1.45 | 2.18 | 2.9 | 91.9 | 95.1 | 96.2 | 96.7 | 96.5 | 96.1 | 96.3 | 91.3 | 94.7 | 95.9 | 96.5 | 96.4 | 96 | 96.1 | 89.3 | 93.3 | 94.8 | 95.8 | 95.8 | 95.4 | 95.3 |  | 2018-02-15
Yaskawa Solectria Solar | PVI 3000-POS-240 [240V] | 3 kW, 240 Vac Utility Interactive Inverter | 2.9 | 240 | 96 | Y | N | Formerly "Solectria Renewables, LLC" | 0.5 |  |  | 100 | 250 | 400 | 0.29 | 0.58 | 0.87 | 1.45 | 2.18 | 2.9 | 91.9 | 95.1 | 96.2 | 96.7 | 96.5 | 96.1 | 96.3 | 91.3 | 94.7 | 95.9 | 96.5 | 96.4 | 96 | 96.1 | 89.3 | 93.3 | 94.8 | 95.8 | 95.8 | 95.4 | 95.3 |  | 2018-02-15
Yaskawa Solectria Solar | PVI 3000S [240V] | 2.7 kW, 240 Vac Utility Interactive Inverter | 3.01 | 240 | 96 | Y | N | Formerly "Solectria Renewables, LLC" | 0.47 |  |  | 100 | 275 | 400 | 0.3 | 0.6 | 0.9 | 1.51 | 2.26 | 3.01 | 90.6 | 95 | 96 | 96.6 | 96.6 | 96.2 | 96.2 | 89.8 | 94.4 | 95.6 | 96.4 | 96.4 | 96 | 95.9 | 87.7 | 92.9 | 94.5 | 95.6 | 95.8 | 95.5 | 95.1 |  | 2018-02-15
Yaskawa Solectria Solar | PVI 3000S-P [240V] | 2.9 kW, 240 Vac Utility Interactive Inverter | 3.01 | 240 | 96 | Y | N | Formerly "Solectria Renewables, LLC" | 0.47 |  |  | 100 | 275 | 400 | 0.3 | 0.6 | 0.9 | 1.51 | 2.26 | 3.01 | 90.6 | 95 | 96 | 96.6 | 96.6 | 96.2 | 96.2 | 89.8 | 94.4 | 95.6 | 96.4 | 96.4 | 96 | 95.9 | 87.7 | 92.9 | 94.5 | 95.6 | 95.8 | 95.5 | 95.1 |  | 2018-02-15
Yaskawa Solectria Solar | PVI 3800TL [208V] | 3.8 kW, non-isolated PV Inverter | 3.32 | 208 | 97.5 | Y | N | Formerly "Solectria Renewables, LLC" | 1.14 |  |  | 100 | 380 | 500 | 0.33 | 0.66 | 1 | 1.66 | 2.49 | 3.32 | 94.6 | 96.1 | 97 | 97.3 | 97.1 | 96.8 | 97 | 96.3 | 96.9 | 97.8 | 97.9 | 98.1 | 97.5 | 97.8 | 95.9 | 95.8 | 96.9 | 97.4 | 97.4 | 97.1 | 97.2 |  | 2018-02-15
Yaskawa Solectria Solar | PVI 4000-208 [208V] | 3.4 kW, 208 Vac Utility Interactive Inverter | 3.4 | 208 | 95.5 | Y | N | Formerly "Solectria Renewables, LLC" | 0.5 |  |  | 100 | 250 | 400 | 0.34 | 0.68 | 1.02 | 1.7 | 2.55 | 3.4 | 92.4 | 95.4 | 96.3 | 96.5 | 96.1 | 95.3 | 96 | 91.8 | 95.1 | 96 | 96.3 | 96 | 95.2 | 95.8 | 90.1 | 93.8 | 95.1 | 95.7 | 95.5 | 94.9 | 95.2 |  | 2018-02-15
Yaskawa Solectria Solar | PVI 4000-POS-208 [208V] | 3.4 kW, 208 Vac Utility Interactive Inverter | 3.4 | 208 | 95.5 | Y | N | Formerly "Solectria Renewables, LLC" | 0.5 |  |  | 100 | 250 | 400 | 0.34 | 0.68 | 1.02 | 1.7 | 2.55 | 3.4 | 92.4 | 95.4 | 96.3 | 96.5 | 96.1 | 95.3 | 96 | 91.8 | 95.1 | 96 | 96.3 | 96 | 95.2 | 95.8 | 90.1 | 93.8 | 95.1 | 95.7 | 95.5 | 94.9 | 95.2 |  | 2018-02-15
Yaskawa Solectria Solar | PVI 4000S [208V] | 3.4 kW, 208 Vac Utility Interactive Inverter | 3.51 | 208 | 95.5 | Y | N | Formerly "Solectria Renewables, LLC" | 0.35 |  |  | 100 | 275 | 400 | 0.35 | 0.7 | 1.05 | 1.76 | 2.63 | 3.51 | 91.3 | 95.1 | 96 | 96.3 | 96.1 | 95.4 | 95.9 | 90.4 | 94.7 | 95.7 | 96 | 95.9 | 95.3 | 95.6 | 88.4 | 93.3 | 94.7 | 95.3 | 95.3 | 94.7 | 94.8 |  | 2018-02-15
Yaskawa Solectria Solar | PVI 4000S-P [208V] | 3.5 kW, 208 Vac Utility Interactive Inverter | 3.51 | 208 | 95.5 | Y | N | Formerly "Solectria Renewables, LLC" | 0.35 |  |  | 100 | 275 | 400 | 0.35 | 0.7 | 1.05 | 1.76 | 2.63 | 3.51 | 91.3 | 95.1 | 96 | 96.3 | 96.1 | 95.4 | 95.9 | 90.4 | 94.7 | 95.7 | 96 | 95.9 | 95.3 | 95.6 | 88.4 | 93.3 | 94.7 | 95.3 | 95.3 | 94.7 | 94.8 |  | 2018-02-15
Yaskawa Solectria Solar | PVI 3800TL [240V] | 3.8 kW, non-isolated PV Inverter | 3.81 | 240 | 97.5 | Y | N | Formerly "Solectria Renewables, LLC" | 1.19 |  |  | 100 | 380 | 500 | 0.38 | 0.76 | 1.14 | 1.91 | 2.86 | 3.81 | 94.1 | 95.9 | 96.9 | 97.3 | 97.2 | 96.8 | 97 | 95.5 | 96.9 | 98 | 98.3 | 98.1 | 98 | 98 | 94.6 | 95.6 | 97.3 | 97.8 | 97.8 | 97.6 | 97.5 |  | 2018-02-15
Yaskawa Solectria Solar | PVI 4000-240 [240V] | 3.9 kW, 240 Vac Utility Interactive Inverter | 3.9 | 240 | 96 | Y | N | Formerly "Solectria Renewables, LLC" | 0.5 |  |  | 100 | 250 | 400 | 0.39 | 0.78 | 1.17 | 1.95 | 2.93 | 3.9 | 93 | 95.7 | 96.5 | 96.7 | 96.1 | 95.5 | 96.1 | 92.9 | 95.6 | 96.4 | 96.5 | 96 | 95.4 | 96 | 90 | 93.7 | 95.2 | 95.7 | 95.5 | 95 | 95.2 |  | 2018-02-15
Yaskawa Solectria Solar | PVI 4000-POS-240 [240V] | 3.9 kW, 240 Vac Utility Interactive Inverter | 3.9 | 240 | 96 | Y | N | Formerly "Solectria Renewables, LLC" | 0.5 |  |  | 100 | 250 | 400 | 0.39 | 0.78 | 1.17 | 1.95 | 2.93 | 3.9 | 93 | 95.7 | 96.5 | 96.7 | 96.1 | 95.5 | 96.1 | 92.9 | 95.6 | 96.4 | 96.5 | 96 | 95.4 | 96 | 90 | 93.7 | 95.2 | 95.7 | 95.5 | 95 | 95.2 |  | 2018-02-15
Yaskawa Solectria Solar | PVI 4000S [240V] | 4 kW, 240 Vac Utility Interactive Inverter | 4.02 | 240 | 96 | Y | N | Formerly "Solectria Renewables, LLC" | 0.47 |  |  | 100 | 275 | 400 | 0.4 | 0.8 | 1.21 | 2.01 | 3.02 | 4.02 | 92.6 | 95.7 | 96.4 | 96.5 | 96.3 | 95.5 | 96.1 | 91.8 | 95.3 | 96.1 | 96.3 | 96.1 | 95.4 | 95.9 | 90 | 94.1 | 95.2 | 95.7 | 95.5 | 94.9 | 95.2 |  | 2018-02-15
Yaskawa Solectria Solar | PVI 4000S-P [240V] | 4 kW, 240 Vac Utility Interactive Inverter | 4.02 | 240 | 96 | Y | N | Formerly "Solectria Renewables, LLC" | 0.47 |  |  | 100 | 275 | 400 | 0.4 | 0.8 | 1.21 | 2.01 | 3.02 | 4.02 | 92.6 | 95.7 | 96.4 | 96.5 | 96.3 | 95.5 | 96.1 | 91.8 | 95.3 | 96.1 | 96.3 | 96.1 | 95.4 | 95.9 | 90 | 94.1 | 95.2 | 95.7 | 95.5 | 94.9 | 95.2 |  | 2018-02-15
Yaskawa Solectria Solar | PVI 5000-208 [208V] | 4.3 kW, 208 Vac Utility Interactive Inverter | 4.3 | 208 | 96 | Y | N | Formerly "Solectria Renewables, LLC" | 0.5 |  |  | 100 | 275 | 400 | 0.43 | 0.86 | 1.29 | 2.15 | 3.23 | 4.3 | 93.3 | 95.5 | 96.2 | 96.4 | 96.1 | 95.6 | 96 | 92.7 | 95.2 | 95.9 | 96.2 | 96 | 95.5 | 95.8 | 91.4 | 94.2 | 95.2 | 95.8 | 95.7 | 95.2 | 95.4 |  | 2018-02-15
Yaskawa Solectria Solar | PVI 5000-POS-208 [208V] | 4.3 kW, 208 Vac Utility Interactive Inverter | 4.3 | 208 | 96 | Y | N | Formerly "Solectria Renewables, LLC" | 0.5 |  |  | 100 | 275 | 400 | 0.43 | 0.86 | 1.29 | 2.15 | 3.23 | 4.3 | 93.3 | 95.5 | 96.2 | 96.4 | 96.1 | 95.6 | 96 | 92.7 | 95.2 | 95.9 | 96.2 | 96 | 95.5 | 95.8 | 91.4 | 94.2 | 95.2 | 95.8 | 95.7 | 95.2 | 95.4 |  | 2018-02-15
Yaskawa Solectria Solar | PVI 5000S [208V] | 4.3 kW, 208 Vac Utility Interactive Inverter | 4.4 | 208 | 96 | Y | N | Formerly "Solectria Renewables, LLC" | 0.47 |  |  | 100 | 275 | 400 | 0.44 | 0.88 | 1.32 | 2.2 | 3.3 | 4.4 | 92.9 | 95.8 | 96.5 | 96.8 | 96.6 | 95.9 | 96.4 | 92.2 | 95.3 | 96.2 | 96.4 | 96.2 | 95.5 | 96 | 90.1 | 93.9 | 95 | 95.7 | 95.6 | 95.2 | 95.2 |  | 2018-02-15
Yaskawa Solectria Solar | PVI 5000S-P [208V] | 4.3 kW, 208 Vac Utility Interactive Inverter | 4.4 | 208 | 96 | Y | N | Formerly "Solectria Renewables, LLC" | 0.47 |  |  | 100 | 275 | 400 | 0.44 | 0.88 | 1.32 | 2.2 | 3.3 | 4.4 | 92.9 | 95.8 | 96.5 | 96.8 | 96.6 | 95.9 | 96.4 | 92.2 | 95.3 | 96.2 | 96.4 | 96.2 | 95.5 | 96 | 90.1 | 93.9 | 95 | 95.7 | 95.6 | 95.2 | 95.2 |  | 2018-02-15
Yaskawa Solectria Solar | PVI 5300-208 [208V] | 4.6 kW, 208 Vac Utility Interactive Inverter | 4.6 | 208 | 95.5 | Y | N | Formerly "Solectria Renewables, LLC" | 0.5 |  |  | 100 | 275 | 400 | 0.46 | 0.92 | 1.38 | 2.3 | 3.45 | 4.6 | 93.5 | 95.6 | 96.2 | 96.1 | 95.9 | 95.3 | 95.9 | 93 | 95.3 | 96 | 95.9 | 95.9 | 95.2 | 95.7 | 91.7 | 94.4 | 95.2 | 95.7 | 95.5 | 95 | 95.3 |  | 2018-02-15
Yaskawa Solectria Solar | PVI 5300-POS-208 [208V] | 4.6 kW, 208 Vac Utility Interactive Inverter | 4.6 | 208 | 95.5 | Y | N | Formerly "Solectria Renewables, LLC" | 0.5 |  |  | 100 | 275 | 400 | 0.46 | 0.92 | 1.38 | 2.3 | 3.45 | 4.6 | 93.5 | 95.6 | 96.2 | 96.1 | 95.9 | 95.3 | 95.9 | 93 | 95.3 | 96 | 95.9 | 95.9 | 95.2 | 95.7 | 91.7 | 94.4 | 95.2 | 95.7 | 95.5 | 95 | 95.3 |  | 2018-02-15
Yaskawa Solectria Solar | PVI 5000-240 [240V] | 4.6 kW, 208 Vac Utility Interactive Inverter | 4.9 | 240 | 96 | Y | N | Formerly "Solectria Renewables, LLC" | 0.5 |  |  | 100 | 275 | 400 | 0.49 | 0.98 | 1.47 | 2.45 | 3.68 | 4.9 | 93.9 | 96 | 96.5 | 96.6 | 96.2 | 95.6 | 96.2 | 93.4 | 95.7 | 96.3 | 96.5 | 96 | 95.4 | 96 | 92.1 | 94.8 | 95.7 | 96 | 95.8 | 95.2 | 95.6 |  | 2018-02-15
Yaskawa Solectria Solar | PVI 5000-POS-240 [240V] | 4.9 kW, 240 Vac Utility Interactive Inverter | 4.9 | 240 | 96 | Y | N | Formerly "Solectria Renewables, LLC" | 0.5 |  |  | 100 | 275 | 400 | 0.49 | 0.98 | 1.47 | 2.45 | 3.68 | 4.9 | 93.9 | 96 | 96.5 | 96.6 | 96.2 | 95.6 | 96.2 | 93.4 | 95.7 | 96.3 | 96.5 | 96 | 95.4 | 96 | 92.1 | 94.8 | 95.7 | 96 | 95.8 | 95.2 | 95.6 |  | 2018-02-15
Yaskawa Solectria Solar | PVI 5000S [240V] | 4.9 kW, 240 Vac Utility Interactive Inverter | 5.01 | 240 | 96 | Y | N | Formerly "Solectria Renewables, LLC" | 0.47 |  |  | 100 | 275 | 400 | 0.5 | 1 | 1.5 | 2.51 | 3.76 | 5.01 | 93.9 | 96.1 | 96.6 | 96.7 | 96.4 | 95.7 | 96.3 | 92.7 | 95.8 | 96.4 | 96.5 | 96.2 | 95.6 | 96.1 | 91.2 | 94.7 | 95.7 | 96.1 | 95.9 | 95.4 | 95.7 |  | 2018-02-15
Yaskawa Solectria Solar | PVI 5000S-P [240V] | 5 kW, 240 Vac Utility Interactive Inverter | 5.01 | 240 | 96 | Y | N | Formerly "Solectria Renewables, LLC" | 0.47 |  |  | 100 | 275 | 400 | 0.5 | 1 | 1.5 | 2.51 | 3.76 | 5.01 | 93.9 | 96.1 | 96.6 | 96.7 | 96.4 | 95.7 | 96.3 | 92.7 | 95.8 | 96.4 | 96.5 | 96.2 | 95.6 | 96.1 | 91.2 | 94.7 | 95.7 | 96.1 | 95.9 | 95.4 | 95.7 |  | 2018-02-15
Yaskawa Solectria Solar | PVI 5200TL [208V] | 5.2 kVA, 1-phase, transformerless Utility Interactive Inverter | 5.2 | 208 | 97.5 | Y | N | Formerly "Solectria Renewables, LLC" | 1.31 |  |  | 100 | 380 | 500 | 0.52 | 1.04 | 1.56 | 2.6 | 3.9 | 5.2 | 93.6 | 95.6 | 96.3 | 97.2 | 97.1 | 96.8 | 96.8 | 95.2 | 96.6 | 97.5 | 98 | 98 | 97.7 | 97.7 | 93.6 | 96.3 | 97 | 97.7 | 97.7 | 97.5 | 97.4 |  | 2018-02-15
Yaskawa Solectria Solar | PVI 5200TL [240V] | 5.2 kVA, 1-phase, transformerless Utility Interactive Inverter | 5.2 | 240 | 97.5 | Y | N | Formerly "Solectria Renewables, LLC" | 1.42 |  |  | 100 | 380 | 500 | 0.52 | 1.04 | 1.56 | 2.6 | 3.9 | 5.2 | 94 | 95.8 | 96.4 | 97.3 | 97.4 | 97.1 | 97 | 95.2 | 97 | 97.5 | 98.2 | 98.3 | 98.1 | 98 | 93.8 | 96.6 | 97.2 | 97.9 | 98 | 98 | 97.7 |  | 2018-02-15
Yaskawa Solectria Solar | PVI 5300-240 [240V] | 5.3 kW, 240 Vac Utility Interactive Inverter | 5.3 | 240 | 96 | Y | N | Formerly "Solectria Renewables, LLC" | 0.5 |  |  | 100 | 275 | 400 | 0.53 | 1.06 | 1.59 | 2.65 | 3.98 | 5.3 | 94.3 | 96.1 | 96.3 | 96.4 | 96 | 95.2 | 96 | 93.8 | 95.9 | 96.1 | 96.3 | 95.8 | 95.2 | 95.8 | 92.5 | 95 | 95.7 | 96 | 95.5 | 94.9 | 95.4 |  | 2018-02-15
Yaskawa Solectria Solar | PVI 5300-POS-240 [240V] | 5.3 kW, 240 Vac Utility Interactive Inverter | 5.3 | 240 | 96 | Y | N | Formerly "Solectria Renewables, LLC" | 0.5 |  |  | 100 | 275 | 400 | 0.53 | 1.06 | 1.59 | 2.65 | 3.98 | 5.3 | 94.3 | 96.1 | 96.3 | 96.4 | 96 | 95.2 | 96 | 93.8 | 95.9 | 96.1 | 96.3 | 95.8 | 95.2 | 95.8 | 92.5 | 95 | 95.7 | 96 | 95.5 | 94.9 | 95.4 |  | 2018-02-15
Yaskawa Solectria Solar | PVI 6500-208 [208V] | 6.43 kW, 208 Vac Utility Interactive Inverter | 6.43 | 208 | 95.5 | Y | N | Formerly "Solectria Renewables, LLC" | 0.5 |  |  | 100 | 275 | 400 | 0.643 | 1.286 | 1.929 | 3.215 | 4.823 | 6.43 | 93.3 | 95.6 | 96 | 96 | 95.6 | 94.8 | 95.6 | 92.9 | 95.4 | 95.9 | 95.9 | 95.5 | 94.8 | 95.5 | 91.6 | 94.8 | 95.4 | 95.6 | 95.2 | 94.6 | 95.1 |  | 2018-02-15
Yaskawa Solectria Solar | PVI 6500-240 [240V] | 6.43 kW, 240 Vac Utility Interactive Inverter | 6.45 | 240 | 96 | Y | N | Formerly "Solectria Renewables, LLC" | 0.65 |  |  | 100 | 275 | 400 | 0.645 | 1.29 | 1.935 | 3.225 | 4.838 | 6.45 | 93.5 | 95.9 | 96.3 | 96.3 | 96 | 95.4 | 96 | 93.1 | 95.7 | 96.2 | 96.3 | 96 | 95.3 | 95.9 | 91.8 | 95 | 95.6 | 95.9 | 95.7 | 95.2 | 95.5 |  | 2018-02-15
Yaskawa Solectria Solar | PVI 6500-277 [277V] | 6.43 kW, 277 Vac Utility Interactive Inverter | 6.45 | 277 | 96 | Y | N | Formerly "Solectria Renewables, LLC" | 0.9 |  |  | 100 | 275 | 400 | 0.645 | 1.29 | 1.935 | 3.225 | 4.838 | 6.45 | 93.8 | 96.1 | 96.5 | 96.7 | 96.4 | 95.8 | 96.3 | 93.4 | 95.9 | 96.4 | 96.5 | 96.3 | 95.8 | 96.2 | 92 | 95.3 | 95.9 | 96.2 | 96 | 95.6 | 95.8 |  | 2018-02-15
Yaskawa Solectria Solar | PVI 6600TL [208V] | 6.6 kVA, 1-phase, transformerless Utility Interactive Inverter | 6.6 | 208 | 97.5 | Y | N | Formerly "Solectria Renewables, LLC" | 1.23 |  |  | 100 | 380 | 500 | 0.66 | 1.32 | 1.98 | 3.3 | 4.95 | 6.6 | 94.4 | 96.1 | 97 | 97.2 | 96.9 | 96.2 | 96.8 | 95.9 | 96.9 | 97.8 | 98 | 97.7 | 97.3 | 97.7 | 95 | 96.4 | 97.4 | 97.7 | 97.6 | 97.1 | 97.4 |  | 2018-02-15
Yaskawa Solectria Solar | PVI 6600TL [240V] | 6.6 kVA, 1-phase, transformerless Utility Interactive Inverter | 6.6 | 240 | 97.5 | Y | N | Formerly "Solectria Renewables, LLC" | 1.45 |  |  | 100 | 380 | 500 | 0.66 | 1.32 | 1.98 | 3.3 | 4.95 | 6.6 | 94.3 | 96.2 | 96.9 | 97.4 | 97.2 | 96.8 | 97 | 96 | 97.3 | 97.9 | 98.3 | 98.2 | 97.9 | 98 | 95 | 96.8 | 97.6 | 98 | 98 | 97.7 | 97.7 |  | 2018-02-15
Yaskawa Solectria Solar | PVI 7600TL [208V] | 7.6 kVA, 1-phase, transformerless Utility Interactive Inverter | 6.6 | 208 | 97.5 | Y | N | Formerly "Solectria Renewables, LLC" | 1.23 |  |  | 100 | 380 | 500 | 0.66 | 1.32 | 1.98 | 3.3 | 4.95 | 6.6 | 94.4 | 96.1 | 97 | 97.2 | 96.9 | 96.2 | 96.8 | 95.9 | 96.9 | 97.8 | 98 | 97.7 | 97.3 | 97.7 | 95 | 96.4 | 97.4 | 97.7 | 97.6 | 97.1 | 97.4 |  | 2018-02-15
Yaskawa Solectria Solar | PVI 7500-208 [208V] | 7.43 kW, 208 Vac Utility Interactive Inverter | 7.43 | 208 | 95.5 | Y | N | Formerly "Solectria Renewables, LLC" | 0.52 |  |  | 100 | 275 | 400 | 0.743 | 1.486 | 2.229 | 3.715 | 5.573 | 7.43 | 94.1 | 96 | 96.2 | 96.1 | 95.4 | 94.6 | 95.6 | 93.7 | 95.7 | 96 | 96 | 95.3 | 94.5 | 95.5 | 92.5 | 95.1 | 95.6 | 95.6 | 95.1 | 94.3 | 95.1 |  | 2018-02-15
Yaskawa Solectria Solar | PVI 7500-240 [240V] | 7.43 kW, 240 Vac Utility Interactive Inverter | 7.45 | 240 | 96 | Y | N | Formerly "Solectria Renewables, LLC" | 0.68 |  |  | 100 | 275 | 400 | 0.745 | 1.49 | 2.235 | 3.725 | 5.588 | 7.45 | 94.3 | 96.2 | 96.5 | 96.5 | 95.9 | 95.2 | 96 | 93.9 | 96 | 96.3 | 96.3 | 95.8 | 95.1 | 95.9 | 92.7 | 95.4 | 95.9 | 96 | 95.5 | 94.9 | 95.5 |  | 2018-02-15
Yaskawa Solectria Solar | PVI 7500-277 [277V] | 7.43 kW, 277 Vac Utility Interactive Inverter | 7.46 | 277 | 96 | Y | N | Formerly "Solectria Renewables, LLC" | 0.9 |  |  | 100 | 275 | 400 | 0.746 | 1.492 | 2.238 | 3.73 | 5.595 | 7.46 | 94.4 | 96.4 | 96.7 | 96.6 | 96.2 | 95.5 | 96.3 | 94 | 96.1 | 96.5 | 96.6 | 96.2 | 95.5 | 96.2 | 92.9 | 95.5 | 96.1 | 96.2 | 95.9 | 95.3 | 95.8 |  | 2018-02-15
Yaskawa Solectria Solar | PVI 7600TL [240V] | 7.6 kVA, 1-phase, transformerless Utility Interactive Inverter | 7.6 | 240 | 97.5 | Y | N | Formerly "Solectria Renewables, LLC" | 1.43 |  |  | 100 | 380 | 500 | 0.76 | 1.52 | 2.28 | 3.8 | 5.7 | 7.6 | 95 | 96.4 | 97.3 | 97.4 | 97 | 96.4 | 97 | 96.3 | 97.4 | 98.1 | 98.3 | 98 | 97.7 | 98 | 95.5 | 97.2 | 97.7 | 98 | 97.9 | 97.5 | 97.7 |  | 2018-02-15
Yaskawa Solectria Solar | PVI 10kW-208 [208V] | 10 kW, 208 Vac Commercial Grid-Tied Solar PV Inverter | 10.36 | 208 | 96 | Y | N | Formerly "Solectria Renewables, LLC" | 2.56 |  |  | 225 | 270 | 380 | 1.04 | 2.07 | 3.11 | 5.18 | 7.77 | 10.36 | 88.6 | 93.7 | 95 | 96.4 | 96.3 | 96.1 | 95.7 | 93.2 | 94.8 | 95.7 | 96.4 | 96.2 | 95.8 | 96 | 82.5 | 93.9 | 95.8 | 96.7 | 96.7 | 96.2 | 95.9 |  | 2018-02-15
Yaskawa Solectria Solar | PVI 10kW-480 [480V] | 10 kW, 480 Vac Commercial Grid-Tied Solar PV Inverter | 10.41 | 480 | 96 | Y | N | Formerly "Solectria Renewables, LLC" | 11.36 |  |  | 225 | 270 | 380 | 1.04 | 2.08 | 3.12 | 5.2 | 7.81 | 10.41 | 91.7 | 95.4 | 96 | 96.4 | 96.3 | 96.1 | 96.1 | 91.7 | 95.5 | 96.2 | 96.4 | 96.3 | 96.1 | 96.1 | 92.3 | 95.5 | 96.2 | 96.6 | 96.4 | 96.2 | 96.2 |  | 2018-02-15
Yaskawa Solectria Solar | PVI 13 kW-208 [208V] | 13 kW, 208 Vac Commercial Grid-Tied Solar PV Inverter | 13.69 | 208 | 96 | Y | N | Formerly "Solectria Renewables, LLC" | 2.56 |  |  | 225 | 270 | 380 | 1.37 | 2.74 | 4.11 | 6.85 | 10.27 | 13.69 | 91.2 | 94.7 | 96.1 | 96.3 | 96.1 | 95.7 | 95.9 | 93.5 | 95.9 | 96.9 | 96.3 | 95.8 | 95.3 | 95.9 | 94.3 | 96.4 | 96.9 | 96.5 | 96.2 | 95.8 | 96.2 |  | 2018-02-15
Yaskawa Solectria Solar | PVI 13 kW-480 [480V] | 13 kW, 480 Vac Commercial Grid-Tied Solar PV Inverter | 13.7 | 480 | 96 | Y | N | Formerly "Solectria Renewables, LLC" | 11.36 |  |  | 225 | 270 | 380 | 1.37 | 2.74 | 4.11 | 6.85 | 10.27 | 13.7 | 93.3 | 95.8 | 96.3 | 96.4 | 96.1 | 95.6 | 96 | 93.6 | 96 | 96.4 | 96.4 | 96.1 | 95.6 | 96 | 93.2 | 96.1 | 96.5 | 96.5 | 96.2 | 95.8 | 96.2 |  | 2018-02-15
Yaskawa Solectria Solar | PVI 14TL-208 | Photovoltaic Inverter | 14 |  | 96 | Y | N | Formerly "Solectria Renewables, LLC" | 4 |  |  | 300 | 385 | 540 | 1.4 | 2.8 | 4.2 | 7 | 10.5 | 14 | 94.9 | 95.4 | 95.6 | 95.6 | 95.2 | 94.7 | 95.3 | 95.7 | 96.5 | 96.9 | 96.8 | 96.5 | 96.1 | 96.6 | 93.7 | 96.8 | 95.9 | 96.2 | 96 | 95.6 | 96 |  | 2018-02-15
Yaskawa Solectria Solar | PVI 15kW-208 [208V] | 15 kW, 208 Vac Commercial Grid-Tied Solar PV Inverter | 15.05 | 208 | 96 | Y | N | Formerly "Solectria Renewables, LLC" | 2.56 |  |  | 225 | 270 | 380 | 1.5 | 3.01 | 4.51 | 7.52 | 11.28 | 15.05 | 92.2 | 95 | 96.4 | 96.3 | 95.9 | 95.4 | 95.8 | 92.2 | 95.7 | 96.4 | 96.3 | 95.7 | 95 | 95.7 | 92.1 | 95.8 | 96.5 | 96.5 | 96.3 | 95.3 | 96.1 |  | 2018-02-15
Yaskawa Solectria Solar | PVI 15kW-480 [480V] | 15 kW, 480 Vac Commercial Grid-Tied Solar PV Inverter | 15.35 | 480 | 96 | Y | N | Formerly "Solectria Renewables, LLC" | 11.36 |  |  | 225 | 270 | 380 | 1.54 | 3.07 | 4.61 | 7.68 | 11.51 | 15.35 | 93.9 | 96 | 96.4 | 96.3 | 96 | 95.3 | 96 | 94.2 | 96.2 | 96.4 | 96.4 | 96 | 95.3 | 96 | 94.1 | 96.2 | 96.6 | 96.5 | 96 | 95.5 | 96.1 |  | 2018-02-15
Yaskawa Solectria Solar | PVI 20TL-480 | Photovoltaic Inverter | 20 |  | 97 | Y | N | Formerly "Solectria Renewables, LLC" | 2 |  |  | 300 | 480 | 550 | 2 | 4 | 6 | 10 | 15 | 20 | 94.9 | 96.2 | 96.4 | 96.6 | 96.2 | 95.7 | 96.2 | 95.2 | 96.7 | 97.1 | 97.2 | 97.1 | 96.9 | 97 | 95.3 | 96.8 | 97.2 | 97.4 | 97.3 | 97.2 | 97.2 |  | 2018-02-15
Yaskawa Solectria Solar | PVI 23TL-480 | 23kVA, 3-phase, transformerless Utility Interactive Inverter | 23 |  | 98 | Y | N | Formerly "Solectria Renewables, LLC" | 1 |  |  | 480 | 720 | 800 | 2.3 | 4.6 | 6.9 | 11.5 | 17.25 | 23 | 95.8 | 97 | 97.2 | 97.4 | 97.4 | 97.3 | 97.3 | 97 | 98.2 | 98.4 | 98.6 | 98.5 | 98.4 | 98.4 | 96.6 | 98 | 98.2 | 98.4 | 98.4 | 98.3 | 98.3 |  | 2018-02-15
Yaskawa Solectria Solar | PVI 28TL-480 | 28kVA, 3-phase, transformerless Utility Interactive Inverter | 28 |  | 98 | Y | N | Formerly "Solectria Renewables, LLC" | 0.9 |  |  | 500 | 725 | 800 | 2.8 | 5.6 | 8.4 | 14 | 21 | 28 | 96.3 | 97.2 | 97.4 | 97.5 | 97.4 | 97.2 | 97.3 | 97.5 | 98.3 | 98.5 | 98.5 | 98.4 | 98.2 | 98.4 | 97.2 | 98.1 | 98.4 | 98.4 | 98.3 | 98.1 | 98.3 |  | 2018-02-15
Yaskawa Solectria Solar | PVI 36TL-480 | 36kVA, 3-phase, transformerless Utility Interactive Inverter | 36 |  | 98 | Y | N | Multiple Listing of CHINT POWER SYSTEMS America CPS SCA36KTL-DO/US and Canadian Solar Inc CSI-36KTL-CT Formerly "Solectria Renewables, LLC" | 0 |  |  | 540 | 730 | 800 | 3.6 | 7.2 | 10.8 | 18 | 27 | 36 | 95.5 | 96.8 | 97.2 | 97.5 | 97.5 | 97.3 | 97.3 | 97.4 | 98.3 | 98.5 | 98.5 | 98.5 | 98.3 | 98.4 | 97.1 | 98 | 98.3 | 98.4 | 98.3 | 98.2 | 98.3 |  | 2018-02-15
Yaskawa Solectria Solar | PVI 50 kW-240 | Photovoltaic Inverter | 50 |  | 97 | N | N | Formerly "Solectria Renewables, LLC" | 1 |  |  | 300 | 345 | 480 | 5 | 10 | 15 | 25 | 37.5 | 50 | 92.5 | 96.1 | 97.3 | 97.7 | 97.5 | 97.1 | 97.2 | 92.8 | 96.3 | 96.9 | 97.6 | 97.4 | 97.2 | 97.1 | 90.7 | 95.5 | 96.5 | 97 | 97 | 96.9 | 96.6 |  | 2018-02-15
Yaskawa Solectria Solar | PVI 50 kW-480 [480V] | 50 kW, 480 Vac Commercial Grid-Tied Solar PV Inverter | 50 | 480 | 96 | Y | N | Formerly "Solectria Renewables, LLC" | 2.85 |  |  | 300 | 345 | 480 | 5 | 10 | 15 | 25 | 37.5 | 50 | 90.3 | 94.7 | 95.8 | 96.4 | 96.5 | 96.3 | 96.1 | 89.7 | 94.5 | 95.7 | 96.4 | 96.4 | 96.2 | 95.9 | 87.8 | 93.6 | 95 | 95.9 | 96.1 | 96 | 95.5 |  | 2018-02-15
Yaskawa Solectria Solar | PVI 50TL-480 [480V] | 50 kVA , 480 Vac, 3-phase Utility Interactive Inverter, non-isolated, 1000Vdc | 50 | 480 | 98.5 | Y | N | Multiple Listing of CHINT POWER SYSTEMS America CPS SCA50KTL-DO/US and Canadian Solar Inc CSI-50KTL-CT Formerly "Solectria Renewables, LLC" | 0.88 |  |  | 480 | 730 | 850 | 5 | 10 | 15 | 25 | 37.5 | 50 | 95.6 | 96.8 | 97.5 | 97.9 | 97.8 | 97.7 | 97.6 | 98 | 98.6 | 98.8 | 98.8 | 98.7 | 98.6 | 98.7 | 97.7 | 98.5 | 98.6 | 98.7 | 98.6 | 98.5 | 98.6 | 2017-10-01 | 2018-10-15
Yaskawa Solectria Solar | PVI-50-208 [208V] |  | 50 | 208 | 96 | Y | N | Formerly "Solectria Renewables, LLC" | 0.49 |  |  | 300 | 345 | 480 | 5 | 10 | 15 | 25 | 37.5 | 50 | 90.4 | 95.3 | 96.5 | 96.6 | 96.6 | 96.4 | 96.3 | 91.4 | 95.3 | 96.2 | 96.6 | 96.7 | 96.3 | 96.3 | 88.8 | 94.6 | 96.1 | 96.3 | 96.4 | 96.2 | 95.9 |  | 2018-02-15
Yaskawa Solectria Solar | PVI 60kW-208 [208V] | 60 kW, 208 Vac Commercial Grid-Tied Solar PV Inverter | 60 | 208 | 96 | Y | N | Formerly "Solectria Renewables, LLC" | 0.49 |  |  | 300 | 345 | 480 | 6 | 12 | 18 | 30 | 45 | 60 | 92.5 | 95.7 | 96.4 | 96.6 | 96.5 | 96.2 | 96.3 | 91.9 | 95.5 | 96.5 | 96.7 | 96.5 | 96.1 | 96.3 | 90.2 | 95.2 | 96.1 | 96.4 | 96.2 | 95.9 | 96 |  | 2018-02-15
Yaskawa Solectria Solar | PVI 60kW-240 | Photovoltaic Inverter | 60 |  | 97 | N | N | Formerly "Solectria Renewables, LLC" | 1 |  |  | 300 | 345 | 480 | 6 | 12 | 18 | 30 | 45 | 60 | 93.6 | 96.8 | 97.2 | 97.8 | 97.5 | 97 | 97.3 | 93.6 | 96.7 | 97.6 | 97.4 | 97.2 | 97 | 97.1 | 92.1 | 96.1 | 96.9 | 97.2 | 96.9 | 96.6 | 96.7 |  | 2018-02-15
Yaskawa Solectria Solar | PVI 60kW-480 [180V] | 60 kW, 480 Vac Commercial Grid-Tied Solar PV Inverter | 60 | 180 | 96 | Y | N | Formerly "Solectria Renewables, LLC" | 2.85 |  |  | 300 | 345 | 480 | 6 | 12 | 18 | 30 | 45 | 60 | 91.6 | 95.2 | 96.1 | 96.5 | 96.4 | 96.1 | 96.1 | 91.3 | 95.1 | 96.1 | 96.4 | 96.4 | 96.1 | 96.1 | 89.5 | 94.1 | 95.2 | 96 | 96 | 95.8 | 95.5 |  | 2018-02-15
Yaskawa Solectria Solar | PVI 60TL-480 [480V] | 60 kVA , 480 Vac, 3-phase Utility Interactive Inverter, non-isolated, 1000Vdc | 60 | 480 | 98.5 | Y | N | Multiple Listing of CHINT POWER SYSTEMS America CPS SCA60KTL-DO/US and Canadian Solar Inc CSI-60KTL-CT Formerly "Solectria Renewables, LLC" | 0.88 |  |  | 540 | 730 | 850 | 6 | 12 | 18 | 30 | 45 | 60 | 96.5 | 97.5 | 97.9 | 98.1 | 97.9 | 97.7 | 97.9 | 98.2 | 98.7 | 98.8 | 98.8 | 98.7 | 98.5 | 98.7 | 98 | 98.6 | 98.7 | 98.7 | 98.5 | 98.4 | 98.5 | 2017-10-01 | 2018-10-15
Yaskawa Solectria Solar | XGI 1000-60 [480V] | 60 kW, 1000 Vdc, 480 Vac Utility Interactive Inverter | 61.36 | 480 | 98 | N | N |  | 0.10909 |  |  | 580 | 715 | 850 | 6.1364 | 12.2728 | 18.4092 | 30.682 | 46.023 | 61.364 | 95.7 | 96.9 | 97.4 | 97.6 | 97.5 | 97.3 | 97.4 | 96.5 | 97.7 | 97.9 | 98 | 97.9 | 97.7 | 97.8 | 96.8 | 97.9 | 98 | 98.2 | 98.1 | 97.9 | 98 | 2018-02-15
Yaskawa Solectria Solar | XGI 1000-65 [480V] | 65 kW, 1000 Vdc, 480 Vac Utility Interastive Inverter | 65.31 | 480 | 98 | N | N |  | 0.10909 |  |  | 600 | 725 | 850 | 6.5311 | 13.0622 | 19.5933 | 32.6555 | 48.9833 | 65.311 | 96 | 97.2 | 97.4 | 97.6 | 97.5 | 97.2 | 97.4 | 96.7 | 97.8 | 97.9 | 98 | 97.9 | 97.7 | 97.9 | 97 | 98 | 98.1 | 98.2 | 98.1 | 97.9 | 98 | 2018-02-15
Yaskawa Solectria Solar | PVI 75 kW-208 [208V] | 75 kW, 208 Vac Commercial Grid-Tied Solar PV Inverter | 75 | 208 | 97 | Y | N | Formerly "Solectria Renewables, LLC" | 1 |  |  | 300 | 345 | 480 | 7.5 | 15 | 22.5 | 37.5 | 56.25 | 75 | 93.7 | 96.6 | 97 | 97.3 | 97.1 | 96.7 | 97 | 93.5 | 96.6 | 97.1 | 97.3 | 97 | 96.5 | 96.9 | 92.4 | 96.2 | 97 | 97.1 | 97 | 96.5 | 96.8 |  | 2018-02-15
Yaskawa Solectria Solar | PVI 75 kW-240 [240V] | 75 kW, 240 Vac Commercial Grid-Tied Solar PV Inverter | 75 | 240 | 96 | N | N | Formerly "Solectria Renewables, LLC" | 2 |  |  | 300 | 345 | 480 | 7.5 | 15 | 22.5 | 37.5 | 56.25 | 75 | 90.4 | 94.5 | 96 | 96.6 | 96.7 | 96.3 | 96.2 | 88 | 94.7 | 95.8 | 96.6 | 97.1 | 96.3 | 96.3 | 87.8 | 94.3 | 95.5 | 96.1 | 96.4 | 96.3 | 95.8 |  | 2018-02-15
Yaskawa Solectria Solar | PVI 75 kW-480 [480V] | 75 kW, 480 Vac Commercial Grid-Tied Solar PV Inverter | 75 | 480 | 97 | Y | N | Formerly "Solectria Renewables, LLC" | 2.71 |  |  | 300 | 345 | 480 | 7.5 | 15 | 22.5 | 37.5 | 56.25 | 75 | 93.8 | 96.4 | 97 | 97.2 | 97 | 96.6 | 96.9 | 93.3 | 96.4 | 96.9 | 97.2 | 96.9 | 96.4 | 96.8 | 92.6 | 96 | 96.6 | 96.9 | 96.9 | 96.5 | 96.6 |  | 2018-02-15
Yaskawa Solectria Solar | PVI 75 kW-480PE | Photovoltaic Inverter | 75 |  | 97.5 | N | N | Formerly "Solectria Renewables, LLC" | 3.89 |  |  | 300 | 345 | 480 | 7.5 | 15 | 22.5 | 37.5 | 56.25 | 75 | 95.3 | 97.3 | 97.7 | 97.7 | 97.4 | 97.2 | 97.4 | 95.4 | 96.9 | 97.4 | 97.6 | 97.4 | 97.1 | 97.3 | 95.3 | 96.2 | 97.1 | 97.4 | 97.1 | 96.9 | 97 |  | 2018-02-15
Yaskawa Solectria Solar | PVI 75-208-PE | Photovoltaic Inverter | 75 |  | 97.5 | N | N | Formerly "Solectria Renewables, LLC" | 0.5 |  |  | 300 | 345 | 480 | 7.5 | 15 | 22.5 | 37.5 | 56.25 | 75 | 95.6 | 97.4 | 97.6 | 97.8 | 97.6 | 97.2 | 97.5 | 95.6 | 97.6 | 97.6 | 97.8 | 97.5 | 97.2 | 97.5 | 92.2 | 96.6 | 97.2 | 97.5 | 97.2 | 96.9 | 97 |  | 2018-02-15
Yaskawa Solectria Solar | PVI 82 kW-480 [480V] | 82 kW, 480 Vac Commercial Grid-Tied Solar PV Inverter | 81.99 | 480 | 95.5 | Y | N | Formerly "Solectria Renewables, LLC" | 1 |  |  | 347 | 390 | 480 | 8.2 | 16.4 | 24.6 | 40.99 | 61.49 | 81.99 | 87.9 | 91.9 | 93.2 | 94.2 | 94.4 | 94.1 | 93.8 | 90.9 | 94.7 | 96.2 | 97.4 | 97.6 | 96.5 | 96.9 | 88.9 | 93.1 | 95.3 | 97.1 | 96.8 | 96.2 | 96.2 |  | 2018-02-15
Yaskawa Solectria Solar | PVI 82 kW-208 [208V] | 82 kW, 208 Vac Commercial Grid-Tied Solar PV Inverter | 83.3 | 208 | 94.5 | N | N | Formerly "Solectria Renewables, LLC" | 1 |  |  | 346 | 390 | 480 | 8.33 | 16.66 | 24.99 | 41.65 | 62.48 | 83.3 | 84.8 | 91.2 | 93.3 | 94.8 | 95.2 | 94.8 | 94.2 | 87.3 | 93.4 | 94.8 | 95.1 | 95 | 94.8 | 94.6 | 87.6 | 92.7 | 94.1 | 94.8 | 95.6 | 95.4 | 94.8 |  | 2018-02-15
Yaskawa Solectria Solar | PVI 85-208-PE | Photovoltaic Inverter | 85 |  | 97 | Y | N | Formerly "Solectria Renewables, LLC" | 0.5 |  |  | 300 | 345 | 480 | 8.5 | 17 | 25.5 | 42.5 | 63.75 | 85 | 93.5 | 96.5 | 97 | 97.4 | 97.3 | 96.8 | 97.1 | 92.2 | 96.3 | 96.8 | 97.3 | 97.1 | 96.8 | 96.8 | 92.7 | 96 | 96.9 | 97.1 | 97.1 | 96.7 | 96.8 |  | 2018-02-15
Yaskawa Solectria Solar | PVI 85kW-208 [208V] | 85 kW, 208 Vac Commercial Grid-Tied Solar PV Inverter | 85 | 208 | 96 | Y | N | Formerly "Solectria Renewables, LLC" | 1 |  |  | 300 | 345 | 480 | 8.5 | 17 | 25.5 | 42.5 | 63.75 | 85 | 89.7 | 94.6 | 95.8 | 96.6 | 96.4 | 96.3 | 96 | 88.4 | 94.1 | 95.4 | 96.2 | 96.2 | 96 | 95.7 | 86.9 | 94.5 | 95.6 | 96.3 | 96.5 | 96.1 | 95.8 |  | 2018-02-15
Yaskawa Solectria Solar | PVI 85kW-240 [240V] | 85 kW, 240 Vac Commercial Grid-Tied Solar PV Inverter | 85 | 240 | 96 | Y | N | Formerly "Solectria Renewables, LLC" | 2 |  |  | 300 | 345 | 480 | 8.5 | 17 | 25.5 | 42.5 | 63.75 | 85 | 91.4 | 95.3 | 96.4 | 96.7 | 96.6 | 96 | 96.3 | 89.9 | 95.1 | 96.2 | 96.7 | 96.4 | 96.2 | 96.1 | 89 | 94.5 | 95.7 | 96.4 | 96.3 | 96.2 | 95.9 |  | 2018-02-15
Yaskawa Solectria Solar | PVI 85kW-480 [480V] | 85 kW, 480 Vac Commercial Grid-Tied Solar PV Inverter | 85 | 480 | 96.5 | Y | N | Formerly "Solectria Renewables, LLC" | 2.86 |  |  | 300 | 345 | 480 | 8.5 | 17 | 25.5 | 42.5 | 63.75 | 85 | 90.4 | 95.2 | 96.3 | 96.7 | 96.7 | 96.3 | 96.3 | 90.1 | 94.9 | 96 | 96.7 | 96.8 | 96.5 | 96.3 | 89 | 94 | 96 | 96.7 | 96.9 | 96.3 | 96.3 |  | 2018-02-15
Yaskawa Solectria Solar | PVI 95kW-480 [480V] | 95 kW, 480 Vac Commercial Grid-Tied Solar PV Inverter | 95.32 | 480 | 95.5 | Y | N | Formerly "Solectria Renewables, LLC" | 1 |  |  | 347 | 390 | 480 | 9.53 | 19.06 | 28.6 | 47.66 | 71.49 | 95.32 | 89 | 91.9 | 94 | 94.2 | 94.3 | 94 | 93.9 | 89.4 | 94.7 | 97.8 | 98 | 97.1 | 96 | 96.9 | 89.8 | 94.3 | 96.3 | 97.1 | 96.6 | 95.7 | 96.2 |  | 2018-02-15
Yaskawa Solectria Solar | PVI 95kW-208 [208V] | 95 kW, 208 Vac Commercial Grid-Tied Solar PV Inverter | 95.47 | 208 | 94.5 | N | N | Formerly "Solectria Renewables, LLC" | 1 |  |  | 347 | 390 | 480 | 9.55 | 19.09 | 28.64 | 47.73 | 71.6 | 95.47 | 86.1 | 92.6 | 94.4 | 94.8 | 94.8 | 94.3 | 94.3 | 89.3 | 93.6 | 94.6 | 95.1 | 94.9 | 94.4 | 94.6 | 89.5 | 93.7 | 94.2 | 94.8 | 95.3 | 94.7 | 94.7 |  | 2018-02-15
Yaskawa Solectria Solar | PVI 100 kW-208 [208V] | 100 kW, 208 Vac Commercial Grid-Tied Solar PV Inverter | 100 | 208 | 96 | Y | N | Formerly "Solectria Renewables, LLC" | 1 |  |  | 300 | 354 | 480 | 10 | 20 | 30 | 50 | 75 | 100 | 91.2 | 95.3 | 96.2 | 96.5 | 96.4 | 95.9 | 96.1 | 90.3 | 94.7 | 95.9 | 96.2 | 96.1 | 95.8 | 95.8 | 90.2 | 95 | 95.9 | 96.4 | 96.3 | 95.9 | 95.9 |  | 2018-02-15
Yaskawa Solectria Solar | PVI 100 kW-240 [240V] | 100 kW, 240 Vac Commercial Grid-Tied Solar PV Inverter | 100 | 240 | 96 | N | N | Formerly "Solectria Renewables, LLC" | 2 |  |  | 300 | 345 | 480 | 10 | 20 | 30 | 50 | 75 | 100 | 91.8 | 95.6 | 96.5 | 96.7 | 96.3 | 95.6 | 96.2 | 92 | 95.6 | 96.3 | 96.9 | 96.3 | 96.5 | 96.2 | 91.2 | 94.9 | 96 | 96.7 | 96.3 | 95.9 | 96 |  | 2018-02-15
Yaskawa Solectria Solar | PVI 100 kW-480 [480V] | 100 kW, 480 Vac Commercial Grid-Tied Solar PV Inverter | 100 | 480 | 96.5 | Y | N | Formerly "Solectria Renewables, LLC" | 2.86 |  |  | 300 | 354 | 480 | 10 | 20 | 30 | 50 | 75 | 100 | 92.1 | 95.6 | 96.4 | 96.8 | 96.6 | 95.9 | 96.3 | 91.2 | 95.3 | 96.4 | 96.8 | 96.6 | 96.2 | 96.3 | 90.3 | 95.1 | 96.5 | 96.9 | 96.4 | 96.1 | 96.2 |  | 2018-02-15
Yaskawa Solectria Solar | PVI 100-208-PE | Photovoltaic Inverter | 100 |  | 97 | N | N | Formerly "Solectria Renewables, LLC" | 0.5 |  |  | 300 | 345 | 480 | 10 | 20 | 30 | 50 | 75 | 100 | 94 | 96.8 | 97.3 | 97.3 | 97 | 96.4 | 97 | 94.4 | 96.5 | 97.2 | 97.2 | 97.1 | 96.4 | 97 | 93.6 | 96.3 | 97 | 97 | 96.9 | 96.4 | 96.7 |  | 2018-02-15
Yaskawa Solectria Solar | XGI 1500-125/125 [600V] | 125 kW, 125 kVA, 600 Vac, 1500VDC, 3-Phase Utility Interactive Inverter | 124.6176 | 600 | 98.5 | N | N |  | 3.8421 |  |  | 860 | 1050 | 1250 | 12.4618 | 24.9235 | 37.3853 | 62.3088 | 93.4632 | 124.6176 | 98.4216 | 98.8698 | 98.9434 | 98.8944 | 98.8062 | 98.7204 | 98.8247 | 97.0398 | 98.3964 | 98.442 | 98.5462 | 98.5064 | 98.4522 | 98.4402 | 95.8522 | 97.5256 | 98.1534 | 98.2428 | 98.249 | 98.2622 | 98.1048 | 2018-11-15
Yaskawa Solectria Solar | XGI 1500-125/150 [600V] | 125 kW, 150 kVA, 600 Vac, 1500VDC, 3-Phase Utility Interactive Inverter | 124.6176 | 600 | 98.5 | N | N |  | 3.8421 |  |  | 860 | 1050 | 1250 | 12.4618 | 24.9235 | 37.3853 | 62.3088 | 93.4632 | 124.6176 | 98.4216 | 98.8698 | 98.9434 | 98.8944 | 98.8062 | 98.7204 | 98.8247 | 97.0398 | 98.3964 | 98.442 | 98.5462 | 98.5064 | 98.4522 | 98.4402 | 95.8522 | 97.5256 | 98.1534 | 98.2428 | 98.249 | 98.2622 | 98.1048 | 2018-11-15
Yaskawa Solectria Solar | XGI 1500-150/166 [600V] | 150 KW, 166KVA, 600 Vac, 3-phase Grid Support Utility Interactive Inverter | 150 | 600 | 98.5 | N | N |  | 2.75 |  |  | 860 | 1100 | 1250 | 15 | 30 | 45 | 75 | 112.5 | 150 | 98.4688 | 98.9332 | 98.9862 | 98.8872 | 98.8088 | 98.718 | 98.8346 | 98.1948 | 98.2298 | 98.5054 | 98.5424 | 98.4976 | 98.38 | 98.4766 | 98.2596 | 98.2596 | 98.2786 | 98.3684 | 98.298 | 98.178 | 98.301 | 2018-11-01
Yaskawa Solectria Solar | XGI 1500-166/166 [600V] | 166 kW, 166 kVA, 600 Vac, 1500VDC, 3-Phase Utility Interactive Inverter | 165.1393 | 600 | 98.5 | N | N |  | 3.8421 |  |  | 860 | 1050 | 1250 | 16.5139 | 33.0279 | 49.5418 | 82.5697 | 123.8545 | 165.1393 | 98.5516 | 99.0108 | 99.0266 | 98.8722 | 98.7684 | 98.6026 | 98.8163 | 97.5988 | 98.6058 | 98.6698 | 98.5888 | 98.4886 | 98.3066 | 98.4926 | 96.512 | 97.8936 | 98.1316 | 98.269 | 98.1834 | 98.0808 | 98.1087 | 2018-11-15
Yaskawa Solectria Solar | SGI 225-480 [480V] | 225 kW, 480 Vac Utility Scale Grid-Tied Smartgrid PV Inverter | 230.1 | 480 | 97.5 | Y | N | Formerly "Solectria Renewables, LLC" | 28 |  |  | 300 | 360 | 480 | 23.01 | 46.03 | 69.04 | 115.1 | 172.6 | 230.1 | 95.16 | 97.39 | 97.82 | 97.99 | 97.88 | 97.7 | 97.76 | 94.02 | 96.8 | 97.47 | 97.76 | 97.76 | 97.61 | 97.52 | 93.06 | 96.24 | 97.21 | 97.56 | 97.66 | 97.51 | 97.32 |  | 2018-02-15
Yaskawa Solectria Solar | SGI 250-480 [480V] | 250 kW, 480 Vac Utility Scale Grid-Tied Smartgrid PV Inverter | 258.2 | 480 | 97.5 | Y | N | Formerly "Solectria Renewables, LLC" | 28 |  |  | 300 | 360 | 480 | 25.82 | 51.63 | 77.45 | 129.1 | 193.6 | 258.2 | 95.48 | 97.54 | 97.89 | 97.98 | 97.84 | 97.75 | 97.76 | 94.71 | 97.15 | 97.63 | 97.79 | 97.75 | 97.56 | 97.58 | 93.93 | 96.47 | 97.32 | 97.59 | 97.62 | 97.44 | 97.36 |  | 2018-02-15
Yaskawa Solectria Solar | SGI 266-480 [480V] | 266 kW, 480 Vac Utility Scale Grid-Tied Smartgrid PV Inverter | 269.8 | 480 | 97.5 | Y | N | Formerly "Solectria Renewables, LLC" | 28 |  |  | 300 | 360 | 480 | 26.98 | 53.97 | 80.95 | 134.9 | 202.4 | 269.8 | 95.79 | 97.59 | 97.9 | 97.96 | 97.81 | 97.68 | 97.75 | 94.99 | 97.15 | 97.66 | 97.83 | 97.72 | 97.49 | 97.59 | 93.93 | 96.88 | 97.39 | 97.6 | 97.59 | 97.38 | 97.38 |  | 2018-02-15
Yaskawa Solectria Solar | SGI 300-480 [480V] | 300 kW, 480 Vac Utility Scale Grid-Tied Smartgrid PV Inverter | 304.9 | 480 | 97.5 | Y | N | Formerly "Solectria Renewables, LLC" | 28 |  |  | 300 | 360 | 480 | 30.49 | 60.97 | 91.46 | 152.4 | 228.6 | 304.9 | 95.97 | 97.73 | 97.9 | 97.88 | 97.72 | 97.49 | 97.7 | 95.43 | 97.36 | 97.67 | 97.76 | 97.7 | 97.41 | 97.58 | 94.51 | 97.07 | 97.49 | 97.66 | 97.52 | 97.2 | 97.39 |  | 2018-02-15
Yaskawa Solectria Solar | SGI 500XT | Photovoltaic Inverter | 500 |  | 98 | N | N | Formerly "Solectria Renewables, LLC" | 39.82 |  |  | 300 | 345 | 480 | 50 | 100 | 150 | 250 | 375 | 500 | 96.1 | 97.7 | 98 | 98.1 | 98 | 97.7 | 97.9 | 95.7 | 97.4 | 97.8 | 98 | 98 | 97.6 | 97.8 | 94.9 | 97.3 | 97.6 | 97.9 | 97.8 | 97.7 | 97.7 |  | 2018-02-15
Yaskawa Solectria Solar | SGI 500-480 [480V] | 500 kW, 480 Vac Utility Scale Grid-Tied Smartgrid PV Inverter | 500.8 | 480 | 97 | Y | N | Formerly "Solectria Renewables, LLC" | 32 |  |  | 300 | 360 | 480 | 50.08 | 100.2 | 150.2 | 250.4 | 375.6 | 500.8 | 95.11 | 97.42 | 97.87 | 97.49 | 97.31 | 96.84 | 97.31 | 94.53 | 96.87 | 97.34 | 97.51 | 97.28 | 96.94 | 97.19 | 93.76 | 96.4 | 97 | 97.2 | 97.09 | 96.82 | 96.92 |  | 2018-02-15
Yaskawa Solectria Solar | SGI 500XTM [380V] | 500 kW, 1000 Vdc, 380 Vac, 3-Phase Utility Interactive Inverter | 507 | 380 | 96.5 | N | N | Efficiency data is inclusive of three Phase transformer from the CSA C802.2 table with transformer efficiency of 98.8%. | 88.78 |  |  | 545 | 615 | 820 | 50.7 | 101.4 | 152.1 | 253.5 | 380.25 | 507 | 93.6 | 96.1 | 96.7 | 97.1 | 97.2 | 97.1 | 96.9 | 93.2 | 95.8 | 96.5 | 96.9 | 97 | 97 | 96.7 | 92.1 | 95.3 | 96.1 | 96.6 | 96.8 | 96.8 | 96.4 | 2018-02-15
Yaskawa Solectria Solar | SGI 499PE [480V] | 499 kW, 480 Vac Utility Scale Grid-Tied PV Inverter | 508.2 | 480 | 97.5 | Y | N | Formerly "Solectria Renewables, LLC" | 17 |  |  | 300 | 360 | 480 | 50.82 | 101.6 | 152.5 | 254.1 | 381.1 | 508.2 | 97.5 | 98.2 | 98.2 | 97.8 | 97.4 | 97 | 97.6 | 96.7 | 98.3 | 98.2 | 97.6 | 97.1 | 96.5 | 97.3 | 97.6 | 97.9 | 97.7 | 97.6 | 96.9 | 96.4 | 97.2 |  | 2018-02-15
Yaskawa Solectria Solar | SGI 500PE [480V] | 500 kW, 480 Vac Utility Scale Grid-Tied PV Inverter | 508.2 | 480 | 97.5 | Y | N | Formerly "Solectria Renewables, LLC" | 17 |  |  | 300 | 360 | 480 | 50.82 | 101.6 | 152.5 | 254.1 | 381.1 | 508.2 | 97.5 | 98.2 | 98.2 | 97.8 | 97.4 | 97 | 97.6 | 96.7 | 98.3 | 98.2 | 97.6 | 97.1 | 96.5 | 97.3 | 97.6 | 97.9 | 97.7 | 97.6 | 96.9 | 96.4 | 97.2 |  | 2018-02-15
Yaskawa Solectria Solar | SGI 750XTM [380V] | 750 kW, 1000 Vdc, 380Vac, 3-Phase Utility Interactive Inverter | 753.2 | 380 | 96.5 | N | N | Efficiency data is inclusive of three Phase transformer from the CSA C802.2 table with transformer efficiency of 98.8%. | 122.55 |  |  | 545 | 615 | 820 | 75.32 | 150.64 | 225.96 | 376.6 | 564.9 | 753.2 | 94 | 96.2 | 96.7 | 97 | 97 | 96.9 | 96.8 | 93.7 | 96.2 | 96.7 | 97.1 | 97.1 | 97 | 96.9 | 91.9 | 95.3 | 96.2 | 96.7 | 96.7 | 96.8 | 96.4 | 2018-02-15
Yes! Solar | ES3000 [208V] | 2.7 kW 208 Vac Utility Interactive Inverter | 2.7 | 208 | 95.5 | Y | N |  | 0.5 |  |  | 100 | 250 | 400 | 0.27 | 0.54 | 0.81 | 1.35 | 2.03 | 2.7 | 90.7 | 94.5 | 95.8 | 96.4 | 96.3 | 95.9 | 95.9 | 89.8 | 94.1 | 95.5 | 96.2 | 96.2 | 95.8 | 95.7 | 88.2 | 92.5 | 94.3 | 95.5 | 95.6 | 95.3 | 94.9
Yes! Solar | ES3000P [208V] | 2.7 kW 208 Vac Utility Interactive Inverter | 2.7 | 208 | 95.5 | Y | N |  | 0.5 |  |  | 100 | 250 | 400 | 0.27 | 0.54 | 0.81 | 1.35 | 2.03 | 2.7 | 90.7 | 94.5 | 95.8 | 96.4 | 96.3 | 95.9 | 95.9 | 89.8 | 94.1 | 95.5 | 96.2 | 96.2 | 95.8 | 95.7 | 88.2 | 92.5 | 94.3 | 95.5 | 95.6 | 95.3 | 94.9
Yes! Solar | ES3000 [240V] | 2.9 kW 240 Vac Utility Interactive Inverter | 2.9 | 240 | 96 | Y | N |  | 0.5 |  |  | 100 | 250 | 400 | 0.29 | 0.58 | 0.87 | 1.45 | 2.18 | 2.9 | 91.9 | 95.1 | 96.2 | 96.7 | 96.5 | 96.1 | 96.3 | 91.3 | 94.7 | 95.9 | 96.5 | 96.4 | 96 | 96.1 | 89.3 | 93.3 | 94.8 | 95.8 | 95.8 | 95.4 | 95.3
Yes! Solar | ES3000P [240V] | 2.9 kW 240 Vac Utility Interactive Inverter | 2.9 | 240 | 96 | Y | N |  | 0.5 |  |  | 100 | 250 | 400 | 0.29 | 0.58 | 0.87 | 1.45 | 2.18 | 2.9 | 91.9 | 95.1 | 96.2 | 96.7 | 96.5 | 96.1 | 96.3 | 91.3 | 94.7 | 95.9 | 96.5 | 96.4 | 96 | 96.1 | 89.3 | 93.3 | 94.8 | 95.8 | 95.8 | 95.4 | 95.3
Yes! Solar | ES4000 [208V] | 3.4 kW 208 Vac Utility Interactive Inverter | 3.4 | 208 | 95.5 | Y | N |  | 0.5 |  |  | 100 | 250 | 400 | 0.34 | 0.68 | 1.02 | 1.7 | 2.55 | 3.4 | 92.4 | 95.4 | 96.3 | 96.5 | 96.1 | 95.3 | 96 | 91.8 | 95.1 | 96 | 96.3 | 96 | 95.2 | 95.8 | 90.1 | 93.8 | 95.1 | 95.7 | 95.5 | 94.9 | 95.2
Yes! Solar | ES4000P [208V] | 3.4 kW 208 Vac Utility Interactive Inverter | 3.4 | 208 | 95.5 | Y | N |  | 0.5 |  |  | 100 | 250 | 400 | 0.34 | 0.68 | 1.02 | 1.7 | 2.55 | 3.4 | 92.4 | 95.4 | 96.3 | 96.5 | 96.1 | 95.3 | 96 | 91.8 | 95.1 | 96 | 96.3 | 96 | 95.2 | 95.8 | 90.1 | 93.8 | 95.1 | 95.7 | 95.5 | 94.9 | 95.2
Yes! Solar | ES4000 [240V] | 3.9 kW 240 Vac Utility Interactive Inverter | 3.9 | 240 | 96 | Y | N |  | 0.5 |  |  | 100 | 250 | 400 | 0.39 | 0.78 | 1.17 | 1.95 | 2.93 | 3.9 | 93 | 95.7 | 96.5 | 96.7 | 96.1 | 95.5 | 96.1 | 92.9 | 95.6 | 96.4 | 96.5 | 96 | 95.4 | 96 | 90 | 93.7 | 95.2 | 95.7 | 95.5 | 95 | 95.2
Yes! Solar | ES4000P [240V] | 3.9 kW 240 Vac Utility Interactive Inverter | 3.9 | 240 | 96 | Y | N |  | 0.5 |  |  | 100 | 250 | 400 | 0.39 | 0.78 | 1.17 | 1.95 | 2.93 | 3.9 | 93 | 95.7 | 96.5 | 96.7 | 96.1 | 95.5 | 96.1 | 92.9 | 95.6 | 96.4 | 96.5 | 96 | 95.4 | 96 | 90 | 93.7 | 95.2 | 95.7 | 95.5 | 95 | 95.2
Yes! Solar | ES5000 [208V] | 4.3 kW 208 Vac Utility Interactive Inverter | 4.3 | 208 | 96 | Y | N |  | 0.5 |  |  | 100 | 275 | 400 | 0.43 | 0.86 | 1.29 | 2.15 | 3.23 | 4.3 | 93.3 | 95.5 | 96.2 | 96.4 | 96.1 | 95.6 | 96 | 92.7 | 95.2 | 95.9 | 96.2 | 96 | 95.5 | 95.8 | 91.4 | 94.2 | 95.2 | 95.8 | 95.7 | 95.2 | 95.4
Yes! Solar | ES5000P [208V] | 4.3 kW 208 Vac Utility Interactive Inverter | 4.3 | 208 | 96 | Y | N |  | 0.5 |  |  | 100 | 275 | 400 | 0.43 | 0.86 | 1.29 | 2.15 | 3.23 | 4.3 | 93.3 | 95.5 | 96.2 | 96.4 | 96.1 | 95.6 | 96 | 92.7 | 95.2 | 95.9 | 96.2 | 96 | 95.5 | 95.8 | 91.4 | 94.2 | 95.2 | 95.8 | 95.7 | 95.2 | 95.4
Yes! Solar | ES5400 [208V] | 4.6 kW 208 Vac Utility Interactive Inverter | 4.6 | 208 | 95.5 | Y | N |  | 0.5 |  |  | 100 | 275 | 400 | 0.46 | 0.92 | 1.38 | 2.3 | 3.45 | 4.6 | 93.5 | 95.6 | 96.2 | 96.1 | 95.9 | 95.3 | 95.9 | 93 | 95.3 | 96 | 95.9 | 95.9 | 95.2 | 95.7 | 91.7 | 94.4 | 95.2 | 95.7 | 95.5 | 95 | 95.3
Yes! Solar | ES5400P [208V] | 4.6 kW 208 Vac Utility Interactive Inverter | 4.6 | 208 | 95.5 | Y | N |  | 0.5 |  |  | 100 | 275 | 400 | 0.46 | 0.92 | 1.38 | 2.3 | 3.45 | 4.6 | 93.5 | 95.6 | 96.2 | 96.1 | 95.9 | 95.3 | 95.9 | 93 | 95.3 | 96 | 95.9 | 95.9 | 95.2 | 95.7 | 91.7 | 94.4 | 95.2 | 95.7 | 95.5 | 95 | 95.3
Yes! Solar | ES5000 [240V] | 4.9 kW 240 Vac Utility Interactive Inverter | 4.9 | 240 | 96 | Y | N |  | 0.5 |  |  | 100 | 275 | 400 | 0.49 | 0.98 | 1.47 | 2.45 | 3.68 | 4.9 | 93.9 | 96 | 96.5 | 96.6 | 96.2 | 95.6 | 96.2 | 93.4 | 95.7 | 96.3 | 96.5 | 96 | 95.4 | 96 | 92.1 | 94.8 | 95.7 | 96 | 95.8 | 95.2 | 95.6
Yes! Solar | ES5000P [240V] | 4.9 kW 240 Vac Utility Interactive Inverter | 4.9 | 240 | 96 | Y | N |  | 0.5 |  |  | 100 | 275 | 400 | 0.49 | 0.98 | 1.47 | 2.45 | 3.68 | 4.9 | 93.9 | 96 | 96.5 | 96.6 | 96.2 | 95.6 | 96.2 | 93.4 | 95.7 | 96.3 | 96.5 | 96 | 95.4 | 96 | 92.1 | 94.8 | 95.7 | 96 | 95.8 | 95.2 | 95.6
Yes! Solar | ES5400 [240V] | 5.3 kW 240 Vac Utility Interactive Inverter | 5.3 | 240 | 96 | Y | N |  | 0.5 |  |  | 100 | 275 | 400 | 0.53 | 1.06 | 1.59 | 2.65 | 3.98 | 5.3 | 94.3 | 96.1 | 96.3 | 96.4 | 96 | 95.2 | 96 | 93.8 | 95.9 | 96.1 | 96.3 | 95.8 | 95.2 | 95.8 | 92.5 | 95 | 95.7 | 96 | 95.5 | 94.9 | 95.4
Yes! Solar | ES5400P [240V] | 5.3 kW 240 Vac Utility Interactive Inverter | 5.3 | 240 | 96 | Y | N |  | 0.5 |  |  | 100 | 275 | 400 | 0.53 | 1.06 | 1.59 | 2.65 | 3.98 | 5.3 | 94.3 | 96.1 | 96.3 | 96.4 | 96 | 95.2 | 96 | 93.8 | 95.9 | 96.1 | 96.3 | 95.8 | 95.2 | 95.8 | 92.5 | 95 | 95.7 | 96 | 95.5 | 94.9 | 95.4
Zhongli Talesun Solar | TAC208/240 [208V] | 240 W, 208 Vac Inverter | 0.24 | 208 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6
Zhongli Talesun Solar | TAC208/240 [240V] | 240 W, 240 Vac Inverter | 0.24 | 240 | 95 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6
Zigor | Sunzet 2 TL-US [240V] | 2110 W, 240 Vac Utility Interactive Inverter | 2.11 | 240 | 94.5 | Y | N |  | 0.25 |  |  | 100 | 375 | 400 | 0.21 | 0.42 | 0.63 | 1.06 | 1.58 | 2.11 | 85.3 | 91.6 | 92.9 | 94.3 | 94.6 | 94.5 | 93.8 | 82.1 | 91.9 | 94.2 | 95.6 | 96.1 | 96.4 | 95 | 82.2 | 91.5 | 93.8 | 95.6 | 96.1 | 96.3 | 95
Zigor | Sunzet 3 TL-US [240V] | 3180 W, 240 Vac Utility Interactive Inverter | 3.18 | 240 | 95 | Y | N |  | 0.25 |  |  | 100 | 375 | 400 | 0.32 | 0.64 | 0.95 | 1.59 | 2.39 | 3.18 | 88.8 | 92.9 | 94.1 | 94.6 | 94.3 | 94 | 94 | 88.8 | 94.4 | 95.3 | 96.2 | 96.3 | 95.9 | 95.7 | 89.5 | 93.7 | 95.3 | 96.2 | 96.3 | 96.1 | 95.7
Zigor | SUNZET4-USA [240V] | 4000 W, 240 Vac Utility Interactive Inverter | 4.03 | 240 | 95 | Y | N |  | 0.19 |  |  | 100 | 310 | 440 | 0.4 | 0.81 | 1.21 | 2.02 | 3.02 | 4.03 | 91.6 | 94.5 | 95.2 | 95.3 | 95 | 93.9 | 94.9 | 90.2 | 94.5 | 95.5 | 95.8 | 95.6 | 95 | 95.3 | 87.4 | 92.8 | 94 | 95 | 95.2 | 94.6 | 94.5
Zigor | SUNZET 4 TL-US [240V] | 4100 W, 240 Vac Utility Interactive Inverter | 4.16 | 240 | 95.5 | Y | N |  | 0.2 |  |  | 100 | 380 | 400 | 0.42 | 0.83 | 1.25 | 2.08 | 3.12 | 4.16 | 90.6 | 93.8 | 94.5 | 94.8 | 94.6 | 94.2 | 94.4 | 91.4 | 95 | 95.7 | 96.1 | 96.2 | 95.9 | 95.9 | 90.7 | 94.7 | 95.5 | 96.1 | 96.1 | 95.9 | 95.7
Zigor | SUNZET 5 TL-US [240V] | 5000 W, 240 Vac Utility Interactive Inverter | 5.24 | 240 | 95.5 | Y | N |  | 0.2 |  |  | 100 | 380 | 400 | 0.52 | 1.05 | 1.57 | 2.62 | 3.93 | 5.24 | 91.8 | 94.1 | 94.6 | 94.7 | 94.3 | 93.5 | 94.3 | 92.5 | 95.1 | 96.1 | 96.2 | 95.9 | 95.6 | 95.8 | 92.3 | 95.3 | 95.8 | 96.1 | 95.9 | 95.5 | 95.8

## Dropdown (hidden)
'ABB MICRO-0.25-I-OUTD-US-240 [240V],N,96,Y'
'ABB MICRO-0.3HV-I-OUTD-US-208 [208V],N,96,Y'
'ABB MICRO-0.3HV-I-OUTD-US-240 [240V],N,96,Y'
'ABB MICRO-0.3-I-OUTD-US-208 [208V],N,96,Y'
'ABB MICRO-0.3-I-OUTD-US-240 [240V],N,96,Y'
'ABB UNO-2.0-I-OUTD-S-US [208V],Y,95.5,N'
'ABB UNO-2.0-I-OUTD-S-US [240V],Y,95.5,N'
'ABB UNO-2.0-I-OUTD-S-US [277V],Y,95.5,N'
'ABB UNO-2.0-TL-OUTD-S-US [208V],Y,96.5,N'
'ABB UNO-2.0-TL-OUTD-S-US [240V],Y,96.5,N'
'ABB UNO-2.0-TL-OUTD-S-US [277V],Y,96.5,N'
'ABB UNO-2.0-TL-OUTD-S-US-A [208V],Y,96.5,N'
'ABB UNO-2.0-TL-OUTD-S-US-A [240V],Y,96.5,N'
'ABB UNO-2.0-TL-OUTD-S-US-A [277V],Y,96.5,N'
'ABB UNO-2.0-TL-OUTD-S-US-B-C-M [208V],Y,96.5,N'
'ABB UNO-2.0-TL-OUTD-S-US-B-C-M [240V],Y,96.5,N'
'ABB UNO-2.0-TL-OUTD-S-US-B-C-M [277V],Y,96.5,N'
'ABB UNO-2.0-TL-OUTD-S-US-B-C-M-A [208V],Y,96.5,N'
'ABB UNO-2.0-TL-OUTD-S-US-B-C-M-A [240V],Y,96.5,N'
'ABB UNO-2.0-TL-OUTD-S-US-B-C-M-A [277V],Y,96.5,N'
'ABB UNO-2.0-TL-OUTD-S-US-B-M [208V],Y,96.5,N'
'ABB UNO-2.0-TL-OUTD-S-US-B-M [240V],Y,96.5,N'
'ABB UNO-2.0-TL-OUTD-S-US-B-M [277V],Y,96.5,N'
'ABB UNO-2.0-TL-OUTD-S-US-B-M-A [208V],Y,96.5,N'
'ABB UNO-2.0-TL-OUTD-S-US-B-M-A [240V],Y,96.5,N'
'ABB UNO-2.0-TL-OUTD-S-US-B-M-A [277V],Y,96.5,N'
'ABB UNO-2.0-TL-OUTD-S-US-C-M [208V],Y,96.5,N'
'ABB UNO-2.0-TL-OUTD-S-US-C-M [240V],Y,96.5,N'
'ABB UNO-2.0-TL-OUTD-S-US-C-M [277V],Y,96.5,N'
'ABB UNO-2.0-TL-OUTD-S-US-C-M-A [208V],Y,96.5,N'
'ABB UNO-2.0-TL-OUTD-S-US-C-M-A [240V],Y,96.5,N'
'ABB UNO-2.0-TL-OUTD-S-US-C-M-A [277V],Y,96.5,N'
'ABB UNO-2.0-TL-OUTD-S-US-Z-A [208V],Y,96.5,N'
'ABB UNO-2.0-TL-OUTD-S-US-Z-A [240V],Y,96.5,N'
'ABB UNO-2.0-TL-OUTD-S-US-Z-A [277V],Y,96.5,N'
'ABB UNO-2.0-TL-OUTD-S-US-Z-M-A [208V],Y,96.5,N'
'ABB UNO-2.0-TL-OUTD-S-US-Z-M-A [240V],Y,96.5,N'
'ABB UNO-2.0-TL-OUTD-S-US-Z-M-A [277V],Y,96.5,N'
'ABB UNO-2.5-I-OUTD-S-US [208V],Y,95.5,N'
'ABB UNO-2.5-I-OUTD-S-US [240V],Y,96,N'
'ABB UNO-2.5-I-OUTD-S-US [277V],Y,96,N'
'ABB PVI-3.0-OUTD-S-US [208V],Y,96,N'
'ABB PVI-3.0-OUTD-S-US [240V],Y,96,N'
'ABB PVI-3.0-OUTD-S-US [277V],Y,96,N'
#REF!
'ABB PVI-3.0-OUTD-S-US-A [208V],Y,96,N'
#REF!
#REF!
'ABB PVI-3.0-OUTD-S-US-A [240V],Y,96,N'
#REF!
#REF!
'ABB PVI-3.0-OUTD-S-US-A [277V],Y,96,N'
#REF!
'ABB PVI-3.0-OUTD-S-US-Z [208V],Y,96,N'
'ABB PVI-3.0-OUTD-S-US-Z [240V],Y,96,N'
'ABB PVI-3.0-OUTD-S-US-Z [277V],Y,96,N'
#REF!
'ABB PVI-3.0-OUTD-S-US-Z-A [208V],Y,96,N'
#REF!
#REF!
'ABB PVI-3.0-OUTD-S-US-Z-A [240V],Y,96,N'
#REF!
#REF!
'ABB PVI-3.0-OUTD-S-US-Z-A [277V],Y,96,N'
#REF!
#REF!
'ABB PVI-3.0-OUTD-S-US-Z-M-A [208V],Y,96,N'
#REF!
#REF!
'ABB PVI-3.0-OUTD-S-US-Z-M-A [240V],Y,96,N'
#REF!
#REF!
'ABB PVI-3.0-OUTD-S-US-Z-M-A [277V],Y,96,N'
#REF!
'ABB PVI-3.0-OUTD-US [208V],Y,96,N'
'ABB PVI-3.0-OUTD-US [240V],Y,96,N'
'ABB PVI-3.0-OUTD-US [277V],Y,96,N'
'ABB UNO-3.0-TL-OUTD-S-US [208V],Y,96.5,N'
'ABB UNO-3.0-TL-OUTD-S-US [240V],Y,96.5,N'
'ABB UNO-3.0-TL-OUTD-S-US [277V],Y,96.5,N'
'ABB UNO-3.0-TL-OUTD-S-US-A [208V],Y,96.5,N'
'ABB UNO-3.0-TL-OUTD-S-US-A [240V],Y,96.5,N'
'ABB UNO-3.0-TL-OUTD-S-US-A [277V],Y,96.5,N'
'ABB UNO-3.0-TL-OUTD-S-US-B-C-M [208V],Y,96.5,N'
'ABB UNO-3.0-TL-OUTD-S-US-B-C-M [240V],Y,96.5,N'
'ABB UNO-3.0-TL-OUTD-S-US-B-C-M [277V],Y,96.5,N'
'ABB UNO-3.0-TL-OUTD-S-US-B-C-M-A [208V],Y,96.5,N'
'ABB UNO-3.0-TL-OUTD-S-US-B-C-M-A [240V],Y,96.5,N'
'ABB UNO-3.0-TL-OUTD-S-US-B-C-M-A [277V],Y,96.5,N'
'ABB UNO-3.0-TL-OUTD-S-US-B-M [208V],Y,96.5,N'
'ABB UNO-3.0-TL-OUTD-S-US-B-M [240V],Y,96.5,N'
'ABB UNO-3.0-TL-OUTD-S-US-B-M [277V],Y,96.5,N'
'ABB UNO-3.0-TL-OUTD-S-US-B-M-A [208V],Y,96.5,N'
'ABB UNO-3.0-TL-OUTD-S-US-B-M-A [240V],Y,96.5,N'
'ABB UNO-3.0-TL-OUTD-S-US-B-M-A [277V],Y,96.5,N'
'ABB UNO-3.0-TL-OUTD-S-US-C-M [208V],Y,96.5,N'
'ABB UNO-3.0-TL-OUTD-S-US-C-M [240V],Y,96.5,N'
'ABB UNO-3.0-TL-OUTD-S-US-C-M [277V],Y,96.5,N'
'ABB UNO-3.0-TL-OUTD-S-US-C-M-A [208V],Y,96.5,N'
'ABB UNO-3.0-TL-OUTD-S-US-C-M-A [240V],Y,96.5,N'
'ABB UNO-3.0-TL-OUTD-S-US-C-M-A [277V],Y,96.5,N'
'ABB UNO-3.0-TL-OUTD-S-US-Z-A [208V],Y,96.5,N'
'ABB UNO-3.0-TL-OUTD-S-US-Z-A [240V],Y,96.5,N'
'ABB UNO-3.0-TL-OUTD-S-US-Z-A [277V],Y,96.5,N'
'ABB UNO-3.0-TL-OUTD-S-US-Z-M-A [208V],Y,96.5,N'
'ABB UNO-3.0-TL-OUTD-S-US-Z-M-A [240V],Y,96.5,N'
'ABB UNO-3.0-TL-OUTD-S-US-Z-M-A [277V],Y,96.5,N'
#REF!
#REF!
#REF!
#REF!
#REF!
#REF!
#REF!
'ABB PVI-3.8-I-OUTD-x-US-y-Z [208V],Y,96,N'
#REF!
#REF!
#REF!
#REF!
#REF!
#REF!
#REF!
#REF!
#REF!
#REF!
#REF!
'ABB PVI-3.6-OUTD-S-US [208V],Y,96,N'
'ABB PVI-3.6-OUTD-S-US [240V],Y,96,N'
#REF!
'ABB PVI-3.6-OUTD-S-US [277V],Y,96,N'
#REF!
#REF!
'ABB PVI-3.6-OUTD-S-US-A [208V],Y,96,N'
#REF!
#REF!
'ABB PVI-3.6-OUTD-S-US-A [240V],Y,96,N'
#REF!
#REF!
'ABB PVI-3.6-OUTD-S-US-A [277V],Y,96,N'
'ABB PVI-3.6-OUTD-S-US-Z [208V],Y,96,N'
#REF!
'ABB PVI-3.6-OUTD-S-US-Z [240V],Y,96,N'
'ABB PVI-3.6-OUTD-S-US-Z [277V],Y,96,N'
#REF!
#REF!
'ABB PVI-3.6-OUTD-S-US-Z-A [208V],Y,96,N'
#REF!
'ABB PVI-3.6-OUTD-S-US-Z-A [240V],Y,96,N'
#REF!
'ABB PVI-3.6-OUTD-S-US-Z-A [277V],Y,96,N'
#REF!
'ABB PVI-3.6-OUTD-S-US-Z-M-A [208V],Y,96,N'
#REF!
'ABB PVI-3.6-OUTD-S-US-Z-M-A [240V],Y,96,N'
#REF!
'ABB PVI-3.6-OUTD-S-US-Z-M-A [277V],Y,96,N'
#REF!
#REF!
#REF!
'ABB PVI-3.6-OUTD-US [208V],Y,96,N'
#REF!
'ABB PVI-3.6-OUTD-US [240V],Y,96,N'
#REF!
#REF!
'ABB PVI-3.6-OUTD-US [277V],Y,96,N'
'ABB PVI-3.8-I-OUTD-x-US-y-Z [240V],Y,96.5,N'
'ABB PVI-3.8-I-OUTD-x-US-y-Z [277V],Y,96.5,N'
'ABB PVI-3.8-OUTD-S-US [208V],Y,95.5,N'
'ABB PVI-3.8-OUTD-S-US [240V],Y,96,N'
'ABB PVI-3.8-OUTD-S-US [277V],Y,96,N'
#REF!
#REF!
'ABB PVI-3.8-OUTD-S-US-A [208V],Y,95.5,N'
#REF!
#REF!
'ABB PVI-3.8-OUTD-S-US-A [240V],Y,96,N'
#REF!
'ABB PVI-3.8-OUTD-S-US-A [277V],Y,96,N'
'ABB PVI-3.8-OUTD-S-US-Z [208V],Y,95.5,N'
#REF!
'ABB PVI-3.8-OUTD-S-US-Z [240V],Y,96,N'
'ABB PVI-3.8-OUTD-S-US-Z [277V],Y,96,N'
#REF!
#REF!
'ABB PVI-3.8-OUTD-S-US-Z-A [208V],Y,95.5,N'
#REF!
'ABB PVI-3.8-OUTD-S-US-Z-A [240V],Y,96,N'
#REF!
'ABB PVI-3.8-OUTD-S-US-Z-A [277V],Y,96,N'
#REF!
'ABB PVI-3.8-OUTD-S-US-Z-M-A [208V],Y,95.5,N'
#REF!
'ABB PVI-3.8-OUTD-S-US-Z-M-A [240V],Y,96,N'
#REF!
'ABB PVI-3.8-OUTD-S-US-Z-M-A [277V],Y,96,N'
'ABB PVI-3.8-OUTD-US [208V],Y,95.5,N'
'ABB PVI-3.8-OUTD-US [240V],Y,96,N'
#REF!
'ABB PVI-3.8-OUTD-US [277V],Y,96,N'
#REF!
#REF!
#REF!
#REF!
#REF!
'ABB UNO-DM-3.8-TL-PLUS-US-SB-RA [240V],Y,96.5,N'
#REF!
#REF!
'ABB UNO-DM-3.8-TL-PLUS-US-SE-RA [240V],Y,96.5,N'
#REF!
#REF!
'ABB UNO-DM-3.8-TL-PLUS-US-SZM-RA [240V],Y,96.5,N'
#REF!
'ABB UNO-DM-3.8-TL-PLUS-US-SZ-RA [240V],Y,96.5,N'
'ABB PVI-4.2-OUTD-S-US [208V],Y,96,N'
'ABB PVI-4.2-OUTD-S-US [240V],Y,96,N'
#REF!
'ABB PVI-4.2-OUTD-S-US [277V],Y,96,N'
#REF!
#REF!
'ABB PVI-4.2-OUTD-S-US-A [208V],Y,96,N'
#REF!
#REF!
'ABB PVI-4.2-OUTD-S-US-A [240V],Y,96,N'
#REF!
#REF!
'ABB PVI-4.2-OUTD-S-US-A [277V],Y,96,N'
'ABB PVI-4.2-OUTD-S-US-Z [208V],Y,96,N'
#REF!
'ABB PVI-4.2-OUTD-S-US-Z [240V],Y,96,N'
'ABB PVI-4.2-OUTD-S-US-Z [277V],Y,96,N'
#REF!
#REF!
'ABB PVI-4.2-OUTD-S-US-Z-A [208V],Y,96,N'
#REF!
'ABB PVI-4.2-OUTD-S-US-Z-A [240V],Y,96,N'
#REF!
'ABB PVI-4.2-OUTD-S-US-Z-A [277V],Y,96,N'
#REF!
'ABB PVI-4.2-OUTD-S-US-Z-M-A [208V],Y,96,N'
#REF!
'ABB PVI-4.2-OUTD-S-US-Z-M-A [240V],Y,96,N'
#REF!
'ABB PVI-4.2-OUTD-S-US-Z-M-A [277V],Y,96,N'
'ABB PVI-4.2-OUTD-US [208V],Y,96,N'
'ABB PVI-4.2-OUTD-US [240V],Y,96,N'
'ABB PVI-4.2-OUTD-US [277V],Y,96,N'
#REF!
#REF!
#REF!
#REF!
'ABB PVI-4.6-1-OUTD-x-US-y [208V],Y,96,N'
'ABB PVI-4.6-1-OUTD-x-US-y [240V],Y,96.5,N'
'ABB PVI-4.6-1-OUTD-x-US-y [277V],Y,96.5,N'
'ABB PVI-4.6-I-OUTD-x-US-y-Z [208V],Y,96,N'
'ABB PVI-4.6-I-OUTD-x-US-y-Z [240V],Y,96.5,N'
'ABB PVI-4.6-I-OUTD-x-US-y-Z [277V],Y,96.5,N'
#REF!
'ABB UNO-DM-4.6-TL-PLUS-US-SB-RA [240V],Y,96.5,N'
#REF!
#REF!
'ABB UNO-DM-4.6-TL-PLUS-US-SE-RA [240V],Y,96.5,N'
#REF!
#REF!
'ABB UNO-DM-4.6-TL-PLUS-US-SZM-RA [240V],Y,96.5,N'
#REF!
#REF!
'ABB UNO-DM-4.6-TL-PLUS-US-SZ-RA [240V],Y,96.5,N'
#REF!
#REF!
#REF!
#REF!
#REF!
'ABB PVI-5000-OUTD-S-US-Z [208V],Y,96,N'
'ABB PVI-5000-OUTD-S-US-Z [240V],Y,96.5,N'
#REF!
'ABB PVI-5000-OUTD-S-US-Z [277V],Y,96.5,N'
'ABB PVI-5000-OUTD-S-US-Z-A [208V],Y,96,N'
#REF!
'ABB PVI-5000-OUTD-S-US-Z-A [240V],Y,96.5,N'
'ABB PVI-5000-OUTD-S-US-Z-A [277V],Y,96.5,N'
#REF!
'ABB PVI-5000-OUTD-US [208V],Y,96,N'
'ABB PVI-5000-OUTD-US [240V],Y,96.5,N'
#REF!
'ABB PVI-5000-OUTD-US [277V],Y,96.5,N'
#REF!
#REF!
'ABB PVI-5000-OUTD-US-A [208V],Y,96,N'
#REF!
'ABB PVI-5000-OUTD-US-A [240V],Y,96.5,N'
#REF!
'ABB PVI-5000-OUTD-US-A [277V],Y,96.5,N'
'ABB PVI-5000-OUTD-US-Z [208V],Y,96,N'
'ABB PVI-5000-OUTD-US-Z [240V],Y,96.5,N'
'ABB PVI-5000-OUTD-US-Z [277V],Y,96.5,N'
#REF!
'ABB PVI-5000-OUTD-US-Z-A [208V],Y,96,N'
#REF!
'ABB PVI-5000-OUTD-US-Z-A [240V],Y,96.5,N'
#REF!
'ABB PVI-5000-OUTD-US-Z-A [277V],Y,96.5,N'
#REF!
#REF!
'ABB PVI-5000-OUTD-US-Z-M-A [208V],Y,96,N'
#REF!
#REF!
'ABB PVI-5000-OUTD-US-Z-M-A [240V],Y,96.5,N'
#REF!
#REF!
'ABB PVI-5000-OUTD-US-Z-M-A [277V],Y,96.5,N'
#REF!
#REF!
#REF!
#REF!
#REF!
'ABB PVI-6000-OUTD-S-US-A [208V],Y,96,N'
#REF!
'ABB PVI-6000-OUTD-S-US-A [240V],Y,96.5,N'
'ABB PVI-6000-OUTD-S-US-A [277V],Y,96.5,N'
#REF!
'ABB PVI-6000-OUTD-S-US-Z [208V],Y,96,N'
'ABB PVI-6000-OUTD-S-US-Z [240V],Y,96.5,N'
#REF!
'ABB PVI-6000-OUTD-S-US-Z [277V],Y,96.5,N'
'ABB PVI-6000-OUTD-S-US-Z-A [208V],Y,96,N'
#REF!
'ABB PVI-6000-OUTD-S-US-Z-A [240V],Y,96.5,N'
'ABB PVI-6000-OUTD-S-US-Z-A [277V],Y,96.5,N'
#REF!
'ABB PVI-6000-OUTD-US [208V],Y,96,N'
'ABB PVI-6000-OUTD-US [240V],Y,96.5,N'
#REF!
'ABB PVI-6000-OUTD-US [277V],Y,96.5,N'
#REF!
#REF!
'ABB PVI-6000-OUTD-US-A [208V],Y,96,N'
#REF!
#REF!
'ABB PVI-6000-OUTD-US-A [240V],Y,96.5,N'
#REF!
#REF!
'ABB PVI-6000-OUTD-US-A [277V],Y,96.5,N'
'ABB PVI-6000-OUTD-US-Z [208V],Y,96,N'
#REF!
'ABB PVI-6000-OUTD-US-Z [240V],Y,96.5,N'
'ABB PVI-6000-OUTD-US-Z [277V],Y,96.5,N'
#REF!
#REF!
'ABB PVI-6000-OUTD-US-Z-A [208V],Y,96,N'
#REF!
'ABB PVI-6000-OUTD-US-Z-A [240V],Y,96.5,N'
#REF!
#REF!
'ABB PVI-6000-OUTD-US-Z-A [277V],Y,96.5,N'
#REF!
#REF!
'ABB PVI-6000-OUTD-US-Z-M-A [208V],Y,96,N'
#REF!
#REF!
'ABB PVI-6000-OUTD-US-Z-M-A [240V],Y,96.5,N'
#REF!
#REF!
'ABB PVI-6000-OUTD-US-Z-M-A [277V],Y,96.5,N'
#REF!
#REF!
#REF!
#REF!
#REF!
#REF!
#REF!
#REF!
#REF!
#REF!
#REF!
#REF!
#REF!
#REF!
#REF!
#REF!
'ABB UNO-7.6-TL-OUTD-S-US-A [208V],Y,97,N'
#REF!
'ABB UNO-7.6-TL-OUTD-S-US-A [240V],Y,97,N'
#REF!
'ABB UNO-7.6-TL-OUTD-S-US-A [277V],Y,97,N'
#REF!
'ABB UNO-7.6-TL-OUTD-S-US-Z-A [208V],Y,97,N'
#REF!
'ABB UNO-7.6-TL-OUTD-S-US-Z-A [240V],Y,97,N'
#REF!
'ABB UNO-7.6-TL-OUTD-S-US-Z-A [277V],Y,97,N'
'ABB UNO-7.6-TL-OUTD-S-US-Z-M [208V],Y,97,N'
'ABB UNO-7.6-TL-OUTD-S-US-Z-M [240V],Y,97,N'
'ABB UNO-7.6-TL-OUTD-S-US-Z-M [277V],Y,97,N'
#REF!
'ABB UNO-7.6-TL-OUTD-S-US-Z-M-A [208V],Y,97,N'
#REF!
'ABB UNO-7.6-TL-OUTD-S-US-Z-M-A [240V],Y,97,N'
#REF!
'ABB UNO-7.6-TL-OUTD-S-US-Z-M-A [277V],Y,97,N'
#REF!
'ABB UNO-8.6-TL-OUTD-S-US-A [240V],Y,97,N'
#REF!
#REF!
'ABB UNO-8.6-TL-OUTD-S-US-A [277V],Y,97,N'
#REF!
#REF!
'ABB UNO-8.6-TL-OUTD-S-US-Z-A [240V],Y,97,N'
#REF!
'ABB UNO-8.6-TL-OUTD-S-US-Z-A [277V],Y,97,N'
'ABB UNO-8.6-TL-OUTD-S-US-Z-M [240V],Y,97,N'
'ABB UNO-8.6-TL-OUTD-S-US-Z-M [277V],Y,97,N'
#REF!
'ABB UNO-8.6-TL-OUTD-S-US-Z-M-A [240V],Y,97,N'
#REF!
'ABB UNO-8.6-TL-OUTD-S-US-Z-M-A [277V],Y,97,N'
'ABB PVI-10.0-I-OUTD-x-US-208-y [208V],Y,96,N'
'ABB PVI-10.0-I-OUTD-x-US-480-y-z [480V],Y,97,N'
'ABB PVI-12.0-I-OUTD-x-US-480-y [480V],Y,97,N'
'ABB TRIO-20.0-TL-OUTD-S1A-US-480 [480V],Y,97.5,N'
'ABB TRIO-20.0-TL-OUTD-S1A-US-480-A [480V],Y,97.5,N'
'ABB TRIO-20.0-TL-OUTD-S1B-US-480 [480V],Y,97.5,N'
'ABB TRIO-20.0-TL-OUTD-S1B-US-480-A [480V],Y,97.5,N'
'ABB TRIO-20.0-TL-OUTD-S1-US-480-A [480V],Y,97.5,N'
'ABB TRIO-20.0-TL-OUTD-S-US-480-A [480V],Y,97.5,N'
'ABB TRIO-27.6-TL-OUTD-S1A-US-480-A [480V],Y,97.5,N'
'ABB TRIO-27.6-TL-OUTD-S1B-US-480-A [480V],Y,97.5,N'
'ABB TRIO-27.6-TL-OUTD-S1-US-480-A [480V],Y,97.5,N'
'ABB TRIO-27.6-TL-OUTD-S-US-480-A [480V],Y,97.5,N'
'ABB PVI-CENTRAL-50-US [480V],Y,95,N'
'ABB TRIO-50.0-TL-OUTD-US-480 [480V],Y,98,N'
#REF!
'ABB TRIO-60.0-TL-OUTD-US-480 [480V],Y,98,N'
#REF!
'ABB PVI-CENTRAL-100-US [208V],Y,95,N'
'ABB PVI-CENTRAL-100-US [480V],Y,95,N'
'ABB PVI-CENTRAL-250-US [480V],Y,97,N'
'ABB PVI-CENTRAL-300-US [480V],Y,97,N'
'ABB ULTRA-750-TL-OUTD-2-US-690-x-y-z [690V],Y,96.5,N'
'ABB ULTRA-750-TL-OUTD-4-US-690-x-y-z [690V],Y,96.5,N'
'ABB ULTRA-750-TL-OUTD-1-US-690-x-y-z [690V],Y,96.5,N'
'ABB ULTRA-750-TL-OUTD-3-US-690-x-y-z [690V],Y,96.5,N'
'ABB ULTRA-1100-TL-OUTD-2-US-690-x-y-z [690V],Y,96.5,N'
'ABB ULTRA-1100-TL-OUTD-4-US-690-x-y-z [690V],Y,97,N'
'ABB ULTRA-1100-TL-OUTD-1-US-690-x-y-z [690V],Y,96.5,N'
'ABB ULTRA-1100-TL-OUTD-3-US-690-x-y-z [690V],Y,97,N'
'ABB ULTRA-1500-TL-OUTD-2-US-690-x-y-z [690V],Y,96.5,N'
'ABB ULTRA-1500-TL-OUTD-4-US-690-x-y-z [690V],Y,97,N'
'ABB ULTRA-1500-TL-OUTD-1-US-690-x-y-z [690V],Y,96.5,N'
'ABB ULTRA-1500-TL-OUTD-3-US-690-x-y-z [690V],Y,97,N'
'ABB PVS980-58-1818kVA-I [600V],Y,97.5,N'
'ABB PVS980-58-2000kVA-K [660V],Y,97.5,N'
'Ablerex Electronics ES 2200-US-240 [240V],Y,94.5,N'
'Ablerex Electronics ES 3300-US-240 [240V],Y,95,N'
'Ablerex Electronics ES 4200-US-240 [240V],Y,95.5,N'
'Ablerex Electronics ES 4200-US-240A [240V],Y,95.5,N'
'Ablerex Electronics ES 5000-US-240 [240V],Y,95.5,N'
'Ablerex Electronics ES 5000-US-240A [240V],Y,95.5,N'
'Advanced Energy Industries AE_3TL-12_10 [480V],N,97.5,N'
'Advanced Energy Industries AE_3TL-12_10-08 [480V],Y,97.5,N'
'Advanced Energy Industries AE_3TL-12_6 [480V],N,97.5,N'
'Advanced Energy Industries AE_3TL-G3_12_10 [480V],N,97.5,N'
'Advanced Energy Industries AE_3TL-G3_12_10-8 [480V],N,97.5,N'
'Advanced Energy Industries 804R012 [480V],Y,97.5,N'
'Advanced Energy Industries AE_3TL-12_6-08 [480V],Y,97.5,N'
'Advanced Energy Industries AE_3TL-G3_12_6 [480V],N,97.5,N'
'Advanced Energy Industries AE_3TL-G3_12_6-08 [480V],N,97.5,N'
'Advanced Energy Industries AE_3TL-16_10-08 [480V],Y,97.5,N'
'Advanced Energy Industries AE_3TL-G3_16_10 [480V],N,97.5,N'
'Advanced Energy Industries 804R016 [480V],Y,97.5,N'
'Advanced Energy Industries AE_3TL-G3_16_6 [480V],N,97.5,N'
'Advanced Energy Industries 804R020 [480V],Y,97.5,N'
'Advanced Energy Industries AE_3TL-G3_20_6 [480V],N,97.5,N'
'Advanced Energy Industries AE_3TL-20_10 [480V],N,97.5,N'
'Advanced Energy Industries AE_3TL-20_6 [480V],N,97.5,N'
'Advanced Energy Industries AE_3TL-G3_20_10-08 [480V],N,97.5,N'
'Advanced Energy Industries AE_3TL-23_10-08 [480V],Y,98,N'
'Advanced Energy Industries AE_3TL-23_06 [480V],N,98,N'
'Advanced Energy Industries AE 35TX-208 [208V],Y,95.5,N'
'Advanced Energy Industries AE 35TX-600 [600V],Y,95.5,N'
'Advanced Energy Industries AE 50TX-480 [480V],Y,96,N'
'Advanced Energy Industries AE 75TX-208 [208V],Y,95.5,N'
'Advanced Energy Industries AE 75TX-480 [480V],Y,95.5,N'
'Advanced Energy Industries AE 100TX-208 [208V],Y,95.5,N'
'Advanced Energy Industries AE 100TX-600 [600V],Y,96,N'
'Advanced Energy Industries AE 250TX-600 [600V],Y,96.5,N'
'Advanced Energy Industries Solaron 250 kW (3159200-XXXX) [480V],N,97.5,N'
'Advanced Energy Industries AE 260TX-480-LV [480V],Y,96.5,N'
'Advanced Energy Industries Solaron 333 kW (3159000-XXXX) [480V],N,97.5,N'
'Advanced Energy Industries AE 500NX-HE (3159502-XXXX) [480V],N,98,N'
'Advanced Energy Industries AE 500TX-600 [600V],N,97,N'
'Advanced Energy Industries Solaron 500kW (3159500-XXXX) [480V],N,97.5,N'
'Advanced Solar Photonics PV240 [208V],Y,97,N'
'Advanced Solar Photonics PV240 [277V],Y,97,N'
'Advanced Solar Photonics PV250 [240V],Y,97,N'
'Advanced Solar Photonics PV250 [277V],Y,97,N'
'Advanced Solar Photonics PV260 [208V],Y,97,N'
'Advanced Solar Photonics PV260 [277V],Y,97,N'
'Advanced Solar Photonics PV260 [240V],Y,97,N'
'Advanced Solar Photonics PV270 [240V],Y,97,N'
'AE Solar Energy AE3.8 [208V],Y,97,N'
'AE Solar Energy AE3.8 [277V],Y,97,N'
'AE Solar Energy AE5.0 [240V],Y,97,N'
'AE Solar Energy AE6.0 [208V],Y,97,N'
'AE Solar Energy AE6.0 [240V],Y,97,N'
'AE Solar Energy AE7.0 [240V],Y,97,N'
'AEconversion GMbH INV250-45US xxxxx [208V],N,91.5,Y'
'AEconversion GMbH INV250-45US xxxxx [240V],N,92,Y'
'AEconversion GMbH INV350-60US xxxxx [208V],N,91.5,Y'
'AEconversion GMbH INV350-60US xxxxx [240V],N,92.5,Y'
'AEconversion GMbH INV500-90US-xxxxx [208V],N,94,Y'
'AEconversion GMbH INV500-90US-xxxxx [240V],N,94.5,Y'
'AEG Power Solutions Protect MPV.030.01 [480V],N,96.5,N'
'AEG Power Solutions Protect MPV.060.01 [480V],N,96.5,N'
'AEG Power Solutions Protect MPV.090.01 [480V],N,96.5,N'
'AEG Power Solutions Protect MPV.120.01 [480V],N,96.5,N'
'AEG Power Solutions Protect MPV.150.01 [480V],N,96.5,N'
'Aero-Sharp X01-030L2E1 [240V],Y,92.5,N'
'Aero-Sharp X01-050L2E1 [240V],Y,93.5,N'
'Agepower Limit Agepower AP 1500TL-US [208V],Y,96,N'
'Agepower Limit Agepower AP 1500TL-US [277V],Y,96,N'
'Agepower Limit Agepower AP 2000TL-US [208V],Y,96.5,N'
'Agepower Limit Agepower AP 2000TL-US [240V],Y,96.5,N'
'Agepower Limit Agepower AP 2000TL-US [277V],Y,96.5,N'
'Agepower Limit Agepower AP 3000TL-US [208V],Y,96.5,N'
'Agepower Limit Agepower AP 3000TL-US [240V],Y,96.5,N'
'Agepower Limit Agepower AP 3000TL-US [277V],Y,96.5,N'
'Agepower Limit Agepower AP 3600MTL-US [208V],Y,97,N'
'Agepower Limit Agepower AP 3600MTL-US [240V],Y,97,N'
'Agepower Limit Agepower AP 3600MTL-US [277V],Y,97,N'
'Agepower Limit Agepower AP 4200MTL-US [208V],Y,97,N'
'Agepower Limit Agepower AP 4200MTL-US [240V],Y,97,N'
'Agepower Limit Agepower AP 4200MTL-US [277V],Y,97,N'
'Agepower Limit Agepower AP 5000MTL-US [208V],Y,97,N'
'Agepower Limit Agepower AP 5000MTL-US [240V],Y,97,N'
'Agepower Limit Agepower AP 5000MTL-US [277V],Y,97,N'
'Agepower Limit Agepower AP 10000 TL3-US [277V],Y,95.5,N'
'Agepower Limit Agepower AP 12000 TL3-US [277V],Y,95.5,N'
'Agepower Limit Agepower AP 18000 TL3-US [277V],Y,96,N'
'Agepower Limit Agepower AP 20000 TL3-US [277V],Y,96.5,N'
'Alpha Technologies Solaris 3500 XP [240V],Y,90.5,N'
'Altenergy Power System Inc. YC200-NA [240V],N,94,Y'
'Altenergy Power System Inc. YC250A [240V],N,94,Y'
'Altenergy Power System Inc. YC250I [240V],N,94,Y'
'Altenergy Power System Inc. YC500A [208V],N,95,Y'
'Altenergy Power System Inc. YC500A [240V],N,95,Y'
'Altenergy Power System Inc. YC500I [208V],N,95,Y'
'Altenergy Power System Inc. YC500I [240V],N,95,Y'
#REF!
'Altenergy Power System Inc. YC600 [240V],N,96.5,Y'
'Altenergy Power System Inc. YC1000-3-208 [480V],N,94.5,Y'
'Altenergy Power System Inc. YC1000-3-480 [480V],N,94.5,Y'
'Altenergy Power System Inc. YC1000-3-K480,N,94.5,Y'
'Altenergy Power System Inc. QS1 [240V],N,96.5,Y'
'Altenergy Power System Inc. QS1200 [240V],N,96.5,Y'
'American Electric Technologies ISIS-1000-15000-60,Y,96.5,N'
'American Electric Technologies ISIS-1000-410-60,Y,96,N'
'AMETEK Solidstate Control RECon 30L-100-US,Y,98,N'
'AMETEK Solidstate Control RECon 30H-150-US [300V],Y,98,N'
'Andalay Solar LW-230-1-AC1-A-B [240V],N,95,Y'
'Andalay Solar LW-230-1-AC3-B-B [208V],N,95,Y'
'Andalay Solar LW-235-1-AC1-A-B [240V],N,95,Y'
'Andalay Solar LW-235-1-AC3-B-B [208V],N,95,Y'
'Andalay Solar LW-240-1-AC1-A-B [240V],N,95,Y'
'Andalay Solar LW-240-1-AC3-B-B [208V],N,95,Y'
'Andalay Solar ST-175-1AC1-A-A [240V],N,95,Y'
'Andalay Solar ST-175-1AC3-B-A [208V],N,95,Y'
'Andalay Solar ST-185-1AC1-A-A [240V],N,95,Y'
'Andalay Solar ST-185-1AC1-A-B [240V],N,95,Y'
'Andalay Solar ST-185-1AC3-B-A [208V],N,95,Y'
'Andalay Solar ST-185-1AC3-B-B [208V],N,95,Y'
'Andalay Solar ST-190-1AC1-A-B [240V],N,95,Y'
'Andalay Solar ST-190-1AC3-B-B [208V],N,95,Y'
'Andalay Solar ST-195-1AC1-A-B [240V],N,95,Y'
'Andalay Solar ST-195-1AC3-B-B [208V],N,95,Y'
'Andalay Solar LW-230-1-AC0-D-B [208V],N,96,Y'
'Andalay Solar LW-230-1-AC0-D-B [240V],N,96,Y'
'Andalay Solar LW-230-1-AC2-D-B [208V],N,96,Y'
'Andalay Solar LW-230-1-AC2-D-B [240V],N,96,Y'
'Andalay Solar LW-235-1-AC0-D-B [208V],N,96,Y'
'Andalay Solar LW-235-1-AC0-D-B [240V],N,96,Y'
'Andalay Solar LW-235-1-AC2-D-B [208V],N,96,Y'
'Andalay Solar LW-235-1-AC2-D-B [240V],N,96,Y'
'Andalay Solar LW-240-1-AC0-D-B [208V],N,96,Y'
'Andalay Solar LW-240-1-AC0-D-B [240V],N,96,Y'
'Andalay Solar LW-240-1-AC2-D-B [208V],N,96,Y'
'Andalay Solar LW-240-1-AC2-D-B [240V],N,96,Y'
'Andalay Solar TW-240-1-AC2-D-B [208V],N,96,Y'
'Andalay Solar TW-240-1-AC2-D-B [240V],N,96,Y'
'Andalay Solar TW-245-1-AC2-D-B [208V],N,96,Y'
'Andalay Solar TW-245-1-AC2-D-B [240V],N,96,Y'
'Andalay Solar TW-250-1-AC2-D-B [208V],N,96,Y'
'Andalay Solar TW-250-1-AC2-D-B [240V],N,96,Y'
'Apparent Inc. MGI220-xxx [240V],N,90,Y'
'Apparent Inc. SG424-120V [120V],N,91.5,Y'
'Apparent Inc. SG424U CA, 120VAC, 60Hz [120V],N,91.5,Y'
'AU Optronics PM060MA0_240 [240V],N,94.5,Y'
'AU Optronics PM060MA0_245 [240V],N,94.5,Y'
'AU Optronics PM060MA0_250 [240V],N,94.5,Y'
'AU Optronics PM060MA0_255 [240V],N,94.5,Y'
'AU Optronics PM060MA0_260 [240V],N,94.5,Y'
'AU Optronics PM060MA0_265 [240V],N,94.5,Y'
'AU Optronics PM060MA0_270 [240V],N,94.5,Y'
'AU Optronics PM060MA0_275 [240V],N,94.5,Y'
'AU Optronics PM060MA1_275 [240V],N,94.5,Y'
'AU Optronics PM060MA2_275 [240V],N,94.5,Y'
'AU Optronics PM060PA0_235 [240V],N,94.5,Y'
'AU Optronics PM060PA0_240 [240V],N,94.5,Y'
'AU Optronics PM060PA0_250 [240V],N,94.5,Y'
'AU Optronics PM060PA0_255 [240V],N,94.5,Y'
'AU Optronics PM060PA0_260 [240V],N,94.5,Y'
'AU Optronics PM240PA0_235 [240V],N,94.5,Y'
'AU Optronics PM240PA0_240 [240V],N,94.5,Y'
'AU Optronics PM240PA0_245 [240V],N,94.5,Y'
'AU Optronics PM245PA0_235 [240V],N,94.5,Y'
'AU Optronics PM245PA0_240 [240V],N,94.5,Y'
'AU Optronics PM245PA0_245 [240V],N,94.5,Y'
'AU Optronics PM245PA0_250 [240V],N,94.5,Y'
'AU Optronics PM245PA0_255 [240V],N,94.5,Y'
'AU Optronics PM245PA0_260 [240V],N,94.5,Y'
'AU Optronics PM250MA0_240 [240V],N,94.5,Y'
'AU Optronics PM250MA0_245 [240V],N,94.5,Y'
'AU Optronics PM250MA0_250 [240V],N,94.5,Y'
'AU Optronics PM250MA0_255 [240V],N,94.5,Y'
'AU Optronics PM250MA0_260 [240V],N,94.5,Y'
'AU Optronics PM250MA0_265 [240V],N,94.5,Y'
'AU Optronics PM250MA0_270 [240V],N,94.5,Y'
'AU Optronics PM250MA0_275 [240V],N,94.5,Y'
'AU Optronics PM250MA1_275 [240V],N,94.5,Y'
'AU Optronics PM250MA2_275 [240V],N,94.5,Y'
'AU Optronics PM060MA1_240 [208V],N,95,Y'
'AU Optronics PM060MA1_240 [240V],N,95,Y'
'AU Optronics PM060MA1_245 [208V],N,95,Y'
'AU Optronics PM060MA1_245 [240V],N,95,Y'
'AU Optronics PM060MA1_250 [208V],N,95,Y'
'AU Optronics PM060MA1_250 [240V],N,95,Y'
'AU Optronics PM060MA1_255 [208V],N,95,Y'
'AU Optronics PM060MA1_255 [240V],N,95,Y'
'AU Optronics PM060MA1_260 [208V],N,95,Y'
'AU Optronics PM060MA1_260 [240V],N,95,Y'
'AU Optronics PM060MA1_265 [208V],N,95,Y'
'AU Optronics PM060MA1_265 [240V],N,95,Y'
'AU Optronics PM060MA1_270 [208V],N,95,Y'
'AU Optronics PM060MA1_270 [240V],N,95,Y'
'AU Optronics PM060MA2_240 [208V],N,95,Y'
'AU Optronics PM060MA2_240 [240V],N,95,Y'
'AU Optronics PM060MA2_245 [208V],N,95,Y'
'AU Optronics PM060MA2_245 [240V],N,95,Y'
'AU Optronics PM060MA2_250 [208V],N,95,Y'
'AU Optronics PM060MA2_250 [240V],N,95,Y'
'AU Optronics PM060MA2_255 [208V],N,95,Y'
'AU Optronics PM060MA2_255 [240V],N,95,Y'
'AU Optronics PM060MA2_260 [208V],N,95,Y'
'AU Optronics PM060MA2_260 [240V],N,95,Y'
'AU Optronics PM060MA2_265 [208V],N,95,Y'
'AU Optronics PM060MA2_265 [240V],N,95,Y'
'AU Optronics PM060MA2_270 [208V],N,95,Y'
'AU Optronics PM060MA2_270 [240V],N,95,Y'
'AU Optronics PM060PA0_245 [240V],N,94.5,Y'
'AU Optronics PM060PA1_235 [208V],N,95,Y'
'AU Optronics PM060PA1_235 [240V],N,95,Y'
'AU Optronics PM060PA1_240 [208V],N,95,Y'
'AU Optronics PM060PA1_240 [240V],N,95,Y'
'AU Optronics PM060PA1_245 [208V],N,95,Y'
#REF!
'AU Optronics PM060PA1_245 [240V],N,95,Y'
'AU Optronics PM060PA1_250 [240V],N,95,Y'
'AU Optronics PM060PA1_255 [208V],N,95,Y'
'AU Optronics PM060PA1_255 [240V],N,95,Y'
'AU Optronics PM060PA1_260 [208V],N,95,Y'
'AU Optronics PM060PA1_260 [240V],N,95,Y'
'AU Optronics PM060PA2_235 [208V],N,95,Y'
'AU Optronics PM060PA2_235 [240V],N,95,Y'
'AU Optronics PM060PA2_240 [208V],N,95,Y'
'AU Optronics PM060PA2_240 [240V],N,95,Y'
'AU Optronics PM060PA2_245 [208V],N,95,Y'
'AU Optronics PM060PA2_245 [240V],N,95,Y'
'AU Optronics PM060PA2_250 [208V],N,95,Y'
'AU Optronics PM060PA2_250 [240V],N,95,Y'
'AU Optronics PM060PA2_255 [208V],N,95,Y'
'AU Optronics PM060PA2_255 [240V],N,95,Y'
'AU Optronics PM060PA2_260 [208V],N,95,Y'
'AU Optronics PM060PA2_260 [240V],N,95,Y'
'AU Optronics PM245PA1_235 [240V],N,95,Y'
'AU Optronics PM245PA1_240 [240V],N,95,Y'
'AU Optronics PM245PA1_245 [240V],N,95,Y'
'AU Optronics PM245PA1_250 [240V],N,95,Y'
'AU Optronics PM245PA1_255 [208V],N,95,Y'
'AU Optronics PM245PA1_255 [240V],N,95,Y'
'AU Optronics PM245PA1_260 [208V],N,95,Y'
'AU Optronics PM245PA1_260 [240V],N,95,Y'
'AU Optronics PM245PA2_235 [208V],N,95,Y'
'AU Optronics PM245PA2_235 [240V],N,95,Y'
'AU Optronics PM245PA2_240 [208V],N,95,Y'
'AU Optronics PM245PA2_240 [240V],N,95,Y'
'AU Optronics PM245PA2_245 [208V],N,95,Y'
'AU Optronics PM245PA2_245 [240V],N,95,Y'
'AU Optronics PM245PA2_250 [208V],N,95,Y'
'AU Optronics PM245PA2_250 [240V],N,95,Y'
'AU Optronics PM245PA2_255 [208V],N,95,Y'
'AU Optronics PM245PA2_255 [240V],N,95,Y'
'AU Optronics PM245PA2_260 [208V],N,95,Y'
'AU Optronics PM245PA2_260 [240V],N,95,Y'
'AU Optronics PM250MA1_240 [240V],N,95,Y'
'AU Optronics PM250MA1_245 [240V],N,95,Y'
'AU Optronics PM250MA1_250 [240V],N,95,Y'
'AU Optronics PM250MA1_255 [240V],N,95,Y'
'AU Optronics PM250MA1_260 [240V],N,95,Y'
'AU Optronics PM250MA1_265 [208V],N,95,Y'
'AU Optronics PM250MA1_265 [240V],N,95,Y'
'AU Optronics PM250MA1_270 [208V],N,95,Y'
'AU Optronics PM250MA1_270 [240V],N,95,Y'
'AU Optronics PM250MA2_240 [208V],N,95,Y'
'AU Optronics PM250MA2_240 [240V],N,95,Y'
'AU Optronics PM250MA2_245 [208V],N,95,Y'
'AU Optronics PM250MA2_245 [240V],N,95,Y'
'AU Optronics PM250MA2_250 [208V],N,95,Y'
'AU Optronics PM250MA2_250 [240V],N,95,Y'
'AU Optronics PM250MA2_255 [208V],N,95,Y'
'AU Optronics PM250MA2_255 [240V],N,95,Y'
'AU Optronics PM250MA2_260 [208V],N,95,Y'
'AU Optronics PM250MA2_260 [240V],N,95,Y'
'AU Optronics PM250MA2_265 [208V],N,95,Y'
'AU Optronics PM250MA2_265 [240V],N,95,Y'
'AU Optronics PM250MA2_270 [208V],N,95,Y'
'AU Optronics PM250MA2_270 [240V],N,95,Y'
'Auxin Solar AXU-PV1500U [208V],Y,94.5,N'
'Auxin Solar AXU-PV1500U [240V],Y,94.5,N'
'Auxin Solar AXU-PV2000U [208V],Y,95.5,N'
'Auxin Solar AXU-PV2000U [240V],Y,95,N'
'Auxin Solar AXU-PV3000U [208V],Y,95.5,N'
'Auxin Solar AXU-PV3000U [240V],Y,95.5,N'
'Auxin Solar AXN-PV4000U [208V],Y,95.5,N'
'Auxin Solar AXN-PV4000U [240V],Y,96,N'
'Ballard Power Systems EPC-PV-208-30KW [208V],Y,93,N'
'Ballard Power Systems EPC-PV-480-30KW [480V],Y,93,N'
'Ballard Power Systems EPC-PV-208-75KW,Y,91.5,N'
'Ballard Power Systems EPC-PV-480-75KW [480V],Y,91.5,N'
'Beacon Power M4,N,90,N'
'Beacon Power M4 Plus,Y,91.5,N'
'Beacon Power M5,N,89,N'
'Beacon Power M5 Plus,Y,90,N'
'Beijing Kinglong New Energy Technology Sunteams 1500 [208V],Y,95,N'
'Beijing Kinglong New Energy Technology Sunteams 1500 [240V],Y,95,N'
'Beijing Kinglong New Energy Technology Sunteams 2000 [208V],Y,95.5,N'
'Beijing Kinglong New Energy Technology Sunteams 2000 [240V],Y,96,N'
'Beijing Kinglong New Energy Technology Sunteams 3000 [208V],Y,96,N'
'Beijing Kinglong New Energy Technology Sunteams 3000 [240V],Y,96,N'
'Beijing Kinglong New Energy Technology Sunteams 4000 [208V],Y,97,N'
'Beijing Kinglong New Energy Technology Sunteams 4000 [240V],Y,97.5,N'
'Beijing Kinglong New Energy Technology Sunteams 5000 [208V],Y,97,N'
'Beijing Kinglong New Energy Technology Sunteams 5000 [240V],Y,97.5,N'
'Beyond Building Group SR1500TLI [208V],Y,94.5,N'
'Beyond Building Group SR1500TLI [240V],Y,94.5,N'
'Beyond Building Group SR2000TLI [208V],Y,95.5,N'
'Beyond Building Group SR2000TLI [240V],Y,95,N'
'Beyond Building Group SR3000TLI [208V],Y,95.5,N'
'Beyond Building Group SR3000TLI [240V],Y,95.5,N'
'Beyond Building Group SR4000TLI [208V],Y,95.5,N'
'Beyond Building Group SR4000TLI [240V],Y,96,N'
'Beyond Building Systems SR2000TL-US-240 [240V],Y,94.5,N'
'Beyond Building Systems SR3000TL-US-240 [240V],Y,95,N'
'Beyond Building Systems SR4200TL-US-240 [240V],Y,95.5,N'
'Beyond Building Systems SR5000TL-US-240 [240V],Y,95.5,N'
'Canadian Solar Inc. CM-240-EC,N,96,Y'
'Canadian Solar Inc. CS6P-245M-EA,N,96,Y'
'Canadian Solar Inc. CS6P-245P-EA,N,96,Y'
'Canadian Solar Inc. CS6P-250M-EA,N,96,Y'
'Canadian Solar Inc. CS6P-250P-EA,N,96,Y'
'Canadian Solar Inc. CS6P-255M-EA,N,96,Y'
'Canadian Solar Inc. CS6P-255P-EA,N,96,Y'
'Canadian Solar Inc. CS6P-260M-EA,N,96,Y'
'Canadian Solar Inc. CS6P-260P-EA,N,96,Y'
'Canadian Solar Inc. CM-260-EC,N,96,Y'
'Canadian Solar Inc. CM-280-EC,N,96,Y'
'Canadian Solar Inc. CM-300-EC,N,96,Y'
'Canadian Solar Inc. CSI-3000TL-CT [208V],Y,96,N'
'Canadian Solar Inc. CSI-3000TL-CT [240V],Y,96.5,N'
'Canadian Solar Inc. CSI-4000TL-CT [208V],Y,96.5,N'
'Canadian Solar Inc. CSI-4000TL-CT [240V],Y,97,N'
'Canadian Solar Inc. CSI-5000TL-CT [208V],Y,96.5,N'
'Canadian Solar Inc. CSI-5000TL-CT [240V],Y,97,N'
'Canadian Solar Inc. CSI-6000TL-CT [208V],Y,96.5,N'
'Canadian Solar Inc. CSI-6000TL-CT [240V],Y,97,N'
#REF!
#REF!
#REF!
#REF!
'Canadian Solar Inc. CSI-36KTL-CT,Y,98,N'
'Canadian Solar Inc. CSI-50KTL-CT [480V],N,98.5,N'
#REF!
#REF!
#REF!
#REF!
#REF!
#REF!
#REF!
#REF!
'Canadian Solar Inc. CSI-60KTL-CT [480V],N,98.5,N'
'Carlo Gavazzi ISGA 1 22 [240V],Y,94.5,N'
'Carlo Gavazzi ISGA 1 42 [240V],Y,95.5,N'
#REF!
#REF!
'Carlo Gavazzi ISGA 1 53 [240V],Y,95.5,N'
'CFM Equipment Distributors Green Power 1100 [120V],Y,90.5,N'
'CFM Equipment Distributors Green Power 2000 [240V],Y,92,N'
'CFM Equipment Distributors Green Power 2500 [240V],Y,94.5,N'
'CFM Equipment Distributors Green Power 3000 [240V],Y,93.5,N'
'CFM Equipment Distributors Green Power 3500 [240V],Y,95.5,N'
'CFM Equipment Distributors Green Power 4600 [208V],Y,95.5,N'
'CFM Equipment Distributors Green Power 4800 [240V],Y,96,N'
'CFM Equipment Distributors Green Power 5200 [240V],Y,96,N'
'Changzhou Nesl Solartech DJ-230P-ST15 [240V],N,94.5,Y'
'Changzhou Nesl Solartech DJ-235P-ST15 [240V],N,94.5,Y'
'Changzhou Nesl Solartech DJ-240DA/C-ST15 [240V],N,94.5,Y'
'Changzhou Nesl Solartech DJ-240P-ST15 [240V],N,94.5,Y'
'Changzhou Nesl Solartech DJ-245DA/C-ST15 [240V],N,94.5,Y'
'Changzhou Nesl Solartech DJ-250DA/C-ST15 [240V],N,94.5,Y'
'Changzhou Nesl Solartech DJ-255D/C-ST15 [240V],N,94.5,'
#REF!
'Chiconypower MU300SAP2 [240V],N,96,Y'
#REF!
'Chilicon Power, LLC CP-250-60-208/240-MC4 [208V],N,96,Y'
'Chilicon Power, LLC CP-250-60-208/240-MC4 [240V],N,96,Y'
'Chilicon Power, LLC CP-250E-60/72-208/240-MC4 [208V],N,95.5,Y'
'Chilicon Power, LLC CP-250E-60/72-208/240-MC4 [240V],N,96,Y'
'Chint Power Systems America CPS SCA3KTL-O/US [208V],Y,96,N'
'Chint Power Systems America CPS SCA3KTL-O/US [240V],Y,96.5,N'
'Chint Power Systems America CPS SCE4KTL-O US [208V],Y,97,N'
'Chint Power Systems America CPS SCA4KTL-O/US [208V],Y,96.5,N'
'Chint Power Systems America CPS SCE4KTL-O US [240V],Y,97,N'
'Chint Power Systems America CPS SCE4KTL-O US [277V],Y,97,N'
'Chint Power Systems America CPS SCA4KTL-O/US [240V],Y,97,N'
'Chint Power Systems America CPS SCE5KTL-O US [208V],Y,97,N'
'Chint Power Systems America CPS SCA5KTL-O US [208V],Y,96.5,N'
'Chint Power Systems America CPS SCE5KTL-O US [240V],Y,97,N'
'Chint Power Systems America CPS SCE5KTL-O US [277V],Y,97,N'
'Chint Power Systems America CPS SCA5KTL-O US [240V],Y,97,N'
'Chint Power Systems America CPS SCA6KTL-O US [208V],Y,96.5,N'
'Chint Power Systems America CPS SCE6KTL-O US [208V],Y,97,N'
'Chint Power Systems America CPS SCA6KTL-O US [240V],Y,97,N'
'Chint Power Systems America CPS SCE6KTL-O US [240V],Y,97,N'
'Chint Power Systems America CPS SCE6KTL-O US [277V],Y,97,N'
'Chint Power Systems America CPS SCE7KTL-O US [240V],Y,97,N'
'Chint Power Systems America CPS SCE7KTL-O US [208V],Y,97,N'
'Chint Power Systems America CPS SCE7KTL-O US [277V],Y,97,N'
'Chint Power Systems America CPS SC14KTL-DO/xx-208 [208V],Y,96,N'
'Chint Power Systems America CPS SC20KTL-DO/xx-480 [480V],Y,97,N'
#REF!
#REF!
'Chint Power Systems America CPS SCA28KTL-DO/US-480 [480V],Y,98,N'
'Chint Power Systems America CPS SCA36KTL-DO/US [480V],Y,98,N'
#REF!
'Chint Power Systems America CPS SCA50KTL-DO/US-480 [480V],Y,98.5,N'
#REF!
'Chint Power Systems America CPS SCA60KTL-DO/US-480 [480V],Y,98.5,N'
'Chint Power Systems America CPS SC100KT-O/xx-480 [480V],Y,96,N'
'Chint Power Systems America CPS SCH100KTL-DO/US-600 [600V],N,98.5,N'
'Chint Power Systems America CPS SCH125KTL-DO/US-600 [600V],N,98.5,N'
'Chint Solar Zhejiang CHPI3KTL-US [208V],Y,96,N'
'Chint Solar Zhejiang CHPI3KTL-US [240V],Y,96.5,N'
#REF!
'Chint Solar Zhejiang CHPI4KTL-US [208V],Y,96.5,N'
'Chint Solar Zhejiang CHPI4KTL-US [240V],Y,97,N'
'Chint Solar Zhejiang CHPI5KTL-US [208V],Y,96.5,N'
'Chint Solar Zhejiang CHPI5KTL-US [240V],Y,97,N'
'Chint Solar Zhejiang CHPI 6KTL-US [208V],Y,96.5,N'
'Chint Solar Zhejiang CHPI 6KTL-US [240V],Y,97,N'
'Chint Solar Zhejiang CHPI14KTL-US,Y,96,N'
'Chint Solar Zhejiang CHPI20KTL-US,Y,97,N'
'Chint Solar Zhejiang CHPI 23KTL-US,Y,98,N'
'Chint Solar Zhejiang CHPI 28KTL-US,Y,98,N'
'Concept by US Power Station PS247-05-180 [120V],Y,94,N'
'Concept by US Power Station PS247-10-180 [120V],Y,94,N'
'Concept by US Power Station PS247-15-180 [120V],Y,94,N'
'Connect Renewable Energy CE 4000 [240V],Y,93,N'
'Danfoss MLX 480V [480V],N,98.5,N'
'Danfoss Solar DLX 2.0 UL [208V],Y,96.5,N'
'Danfoss Solar DLX 2.0 UL [240V],Y,96.5,N'
'Danfoss Solar DLX 2.9 UL [240V],Y,96.5,N'
'Danfoss Solar DLX 2.9 UL [208V],Y,96.5,N'
#REF!
'Danfoss Solar DLX 3.8 UL [208V],Y,96.5,N'
'Danfoss Solar DLX 3.8 UL [240V],Y,97,N'
#REF!
'Danfoss Solar DLX 4.4 UL [208V],Y,96.5,N'
'Danfoss Solar DLX 4.4 UL [240V],Y,97,N'
#REF!
#REF!
#REF!
#REF!
#REF!
#REF!
#REF!
'Danfoss Solar MLX 400V [400V],N,98,N'
'Darfon Electronics Corp. MIG240UL00 [240V],N,95,N'
#REF!
'Darfon Electronics Corp. MIG300UL00 [240V],N,95,N'
#REF!
'Darfon Electronics Corp. G32xxxxxx [208V],N,95.5,Y'
'Darfon Electronics Corp. G32xxxxxx [240V],N,96.3,Y'
#REF!
'Darfon Electronics Corp. G32xxxxxx [277V],N,96,Y'
#REF!
#REF!
'Darfon Electronics Corp. G64xxxxxx [240V],N,95.5,Y'
'Darfon Electronics Corp. H5000x [240V],N,95.5,N'
#REF!
#REF!
'DASS tech DSP-M33250KUS,Y,95,N'
'Delta Electronics DDP-260AB XX,N,95,Y'
#REF!
#REF!
'Delta Electronics SOLIVIA 3.8 NA G4 TL [208V],Y,97.5,N'
#REF!
#REF!
#REF!
#REF!
#REF!
#REF!
#REF!
#REF!
#REF!
'Delta Electronics SOLIVIA 3.8 NA G4 TL [240V],Y,97.5,N'
'Delta Electronics SOLIVIA 5.2 NA G4 TL [208V],Y,97.5,N'
#REF!
#REF!
'Delta Electronics SOLIVIA 5.2 NA G4 TL [240V],Y,97.5,N'
#REF!
'Delta Electronics RPI H7U [208V],Y,97,N'
#REF!
#REF!
#REF!
#REF!
'Delta Electronics RPI H7U [240V] [6kVa],Y,97.5,N'
'Delta Electronics SOLIVIA 6.6 NA G4 TL [208V],Y,97.5,N'
'Delta Electronics SOLIVIA 6.6 NA G4 TL [240V],Y,97.5,N'
#REF!
#REF!
#REF!
'Delta Electronics SOLIVIA 7.6 NA G4 TL [208V],Y,97.5,N'
'Delta Electronics RPI H7U [240V] [7kVa],Y,97.5,N'
#REF!
#REF!
#REF!
#REF!
'Delta Electronics SOLIVIA 7.6 NA G4 TL [240V],Y,97.5,N'
#REF!
'Delta Electronics Delta 15 TL,Y,98,N'
#REF!
'Delta Electronics Delta 20 TL,Y,98,N'
#REF!
'Delta Electronics M24U_XXX [480V],N,98,N'
#REF!
'Delta Electronics M28U_XXX [480V],N,98,N'
'Delta Electronics M42U_XXX [480V],N,98,N'
'Delta Electronics M60U_XXX [480V],N,98.5,N'
#REF!
'Delta Electronics M80U_XXX [480V],N,98.5,N'
'Delta Energy Systems SI 1800 US [208V],Y,92.5,N'
'Delta Energy Systems SI 1800 US [240V],Y,92.5,N'
'Delta Energy Systems SI 2500 US [208V],Y,92,N'
'Delta Energy Systems SI 2500 US [240V],Y,93,N'
'Delta Energy Systems SOLIVIA 2.5 NA G4 TR [240V],Y,95,N'
'Delta Energy Systems SOLIVIA 2.5 NA G4 TR [208V],Y,94.5,N'
'Delta Energy Systems SOLIVIA 3.3 NA G4 TR [208V],Y,95,N'
'Delta Energy Systems SOLIVIA 3.3 NA G4 TR [240V],Y,95.5,N'
'Delta Energy Systems SOLIVIA 4.4 NA G4 TR [208V],Y,95,N'
'Delta Energy Systems SOLIVIA 4.4 NA G4 TR [240V],Y,95,N'
'Delta Energy Systems SOLIVIA 5.0 NA G4 TR [208V],Y,95,N'
'Delta Energy Systems SOLIVIA 5.0 NA G4 TR [240V],Y,95,N'
'Destin Power Inc. SAVEEN1000-ES02H.US [440V],N,98,N'
'Diehl AKO Stiftung 4301 S-A [240V],Y,94.5,N'
'Diehl AKO Stiftung Platinum 100 CS-A [480V],Y,94.5,N'
'Diehl AKO Stiftung Platinum 100 CS-A HE [208V],Y,95,N'
'Diehl AKO Stiftung Platinum 100 CS-A HE [480V],Y,95.5,N'
'Direct Grid Technologies DGM-460 [208V],N,92,N'
'Direct Grid Technologies DGM-S460 [240V],N,92.5,N'
'Dow Chemical 362589 (3.5 kW 2-string) [240V],N,94.5,N'
'Dow Chemical 362590 (3.5 kW 3-string) [240V],N,94,N'
'Dow Chemical 362591 (3.5 kW 4-string) [240V],N,94,N'
#REF!
#REF!
#REF!
'Dow Chemical 362592 (5.0 kW 2-string) [240V],N,95,N'
'Eaton PV238 [208V],Y,97,N'
'Eaton PV240 [208V],Y,97,N'
'Eaton PV238 [240V],Y,97,N'
'Eaton PV238 [277V],Y,97,N'
'Eaton PV240 [240V],Y,97,N'
'Eaton PV240 [277V],Y,97,N'
#REF!
'Eaton PV250 [208V],Y,97,N'
#REF!
'Eaton PV250 [240V],Y,97,N'
#REF!
'Eaton PV250 [277V],Y,97,N'
#REF!
'Eaton PV260 [277V],Y,97,N'
'Eaton PV270 [240V],Y,97,N'
'Eaton PV270 [277V],Y,97,N'
'Eaton Xpert1500,Y,98,N'
'Elettronica Santerno TG100NA208Y [208V],N,96,N'
'Elettronica Santerno TG125NA208Y [208V],Y,96,N'
'Eltek Theia 2.0He-t UL [208V],Y,96.5,N'
'Eltek Theia 2.9He-t UL [240V],Y,96.5,N'
'Eltek Theia 3.8He-t UL [208V],Y,96.5,N'
'Eltek Theia 4.4He-t UL [208V],Y,96.5,N'
'Emerson Network Power SPV-4.0AIUSO [240V],N,95,N'
'Emerson Network Power SPV-5.0AIUSO [240V],N,95,N'
'Enecsys SMI-240-60,N,93.5,Y'
'Enecsys 250NL,N,95.5,Y'
'Enecsys SMI-280-72,N,94.5,Y'
'Enecsys 300-60-xx,N,96,Y'
'Enecsys SMI-480-60,N,94.5,Y'
'Enphase Energy Inc. M175-24-208-Sxx [208V],N,94.5,Y'
'Enphase Energy Inc. M175-24-240-Sxx [240V],N,94.5,Y'
'Enphase Energy Inc. M190-72-208-Sxx [208V],N,95,Y'
'Enphase Energy Inc. M190-72-240-Sxx [240V],N,95,Y'
#REF!
'Enphase Energy Inc. M200-32-208-Sxx-NA [208V],N,95,Y'
'Enphase Energy Inc. M200-32-240-Sxx [240V],N,95,Y'
#REF!
#REF!
'Enphase Energy Inc. M210-84-208-Sxx [208V],N,95.5,Y'
#REF!
'Enphase Energy Inc. M210-84-208-Sxx-NA [208V],N,95.5,Y'
#REF!
'Enphase Energy Inc. M210-84-240-Sxx [240V],N,95.5,Y'
'Enphase Energy Inc. M210-84-240-Sxx-NA [240V],N,95.5,Y'
#REF!
'Enphase Energy Inc. M215-60-2LL-S2x [208V],N,96,Y'
'Enphase Energy Inc. M215-60-2LL-S2x [240V],N,96,Y'
#REF!
'Enphase Energy Inc. M215-60-2LL-S2x-IG [208V],N,96,Y'
'Enphase Energy Inc. M215-60-2LL-S2x-IG [240V],N,96,Y'
#REF!
'Enphase Energy Inc. M215-60-2LL-S2x-IG-NA [208V],N,96,Y'
'Enphase Energy Inc. M215-60-2LL-S2x-IG-NA [240V],N,96,Y'
#REF!
'Enphase Energy Inc. M215-60-2LL-S2x-IG-ZC [208V],N,96,Y'
'Enphase Energy Inc. M215-60-2LL-S2x-IG-ZC [240V],N,96,Y'
'Enphase Energy Inc. M215-60-2LL-S2x-IG-ZC-NA [208V],N,96,Y'
'Enphase Energy Inc. M215-60-2LL-S2x-IG-ZC-NA [240V],N,96,Y'
'Enphase Energy Inc. M215-60-2LL-S2x-NA [208V],N,96,Y'
'Enphase Energy Inc. M215-60-2LL-S2x-NA [240V],N,96,Y'
'Enphase Energy Inc. M215-60-2LL-S2x-ZC [240V],N,96,Y'
'Enphase Energy Inc. M215-60-2LL-S2x-ZC-NA [208V],N,96,Y'
'Enphase Energy Inc. M215-60-2LL-S2x-ZC-NA [240V],N,96,Y'
'Enphase Energy Inc. M215-60-SIE-S2x [208V],N,96,Y'
#REF!
'Enphase Energy Inc. M215-60-SIE-S2x [240V],N,96,Y'
#REF!
'Enphase Energy Inc. M215-60-SIE-S2x-NA [208V],N,96,Y'
#REF!
#REF!
#REF!
'Enphase Energy Inc. M215-60-SIE-S2x-NA [240V],N,96,Y'
#REF!
#REF!
#REF!
'Enphase Energy Inc. M215-60-SIE-S2x-ZC [208V],N,96,Y'
#REF!
#REF!
#REF!
'Enphase Energy Inc. M215-60-SIE-S2x-ZC [240V],N,96,Y'
#REF!
#REF!
'Enphase Energy Inc. M215-60-SIE-S2x-ZC-NA [208V],N,96,Y'
#REF!
#REF!
'Enphase Energy Inc. M215-60-SIE-S2x-ZC-NA [240V],N,96,Y'
#REF!
#REF!
'Enphase Energy Inc. S230-60-LL-x [208V],N,97,Y'
#REF!
#REF!
'Enphase Energy Inc. S230-60-LL-x [240V],N,97,Y'
#REF!
'Enphase Energy Inc. IQ6-60-ACM-US [208V],N,97,Y'
#REF!
'Enphase Energy Inc. IQ6-60-ACM-US [240V],N,97,Y'
#REF!
'Enphase Energy Inc. IQ6-60-x-US [208V],N,97,Y'
'Enphase Energy Inc. IQ6-60-x-US [240V],N,97,Y'
'Enphase Energy Inc. IQ7-60-x-ACM-US [208V],N,97,Y'
'Enphase Energy Inc. IQ7-60-x-ACM-US [240V],N,97,Y'
'Enphase Energy Inc. IQ7-60-x-US [208V],N,97,Y'
'Enphase Energy Inc. IQ7-60-x-US [240V],N,97,Y'
#REF!
'Enphase Energy Inc. M250-60-2LL-S2x (-ZC) (-NA) [208V],N,96,Y'
#REF!
'Enphase Energy Inc. M250-60-2LL-S2x (-ZC) (-NA) [240V],N,96.5,Y'
#REF!
'Enphase Energy Inc. M250-72-2LL-S2x [208V],N,96.5,Y'
#REF!
'Enphase Energy Inc. M250-72-2LL-S2x [240V],N,96.5,Y'
#REF!
'Enphase Energy Inc. C250-72-2LN-S2,N,96.5,Y'
#REF!
'Enphase Energy Inc. IQ6PLUS-ACB-LL [240V],N,95.5,Y'
#REF!
'Enphase Energy Inc. S280-60-LL-x [208V],N,96.5,Y'
#REF!
'Enphase Energy Inc. S280-60-LL-x [240V],N,97,Y'
#REF!
'Enphase Energy Inc. IQ6PLUS-72-ACM-US [208V],N,97,Y'
#REF!
'Enphase Energy Inc. IQ6PLUS-72-ACM-US [240V],N,97,Y'
#REF!
'Enphase Energy Inc. IQ6PLUS-72-x-US [208V],N,97,Y'
#REF!
'Enphase Energy Inc. IQ6PLUS-72-x-US [240V],N,97,Y'
#REF!
'Enphase Energy Inc. IQ7PLUS-72-x-ACM-US [208V],N,96.5,Y'
#REF!
'Enphase Energy Inc. IQ7PLUS-72-x-ACM-US [240V],N,97,Y'
#REF!
'Enphase Energy Inc. IQ7PLUS-72-x-US [208V],N,96.5,Y'
#REF!
'Enphase Energy Inc. IQ7PLUS-72-x-US [240V],N,97,Y'
#REF!
'Enphase Energy Inc. IQ7AS-66-ACM-US-x [208V],N,96.5,Y'
'Enphase Energy Inc. IQ7X-96-x-ACM-US [208V],N,97,Y'
'Enphase Energy Inc. IQ7X-96-x-ACM-US [240V],N,97.5,Y'
'Enphase Energy Inc. IQ7X-96-x-US [208V],N,97,Y'
'Enphase Energy Inc. IQ7X-96-x-US [240V],N,97.5,Y'
'Enphase Energy Inc. IQ7XS-96-y-ACM-z [208V],N,97,Y'
'Enphase Energy Inc. IQ7XS-96-y-ACM-z [240V],N,97.5,Y'
'Enphase Energy Inc. IQ7AS-66-ACM-US-x [240V],N,97,Y'
'Enphase Energy Inc. D380-72-208-S1x [208V],N,95,Y'
'Enphase Energy Inc. D380-72-240-S1x [240V],N,95,Y'
'Enphase Energy Inc. D380-72-2LL-S1x [208V],N,95,Y'
'Enphase Energy Inc. D380-72-2LL-S1x [240V],N,95,Y'
'Enphase Energy Inc. D380-72-2LL-S1x-NA [208V],N,95,Y'
'Enphase Energy Inc. D380-72-2LL-S1x-NA [240V],N,95,Y'
'Eoplly New Energy Technology EP156M/60-230S AC [208V],N,96,Y'
'Eoplly New Energy Technology EP156M/60-230S AC [240V],N,96,Y'
'Eoplly New Energy Technology EP156M/60-235S AC [208V],N,96,Y'
'Eoplly New Energy Technology EP156M/60-235S AC [240V],N,96,Y'
'Eoplly New Energy Technology EP156M/60-240S AC [208V],N,96,Y'
'Eoplly New Energy Technology EP156M/60-240S AC [240V],N,96,Y'
'Eoplly New Energy Technology EP156M/60-245S AC [208V],N,96,Y'
'Eoplly New Energy Technology EP156M/60-245S AC [240V],N,96,Y'
'Eoplly New Energy Technology EP156M/60-250S AC [208V],N,96,Y'
'Eoplly New Energy Technology EP156M/60-250S AC [240V],N,96,Y'
'Eoplly New Energy Technology EP156M/60-255S AC [208V],N,96,Y'
'Eoplly New Energy Technology EP156M/60-255S AC [240V],N,96,Y'
'Eoplly New Energy Technology EP156M/60-260S AC [208V],N,96,Y'
'Eoplly New Energy Technology EP156M/60-260S AC [240V],N,96,Y'
'Eoplly New Energy Technology EP156MB/60-230S AC [208V],N,96,Y'
'Eoplly New Energy Technology EP156MB/60-230S AC [240V],N,96,Y'
'Eoplly New Energy Technology EP156MB/60-235S AC [208V],N,96,Y'
'Eoplly New Energy Technology EP156MB/60-235S AC [240V],N,96,Y'
'Eoplly New Energy Technology EP156MB/60-240S AC [208V],N,96,Y'
'Eoplly New Energy Technology EP156MB/60-240S AC [240V],N,96,Y'
'Eoplly New Energy Technology EP156MB/60-245S AC [208V],N,96,Y'
'Eoplly New Energy Technology EP156MB/60-245S AC [240V],N,96,Y'
'Eoplly New Energy Technology EP156MB/60-250S AC [208V],N,96,Y'
'Eoplly New Energy Technology EP156MB/60-250S AC [240V],N,96,Y'
'Eoplly New Energy Technology EP156P/60-225S AC [208V],N,96,Y'
'Eoplly New Energy Technology EP156P/60-225S AC [240V],N,96,Y'
'Eoplly New Energy Technology EP156P/60-230S AC [208V],N,96,Y'
'Eoplly New Energy Technology EP156P/60-230S AC [240V],N,96,Y'
'Eoplly New Energy Technology EP156P/60-235S AC [208V],N,96,Y'
'Eoplly New Energy Technology EP156P/60-235S AC [240V],N,96,Y'
'Eoplly New Energy Technology EP156P/60-240S AC [208V],N,96,Y'
'Eoplly New Energy Technology EP156P/60-240S AC [240V],N,96,Y'
'Eoplly New Energy Technology EP156P/60-245S AC [208V],N,96,Y'
'Eoplly New Energy Technology EP156P/60-245S AC [240V],N,96,Y'
'Eoplly New Energy Technology EP156P/60-250S AC [208V],N,96,Y'
'Eoplly New Energy Technology EP156P/60-250S AC [240V],N,96,Y'
'Eoplly New Energy Technology EP156P/60-255S AC [208V],N,96,Y'
'Eoplly New Energy Technology EP156P/60-255S AC [240V],N,96,Y'
'Eoplly New Energy Technology EP156P/60-260S AC [208V],N,96,Y'
'Eoplly New Energy Technology EP156P/60-260S AC [240V],N,96,Y'
'Eoplly New Energy Technology EP156M/60-250 AC [208V],N,95,Y'
'Eoplly New Energy Technology EP156M/60-250 AC [240V],N,95,Y'
'Eoplly New Energy Technology EP156M/60-255 AC [208V],N,95,Y'
'Eoplly New Energy Technology EP156M/60-255 AC [240V],N,95,Y'
'Eoplly New Energy Technology EP156M/60-260 AC [208V],N,95,Y'
'Eoplly New Energy Technology EP156M/60-260 AC [240V],N,95,Y'
'Eoplly New Energy Technology EP156MB/60-240 AC [208V],N,95,Y'
'Eoplly New Energy Technology EP156MB/60-240 AC [240V],N,95,Y'
'Eoplly New Energy Technology EP156MB/60-245 AC [208V],N,95,Y'
'Eoplly New Energy Technology EP156MB/60-245 AC [240V],N,95,Y'
'Eoplly New Energy Technology EP156P/60-240 AC [208V],N,95,Y'
'Eoplly New Energy Technology EP156P/60-240 AC [240V],N,95,Y'
'Eoplly New Energy Technology EP156P/60-245 AC [208V],N,95,Y'
'Eoplly New Energy Technology EP156P/60-245 AC [240V],N,95,Y'
'ET Solar Industry ET-P660245BAC [240V],N,95,Y'
'ET Solar Industry ET-P660245BBAC [240V],N,95,Y'
'ET Solar Industry ET-P660245BBZAC [240V],N,95,Y'
'ET Solar Industry ET-P660245WBZAC [240V],N,95,Y'
'ET Solar Industry ET-P660250 WBAC [240V],N,95,Y'
'ET Solar Industry ET-P660250 WBZAC [240V],N,95,Y'
'ET Solar Industry ET-P660250BAC [240V],N,95,Y'
'ET Solar Industry ET-P660250BBAC [240V],N,95,Y'
'ET Solar Industry ET-P660250BBZAC [240V],N,95,Y'
'ET Solar Industry ET-P660255BBAC,N,95,Y'
'ET Solar Industry ET-P660255BBZAC,N,95,Y'
'ET Solar Industry ET-P660255WBAC,N,95,Y'
'ET Solar Industry ET-P660255WBZAC,N,95,Y'
'ET Solar Industry ET-P660255WWAC,N,95,Y'
'ET Solar Industry ET-P660255WWZAC,N,95,Y'
'ET Solar Industry ET-P660260WBZAC,N,95,Y'
'ET Solar Industry ET-P660260WWAC,N,95,Y'
'ET Solar Industry ET-P660260WWZAC,N,95,Y'
'ETM Electromatic 290-480-60,Y,96.5,N'
#REF!
'E-Village Solar EVS1100EVR [120V],Y,90.5,N'
'E-Village Solar EVS2000EVR [240V],Y,92,N'
'E-Village Solar EVS2500 [240V],Y,94.5,N'
'E-Village Solar EVS3000 [240V],Y,93.5,N'
'E-Village Solar EVS3500 [240V],Y,95.5,N'
'E-Village Solar EVS4600 [208V],Y,95.5,N'
'E-Village Solar EVS4800 [240V],Y,96,N'
'E-Village Solar EVS5200 [208V],Y,96,N'
'Exeltech AC2-1-2-6-5-XX [120V],N,94.5,Y'
'Exeltech AC2-1-B-6-5-XX [120V],N,94.5,Y'
'Exeltech AC2-1-C-6-5-XX [120V],N,94.5,Y'
'Exeltech AC2-1-L-6-5-XX [120V],N,94.5,Y'
'Exeltech AM24-1-B-6-0-00 [120V],N,94.5,Y'
'Exeltech XLGT18A60 [120V],Y,96.5,N'
'Exeltech XLGT18A60-01 [120V],Y,96.5,N'
'Flextronics Industrial FLV-IA-6.0S1UA,Y,97.5,N'
'Flextronics Industrial FLV-IA-7.0S1UA,Y,97.5,N'
'Flextronics Industrial FLV-IA-7.6S1UA,Y,97.5,N'
'Flextronics Industrial FLV-IA-8.0S1UA,Y,97.5,N'
'Flextronics Industrial FLV-IA-9.0S1UA,Y,97.5,N'
#REF!
#REF!
#REF!
#REF!
#REF!
#REF!
#REF!
#REF!
#REF!
#REF!
#REF!
#REF!
#REF!
#REF!
#REF!
#REF!
#REF!
#REF!
#REF!
#REF!
#REF!
#REF!
#REF!
#REF!
#REF!
#REF!
#REF!
#REF!
#REF!
#REF!
#REF!
#REF!
#REF!
'Flextronics Industrial FLV-IA-10.0S1UA,Y,97.5,N'
'Friem RECon 30L-100-US,Y,98,N'
'Friem RECon 30H-150-US [300V],Y,98,N'
'Fronius USA Galvo 1.5-1 208-240 [208V],Y,94,N'
'Fronius USA Galvo 1.5-1 208-240 [240V],Y,94.5,N'
'Fronius USA Galvo 2.0-1 208-240 [208V],Y,94.5,N'
'Fronius USA Galvo 2.0-1 208-240 [240V],Y,94.5,N'
'Fronius USA IG 2000 NEG,Y,93.5,N'
'Fronius USA IG 2000 POS,Y,93.5,N'
'Fronius USA IG 2500-LV NEG,Y,93,N'
'Fronius USA IG 2500-LV POS,Y,93,N'
'Fronius USA Galvo 2.5-1 208-240 [208V],Y,95,N'
'Fronius USA Galvo 2.5-1 208-240 [240V],Y,95,N'
'Fronius USA IG 3000 NEG,Y,94,N'
'Fronius USA IG 3000 POS,Y,94,N'
'Fronius USA Galvo 3.1-1 208-240 [208V],Y,95,N'
'Fronius USA IG Plus 3.0-1 UNI [208V],Y,95,N'
'Fronius USA IG Plus 3.0-1 UNI [240V],Y,95.5,N'
'Fronius USA IG Plus 3.0-1 UNI [277V],Y,95.5,N'
'Fronius USA IG Plus A 3.0 [208V],Y,95,N'
'Fronius USA IG Plus A 3.0 [240V],Y,95.5,N'
'Fronius USA IG Plus A 3.0 [277V],Y,96,N'
'Fronius USA IG Plus V 3.0 [208V],Y,95,N'
'Fronius USA IG Plus V 3.0 [240V],Y,95.5,N'
'Fronius USA IG Plus V 3.0 [277V],Y,96,N'
'Fronius USA Galvo 3.1-1 208-240 [240V],Y,95.5,N'
'Fronius USA Fronius Primo 3.8-1 208-240 [208V],Y,96,N'
'Fronius USA Fronius Primo 3.8-1 208-240 [240V],Y,95.5,N'
'Fronius USA IG Plus 3.8-1 UNI [208V],Y,95,N'
'Fronius USA IG Plus 3.8-1 UNI [240V],Y,95.5,N'
'Fronius USA IG Plus 3.8-1 UNI [277V],Y,95.5,N'
'Fronius USA IG Plus A 3.8 [208V],Y,95,N'
'Fronius USA IG Plus A 3.8 [240V],Y,95.5,N'
'Fronius USA IG Plus A 3.8 [277V],Y,96,N'
'Fronius USA IG Plus V 3.8 [208V],Y,95,N'
'Fronius USA IG Plus V 3.8 [240V],Y,95.5,N'
'Fronius USA IG Plus V 3.8 [277V],Y,96,N'
'Fronius USA IG 4000 NEG,Y,94,N'
'Fronius USA IG 4000 POS,Y,94,N'
'Fronius USA IG 4500-LV NEG,Y,93.5,N'
'Fronius USA IG 4500-LV POS,Y,93.5,N'
'Fronius USA Fronius Primo 5.0-1 208-240 [208V],Y,96.5,N'
'Fronius USA Fronius Primo 5.0-1 208-240 [240V],Y,96.5,N'
'Fronius USA IG Plus 5.0-1 UNI [208V],Y,95.5,N'
'Fronius USA IG Plus 5.0-1 UNI [240V],Y,95.5,N'
'Fronius USA IG Plus 5.0-1 UNI [277V],Y,96,N'
'Fronius USA IG Plus A 5.0 [208V],Y,95.5,N'
'Fronius USA IG Plus A 5.0 [240V],Y,95.5,N'
'Fronius USA IG Plus A 5.0 [277V],Y,96,N'
'Fronius USA IG Plus V 5.0 [208V],Y,95.5,N'
'Fronius USA IG Plus V 5.0 [240V],Y,95.5,N'
'Fronius USA IG Plus V 5.0 [277V],Y,96,N'
'Fronius USA IG 5100 NEG,Y,94.5,N'
'Fronius USA IG 5100 POS,Y,94.5,N'
'Fronius USA Fronius Primo 6.0-1 208-240 [208V],Y,96.5,N'
'Fronius USA Fronius Primo 6.0-1 208-240 [240V],Y,96.5,N'
'Fronius USA IG Plus 6.0-1 UNI [208V],Y,95.5,N'
'Fronius USA IG Plus 6.0-1 UNI [240V],Y,96,N'
'Fronius USA IG Plus 6.0-1 UNI [277V],Y,96,N'
'Fronius USA IG Plus A 6.0 [208V],Y,95.5,N'
'Fronius USA IG Plus A 6.0 [240V],Y,96,N'
'Fronius USA IG Plus A 6.0 [277V],Y,96,N'
'Fronius USA IG Plus V 6.0 [208V],Y,95.5,N'
'Fronius USA IG Plus V 6.0 [240V],Y,96,N'
'Fronius USA IG Plus V 6.0 [277V],Y,96,N'
'Fronius USA IG Plus 7.5-1 UNI [208V],Y,95,N'
'Fronius USA IG Plus 7.5-1 UNI [240V],Y,95.5,N'
'Fronius USA IG Plus 7.5-1 UNI [277V],Y,96,N'
'Fronius USA IG Plus A 7.5 [208V],Y,95,N'
'Fronius USA IG Plus A 7.5 [240V],Y,95.5,N'
'Fronius USA IG Plus A 7.5 [277V],Y,96,N'
'Fronius USA IG Plus V 7.5 [208V],Y,95,N'
'Fronius USA IG Plus V 7.5 [240V],Y,95.5,N'
'Fronius USA IG Plus V 7.5 [277V],Y,96,N'
'Fronius USA Fronius Primo 7.6-1 208-240 [208V],Y,97,N'
'Fronius USA Fronius Primo 7.6-1 208-240 [240V],Y,97,N'
'Fronius USA Fronius Primo 8.2-1 208-240 [208V],Y,97,N'
'Fronius USA Fronius Primo 8.2-1 208-240 [240V],Y,97,N'
'Fronius USA Fronius Primo 10.0-1 [208V],Y,96.5,N'
'Fronius USA Fronius Primo 10.0-1 [240V],Y,96.5,N'
'Fronius USA Fronius Symo 10.0-3 208-240 [208V],Y,96.5,N'
'Fronius USA Fronius Symo 10.0-3 208-240 [240V],Y,96.5,N'
'Fronius USA Fronius Symo 10.0-3 480 [480V],Y,96.5,N'
'Fronius USA IG Plus 10.0-1 UNI [208V],Y,95,N'
'Fronius USA IG Plus 10.0-1 UNI [240V],Y,95.5,N'
'Fronius USA IG Plus 10.0-1 UNI [277V],Y,96,N'
'Fronius USA IG Plus V 10.0-3 Delta [208V],Y,95.5,N'
'Fronius USA IG Plus V 10.0-3 Delta [240V],Y,95.5,N'
'Fronius USA IG Plus A 10.0 [208V],Y,95,N'
'Fronius USA IG Plus A 10.0 [240V],Y,95.5,N'
'Fronius USA IG Plus A 10.0 [277V],Y,96,N'
'Fronius USA IG Plus A 10.0-3 Delta [208V],Y,95.5,N'
'Fronius USA IG Plus A 10.0-3 Delta [240V],Y,95.5,N'
'Fronius USA IG Plus V 10.0 [208V],Y,95,N'
'Fronius USA IG Plus V 10.0 [240V],Y,95.5,N'
'Fronius USA IG Plus V 10.0 [277V],Y,96,N'
'Fronius USA Fronius Primo 11.4-1 [208V],Y,96.5,N'
'Fronius USA Fronius Primo 11.4-1 [240V],Y,96.5,N'
'Fronius USA IG Plus 11.4-1 UNI [208V],Y,95.5,N'
'Fronius USA IG Plus 11.4-1 UNI [240V],Y,96,N'
'Fronius USA IG Plus 11.4-1 UNI [277V],Y,96,N'
'Fronius USA IG Plus 11.4-3 Delta [208V],Y,95,N'
'Fronius USA IG Plus 11.4-3 Delta [240V],Y,95.5,N'
'Fronius USA IG Plus A 11.4 [208V],Y,95,N'
'Fronius USA IG Plus A 11.4 [240V],Y,95.5,N'
'Fronius USA IG Plus A 11.4 [277V],Y,96,N'
'Fronius USA IG Plus A 11.4-3 Delta [208V],Y,95,N'
'Fronius USA IG Plus A 11.4-3 Delta [240V],Y,96,N'
'Fronius USA IG Plus V 11.4 [208V],Y,95,N'
'Fronius USA IG Plus V 11.4 [240V],Y,95.5,N'
'Fronius USA IG Plus V 11.4 [277V],Y,96,N'
'Fronius USA IG Plus V 11.4-3 Delta [208V],Y,95,N'
'Fronius USA IG Plus V 11.4-3 Delta [240V],Y,96,N'
'Fronius USA Fronius Symo 12.0-3 208-240 [208V],Y,96.5,N'
'Fronius USA Fronius Symo 12.0-3 208-240 [240V],Y,96.5,N'
'Fronius USA IG Plus 12.0-3 WYE [277V],Y,96,N'
'Fronius USA IG Plus A 12.0-3 WYE [277V],Y,96,N'
'Fronius USA IG Plus V 12.0-3 WYE [277V],Y,96,N'
'Fronius USA Fronius Primo 12.5-1 [208V],Y,96.5,N'
'Fronius USA Fronius Primo 12.5-1 [240V],Y,96.5,N'
'Fronius USA Fronius Symo 12.5-3 480 [480V],Y,97,N'
'Fronius USA Fronius Primo 15.0-1 [208V],Y,97,N'
'Fronius USA Fronius Primo 15.0-1 [240V],Y,97,N'
'Fronius USA Fronius Symo 15.0-3 [208V],Y,96.5,N'
'Fronius USA Fronius Symo 15.0-3 480 [480V],Y,97,N'
'Fronius USA Fronius Symo 17.5-3 480 [480V],Y,97.5,N'
'Fronius USA Fronius Symo 20.0-3 480 [480V],Y,97,N'
'Fronius USA Fronius Symo 22.7-3 480 [480V],Y,97.5,N'
'Fronius USA Fronius Symo 24.0-3 480 [480V],Y,97.5,N'
'Fronius USA CL 33.3 Delta [208V],Y,94.5,N'
'Fronius USA CL 33.3 Delta [240V],Y,95,N'
'Fronius USA CL 36.0 Wye [277V],Y,95.5,N'
'Fronius USA CL 44.4 Delta [208V],Y,94.5,N'
'Fronius USA CL 44.4 Delta [240V],Y,95,N'
'Fronius USA CL 48.0 Wye [277V],Y,95.5,N'
'Fronius USA CL 55.5 Delta [208V],Y,94.5,N'
'Fronius USA CL 55.5 Delta [240V],Y,95,N'
'Fronius USA CL 60.0 Wye [277V],Y,95.5,N'
'FSP Group FSP600PV-NA-208 [208V],N,95,Y'
'FSP Group FSP600PV-NA-240 [240V],N,95,Y'
'FSP Group FSP600PV-NA-277 [277V],N,95,Y'
'GAF RIAC 1000 [208V],N,96,Y'
'GAF RIAC 1000 [240V],N,96,Y'
'GE Energy GEPVe-1100-NA-120 [120V],Y,90.5,N'
'GE Energy GEPVe-2000-NA-240 [240V],Y,92,N'
'GE Energy GEPVb-2500-NA-240 [240V],Y,94,N'
'GE Energy GEPVe-2500-NA-240 [240V],Y,94.5,N'
'GE Energy GEPVb-2800-NA-240/208-02 [208V],Y,93.5,N'
'GE Energy GEPVb-2800-NA-240/208-02 [240V],Y,94,N'
'GE Energy GEPVe-2800-NA-208 [208V],Y,92,N'
'GE Energy GEPVb-3000-NA-240 [240V],Y,94.5,N'
'GE Energy GEPVe-3000-NA-240 [240V],Y,93.5,N'
'GE Energy GEPVb-3300-NA-240/208-02 [208V],Y,95,N'
'GE Energy GEPVb-3300-NA-208 [208V],Y,94,N'
'GE Energy GEPVb-3300-NA-240 [240V],Y,94.5,N'
'GE Energy GEPVb-3300-NA-240/208-02 [240V],Y,95.5,N'
'GE Energy GEPVe-3500-NA-240 [240V],Y,95.5,N'
'GE Energy GEPVb-3800-NA-240 [240V],Y,95,N'
'GE Energy GEPVb-4000-NA-240/208-02 [208V],Y,95,N'
'GE Energy GEPVb-4000-NA-240/208-02 [240V],Y,95.5,N'
'GE Energy GEPVb-5000-NA-240/208-02 [208V],Y,95,N'
'GE Energy GEPVe-4600-NA-208 [208V],Y,95.5,N'
'GE Energy GEPVe-4800-NA-240 [240V],Y,96,N'
'GE Energy GEPVb-5000-NA-240/208-02 [240V],Y,95.5,N'
'GE Energy GEPVb-5000-NA-240-01 [240V],Y,95.5,N'
'Gefran APV 1700-2M-TL-US [208V],Y,96,N'
'Gefran APV 1700-2M-TL-US [277V],Y,96,N'
'Gefran APV 2300-2M-TL-US [240V],Y,96.5,N'
'Gefran APV 3100-2M-TL-US [208V],Y,96.5,N'
'Gefran APV 3100-2M-TL-US [277V],Y,96.5,N'
'Gefran APV 3800-2M-TL-US [240V],Y,97,N'
'Gefran APV 4400-2M-TL-US [208V],Y,97,N'
'Gefran APV 4400-2M-TL-US [277V],Y,97,N'
'Gefran APV 5200-2M-TL-US [240V],Y,97,N'
'General Electric PVIA2000NA1240 [240V],Y,94.5,N'
'General Electric PVIA4000NA1240 [240V],Y,95.5,N'
'Geoprotek Technology GS-1000 [208V],Y,94.5,N'
'Geoprotek Technology GS-1500 [208V],Y,94.5,N'
'Geoprotek Technology GS-2000 [208V],Y,95.5,N'
'Geoprotek Technology GS-3000 [208V],Y,95.5,N'
'Geoprotek Technology GS-3000 [240V],Y,95.5,N'
'Green Power Technologies PV500U + MVT,Y,96,N'
'Green Power Technologies PV500WD,N,96,N'
'Green Power Technologies PV630WD,N,96.5,N'
'Green Power Technologies PV750WD,N,97,N'
'Green Power Technologies 940WD3-LV400 [400V],N,97,N'
'Green Power Technologies PV900WD,N,97,N'
'Green Power Technologies 1170WD3-LV500 [500V],N,97.5,N'
'Green Power Technologies 1140WD3-HV560 [560V],N,97.5,N'
'Green Power Technologies 1260WD3-HV620 [620V],N,97.5,N'
'Green Power Technologies 1400WD3-HV690 [690V],N,98,N'
'GreenVolts GV-SCP001 [480V],Y,96,N'
'GridPoint Connect C36,N,91,N'
'Hansol Technics HSPV-A250,N,93,N'
'Heart Transverter HT2000,Y,89,N'
'Helios USA 6TA [120V],N,94.5,N'
#REF!
'HiQ Solar Mini3500-US,N,94.5,N'
'HiQ Solar TS208-5k75 [208V],Y,97,N'
'HiQ Solar TS480-8k [480V],Y,98,N'
'HiQ Solar TSXL480-10k [480V],N,97.5,N'
'HiSEL Power HiSEL-K 1500 [208V],Y,95,N'
'HiSEL Power HiSEL-K 1500 [240V],Y,95,N'
'HiSEL Power HiSEL-K 2000 [208V],Y,95.5,N'
'HiSEL Power HiSEL-K 2000 [240V],Y,96,N'
'HiSEL Power HiSEL-K 3000 [208V],Y,96,N'
'HiSEL Power HiSEL-K 3000 [240V],Y,96,N'
'HiSEL Power HiSEL-K 4000 [208V],Y,97,N'
'HiSEL Power HiSEL-K 4000 [240V],Y,97.5,N'
'HiSEL Power HiSEL-K 5000 [208V],Y,97,N'
'HiSEL Power HiSEL-K 5000 [240V],Y,97.5,N'
'Home Director HD-SUN-INV1100-EVR [120V],Y,90.5,N'
'Home Director HD-SUN-INV2000-EVR [240V],Y,92,N'
'Home Director HD-SUN-INV2500 [240V],Y,94.5,N'
'Home Director HD-SUN-INV3000 [240V],Y,93.5,N'
'Home Director HD-SUN-INV3500 [240V],Y,95.5,N'
'Home Director HD-SUN-INV5200 [240V],Y,96,N'
'Hoymiles Converter Technology MI-250 [240V],N,96.5,Y'
'Hoymiles Converter Technology Co., Ltd. MI-1200 [240V],N,96.5,Y'
'Hoymiles Converter Technology Co., Ltd. MI-1200T [240V],N,96.5,Y'
'Huawei Technologies Co., Ltd. SUN2000-3.8KTL-USL0 [240V],Y,99,N'
'Huawei Technologies Co., Ltd. SUN2000-5KTL-USL0 [240V],Y,99,N'
'Huawei Technologies Co., Ltd. SUN2000-7.6KTL-USL0 [240V],Y,99,N'
'Huawei Technologies Co., Ltd. SUN2000-9KTL-USL0 [240V],Y,99,N'
'Huawei Technologies Co., Ltd. SUN2000-10KTL-USL0 [240V],Y,99,N'
'Huawei Technologies Co., Ltd. SUN2000-11.4KTL-USL0 [240V],Y,99,N'
#REF!
'Huawei Technologies Co., Ltd. SUN2000-22KTL-US,N,98,N'
#REF!
'Huawei Technologies Co., Ltd. SUN2000-25KTL-US,Y,98,N'
#REF!
#REF!
#REF!
#REF!
'Huawei Technologies Co., Ltd. SUN2000-30KTL-US,Y,98,N'
#REF!
#REF!
'Huawei Technologies Co., Ltd. SUN2000-33KTL-US,N,98.5,N'
'Huawei Technologies Co., Ltd. SUN2000-36KTL-US,N,98.5,N'
'Huawei Technologies Co., Ltd. SUN2000-40KTL-US,N,98.5,N'
'Huawei Technologies Co., Ltd. SUN2000-45KTL-US-HV-D0,N,98.5,N'
'Huawei Technologies Co., Ltd. SUN2000-100KTL-USH0 [800V],N,98.5,N'
'HYOSUNG HS-P1000GLO-U,N,98,N'
'Ideal Power Inc 30C [480V],N,95,N'
'Ideal Power Inc 30C3 [480V],N,95,N'
'Ideal Power Inc 30PV,N,95,N'
'Ideal Power Inc 30PV+S [480V],N,95,N'
'Ideal Power Inc 30PVF,N,95,N'
'Ideal Power Inc 30PVF+S [480V],N,95,N'
'Ideal Power Inc IPV-30 kW-480 [480V],Y,96.5,N'
'i-Energy GT260 [240V],N,92,N'
'INGETEAM POWER TECHNOLOGY S.A INGECON SUN 1140TL U B410 [410V],N,97.5,N'
'INGETEAM POWER TECHNOLOGY S.A INGECON SUN 1245TL U B480 [480V],N,97.5,N'
'INGETEAM POWER TECHNOLOGY S.A INGECON SUN 1190TL U B430 [430V],N,97.5,N'
'INGETEAM POWER TECHNOLOGY S.A INGECON SUN 1220TL U B440 [440V],N,97.5,N'
'INGETEAM POWER TECHNOLOGY S.A INGECON SUN 1250TL U B450 [450V],N,97.5,N'
'INGETEAM POWER TECHNOLOGY S.A INGECON SUN 1275TL U B460 [460V],N,97.5,N'
'INGETEAM POWER TECHNOLOGY S.A INGECON SUN 1740TL U B670 [670V],N,97.5,N'
'INGETEAM POWER TECHNOLOGY S.A INGECON SUN 1800TL U B690 [690V],N,97.5,N'
'INGETEAM POWER TECHNOLOGY S.A INGECON SUN 1665TL U B640 [640V],N,97.5,N'
'INGETEAM POWER TECHNOLOGY S.A INGECON SUN 1690TL U B650 [650V],N,97.5,N'
'INGETEAM POWER TECHNOLOGY S.A INGECON SUN 1715TL U B660 [660V],N,97.5,N'
'INGETEAM POWER TECHNOLOGY S.A. Ingecon Sun 2.8 HF U 208 Vac [208V],Y,95,N'
'INGETEAM POWER TECHNOLOGY S.A. Ingecon Sun 2.8 HF U 240 Vac [240V],Y,95.5,N'
'INGETEAM POWER TECHNOLOGY S.A. Ingecon Sun 2.8 HF U 277Vac [277V],Y,95.5,N'
'INGETEAM POWER TECHNOLOGY S.A. Ingecon Sun 2.8 TL U M 208 Vac [208V],Y,97,N'
#REF!
'INGETEAM POWER TECHNOLOGY S.A. Ingecon Sun 3.3 HF U 208 Vac [208V],Y,95,N'
#REF!
'INGETEAM POWER TECHNOLOGY S.A. Ingecon Sun 3.3 HF U 240 Vac [240V],Y,95.5,N'
#REF!
'INGETEAM POWER TECHNOLOGY S.A. Ingecon Sun 3.3 HF U 277Vac [277V],Y,95.5,N'
#REF!
'INGETEAM POWER TECHNOLOGY S.A. Ingecon Sun 3.3 TL U M 208 Vac [208V],Y,97.5,N'
#REF!
'INGETEAM POWER TECHNOLOGY S.A. Ingecon Sun 3.3 TL U M 240 Vac [240V],Y,97.5,N'
#REF!
'INGETEAM POWER TECHNOLOGY S.A. INGECON SUN 3.6TL U 208V [208V],Y,96,N'
'INGETEAM POWER TECHNOLOGY S.A. INGECON SUN 3.6TL U 240V [240V],Y,96.5,N'
'INGETEAM POWER TECHNOLOGY S.A. INGECON SUN 3.6TL U 277 [277V],Y,96.5,N'
'INGETEAM POWER TECHNOLOGY S.A. Ingecon Sun 5 HF U 208 Vac [208V],Y,95,N'
'INGETEAM POWER TECHNOLOGY S.A. Ingecon Sun 5 HF U 240 Vac [240V],Y,96,N'
'INGETEAM POWER TECHNOLOGY S.A. Ingecon Sun 5 HF U 277Vac [277V],Y,95.5,N'
'INGETEAM POWER TECHNOLOGY S.A. Ingecon Sun 5 TL U M 208 Vac [208V],Y,97.5,N'
'INGETEAM POWER TECHNOLOGY S.A. Ingecon Sun 5 TL U M 240 Vac [240V],Y,97.5,N'
'INGETEAM POWER TECHNOLOGY S.A. Ingecon Sun 5TL U [208V],Y,96,N'
'INGETEAM POWER TECHNOLOGY S.A. Ingecon Sun 5TL U [240V],Y,96,N'
'INGETEAM POWER TECHNOLOGY S.A. Ingecon Sun 5TL U [277V],Y,96,N'
'INGETEAM POWER TECHNOLOGY S.A. Ingecon Sun 5U [208V],Y,95,N'
'INGETEAM POWER TECHNOLOGY S.A. Ingecon Sun 5U [240V],Y,95,N'
'INGETEAM POWER TECHNOLOGY S.A. Ingecon Sun 5U [277V],Y,95.5,N'
#REF!
'INGETEAM POWER TECHNOLOGY S.A. Ingecon Sun 6 HF U 240 Vac [240V],Y,95.5,N'
#REF!
'INGETEAM POWER TECHNOLOGY S.A. Ingecon Sun 6 HF U 277Vac [277V],Y,95,N'
'INGETEAM POWER TECHNOLOGY S.A. Ingecon Sun 6 TL U M 240 Vac [240V],Y,98,N'
#REF!
'INGETEAM POWER TECHNOLOGY S.A. INGECON SUN 6TL U 240 [240V],Y,96.5,N'
'INGETEAM POWER TECHNOLOGY S.A. INGECON SUN 6TL U 277V [277V],Y,97,N'
#REF!
'INGETEAM POWER TECHNOLOGY S.A. INGECON SUN 7.5TL U 208 [208V],Y,96.5,N'
'INGETEAM POWER TECHNOLOGY S.A. INGECON SUN 7.5TL U 240 [240V],Y,96.5,N'
'INGETEAM POWER TECHNOLOGY S.A. INGECON SUN 8.6TL U 240 [240V],Y,96.5,N'
'INGETEAM POWER TECHNOLOGY S.A. INGECON SUN 8.6TL U 277 [277V],Y,97,N'
'INGETEAM POWER TECHNOLOGY S.A. Ingecon Sun 15U [208V],Y,95,N'
'INGETEAM POWER TECHNOLOGY S.A. Ingecon Sun 15U [480V],Y,95,N'
'INGETEAM POWER TECHNOLOGY S.A. Ingecon Sun 18 TL U M [480V],Y,98,N'
'INGETEAM POWER TECHNOLOGY S.A. Ingecon Sun 24 TL U M [480V],Y,98,N'
'INGETEAM POWER TECHNOLOGY S.A. Ingecon Sun 25U [208V],Y,95.5,N'
'INGETEAM POWER TECHNOLOGY S.A. Ingecon Sun 25U [480V],Y,95.5,N'
'INGETEAM POWER TECHNOLOGY S.A. Ingecon Sun 40TL U M [480V],Y,98,N'
'INGETEAM POWER TECHNOLOGY S.A. Ingecon Sun 100U [208V],Y,94.5,N'
'INGETEAM POWER TECHNOLOGY S.A. Ingecon Sun 100U [240V],Y,94.5,N'
'INGETEAM POWER TECHNOLOGY S.A. Ingecon Sun 100UP [208V],Y,95,N'
'INGETEAM POWER TECHNOLOGY S.A. Ingecon Sun 100UP [480V],Y,95.5,N'
'INGETEAM POWER TECHNOLOGY S.A. INGECON SUN 125 TL U 208 Outdoor [208V],Y,96.5,N'
'INGETEAM POWER TECHNOLOGY S.A. INGECON SUN 125 U 208 Outdoor [208V],Y,96.5,N'
'INGETEAM POWER TECHNOLOGY S.A. INGECON SUN 125 U 480 Outdoor [480V],Y,96.5,N'
'INGETEAM POWER TECHNOLOGY S.A. INGECON SUN 165 TL U 275 Outdoor [275V],Y,97,N'
'INGETEAM POWER TECHNOLOGY S.A. INGECON SUN 200 TL U 330 Outdoor [330V],Y,97.5,N'
'INGETEAM POWER TECHNOLOGY S.A. INGECON SUN 220 TL U 360 Outdoor [360V],Y,97.5,N'
'INGETEAM POWER TECHNOLOGY S.A. INGECON SUN 375TL X208 Indoor [208V],Y,96.5,N'
'INGETEAM POWER TECHNOLOGY S.A. INGECON SUN 375TL X208 Outdoor [208V],Y,96.5,N'
'INGETEAM POWER TECHNOLOGY S.A. INGECON SUN 500T U X480 Indoor [208V],Y,96.5,N'
'INGETEAM POWER TECHNOLOGY S.A. INGECON SUN 500T U X480 Outdoor [208V],Y,96.5,N'
'INGETEAM POWER TECHNOLOGY S.A. INGECON SUN 500TL U X208 Indoor [208V],Y,96.5,N'
'INGETEAM POWER TECHNOLOGY S.A. INGECON SUN 500TL U X208 Outdoor [208V],Y,96.5,N'
'INGETEAM POWER TECHNOLOGY S.A. INGECON SUN 500TL U X275 Indoor [275V],Y,97,N'
'INGETEAM POWER TECHNOLOGY S.A. INGECON SUN 600TL U X330 Indoor [330V],Y,97,N'
'INGETEAM POWER TECHNOLOGY S.A. INGECON SUN 600TL U X330 Outdoor [330V],Y,97,N'
'INGETEAM POWER TECHNOLOGY S.A. INGECON SUN 600TL X330 Outdoor [330V],Y,97,N'
'INGETEAM POWER TECHNOLOGY S.A. Ingecon Sun 610TL U B220 Indoor [220V],N,97.5,N'
#REF!
'INGETEAM POWER TECHNOLOGY S.A. Ingecon Sun 610TL U B220 Outdoor [300V],N,97.5,N'
'INGETEAM POWER TECHNOLOGY S.A. INGECON SUN 660TL U X275 Indoor [275V],Y,97,N'
'INGETEAM POWER TECHNOLOGY S.A. INGECON SUN 660TL U X275 Outdoor [275V],Y,97,N'
#REF!
'INGETEAM POWER TECHNOLOGY S.A. INGECON SUN 660TL X360 Indoor [360V],Y,97.5,N'
'INGETEAM POWER TECHNOLOGY S.A. INGECON SUN 660TL X360 Outdoor [360V],Y,97.5,N'
'INGETEAM POWER TECHNOLOGY S.A. INGECON SUN 800TL U X330 Indoor [330V],Y,97,N'
'INGETEAM POWER TECHNOLOGY S.A. INGECON SUN 800TL U X330 Outdoor [330V],Y,97,N'
'INGETEAM POWER TECHNOLOGY S.A. Ingecon Sun 830TL U B300 Indoor [300V],N,97.5,N'
'INGETEAM POWER TECHNOLOGY S.A. Ingecon Sun 830TL U B300 Outdoor [300V],N,97.5,N'
'INGETEAM POWER TECHNOLOGY S.A. INGECON SUN 880TL X360 Indoor [360V],Y,97.5,N'
'INGETEAM POWER TECHNOLOGY S.A. INGECON SUN 880TL X360 Outdoor [360V],Y,97.5,N'
'INGETEAM POWER TECHNOLOGY S.A. Ingecon Sun 915TL U B330 Indoor [330V],N,97.5,N'
'INGETEAM POWER TECHNOLOGY S.A. Ingecon Sun 915TL U B330 Outdoor [330V],N,97.5,N'
'INGETEAM POWER TECHNOLOGY S.A. Ingecon Sun 1000TL U B360 Indoor [360V],N,98,N'
'INGETEAM POWER TECHNOLOGY S.A. Ingecon Sun 1000TL U B360 Outdoor [360V],N,98,N'
'INGETEAM POWER TECHNOLOGY S.A. Ingecon Sun 1110TL U B400 Indoor [400V],N,98,N'
'INGETEAM POWER TECHNOLOGY S.A. Ingecon Sun 1110TL U B400 Outdoor [400V],N,98,N'
'INGETEAM POWER TECHNOLOGY S.A. Ingecon Sun 1165TL U B420 Indoor [420V],N,98,N'
'INGETEAM POWER TECHNOLOGY S.A. Ingecon Sun 1165TL U B420 Outdoor [420V],N,98,N'
'INGETEAM POWER TECHNOLOGY S.A. Ingecon Sun 1170TL U B450 Indoor [450V],Y,97.5,N'
'INGETEAM POWER TECHNOLOGY S.A. Ingecon Sun 1170TL U B450 Outdoor [450V],Y,97.5,N'
'INGETEAM POWER TECHNOLOGY S.A. Ingecon Sun 1400TL U B540 Indoor [450V],Y,97.5,N'
'INGETEAM POWER TECHNOLOGY S.A. Ingecon Sun 1400TL U B540 Outdoor [450V],Y,97.5,N'
'INGETEAM POWER TECHNOLOGY S.A. Ingecon Sun 1500TL U B578 Indoor [450V],Y,97.5,N'
'INGETEAM POWER TECHNOLOGY S.A. Ingecon Sun 1500TL U B578 Outdoor [450V],Y,97.5,N'
'INGETEAM POWER TECHNOLOGY S.A. Ingecon Sun 1560TL U B600 Indoor [450V],Y,98,N'
'INGETEAM POWER TECHNOLOGY S.A. Ingecon Sun 1560TL U B600 Outdoor [450V],Y,98,N'
'INGETEAM POWER TECHNOLOGY S.A. Ingecon Sun 1600TL U B615 Indoor [450V],Y,98,N'
'INGETEAM POWER TECHNOLOGY S.A. Ingecon Sun 1600TL U B615 Outdoor [450V],Y,98,N'
'INGETEAM POWER TECHNOLOGY S.A. Ingecon Sun 1640TL U B630 Indoor [450V],Y,98,N'
'INGETEAM POWER TECHNOLOGY S.A. Ingecon Sun 1640TL U B630 Outdoor [450V],Y,98,N'
'Involar MAC250A-240-NA,N,93,N'
'Involar MAC500-XX,N,94.5,Y'
'iPower SHO-1.1 [120V],Y,90.5,N'
'iPower SHO-2.0 [240V],Y,92,N'
'iPower SHO-2.5 [240V],Y,94.5,N'
'iPower SHO-3.0 [240V],Y,93.5,N'
'iPower SHO-3.5 [240V],Y,95.5,N'
'iPower SHO-4.6 [208V],Y,95.5,N'
'iPower SHO-4.8 [240V],Y,96,N'
'iPower SHO-5.2 [240V],Y,96,N'
'Jema Energy JAE7140,N,95.5,N'
'Jema Energy JAE7141,N,95,N'
'Jema Energy IF500TL-UL OUTDOOR,Y,96,N'
'Jema Energy IF600TL-UL OUTDOOR,Y,96,N'
'Jiangsu Zeversolar New Energy Evershine TL3000-US-208,Y,96,N'
'Jiangsu Zeversolar New Energy Evershine TL3000-US-240,Y,96.5,N'
'Jiangsu Zeversolar New Energy Evershine TL4000-US-208,Y,96.5,N'
'Jiangsu Zeversolar New Energy Evershine TL4000-US-240,Y,96.5,N'
'Jiangsu Zeversolar New Energy Evershine TL5000-US-208,Y,96,N'
'Jiangsu Zeversolar New Energy Evershine TL5000-US-240,Y,96.5,N'
'Jiangsu Zeversolar New Energy Evershine TL6000-US-208,Y,96,N'
'Jiangsu Zeversolar New Energy Evershine TL6000-US-240,Y,96.5,N'
'Jiangyin Hareon Power HR-240P-AC/Bb [208V],N,95,Y'
'Jiangyin Hareon Power HR-240P-AC/Bb [240V],N,95,Y'
'Jiangyin Hareon Power HR-240P-AC/BbP [208V],N,95,Y'
'Jiangyin Hareon Power HR-240P-AC/BbP [240V],N,95,Y'
'Jiangyin Hareon Power HR-245P-AC/Bb [208V],N,95,Y'
'Jiangyin Hareon Power HR-245P-AC/Bb [240V],N,95,Y'
'Jiangyin Hareon Power HR-245P-AC/BbP [208V],N,95,Y'
'Jiangyin Hareon Power HR-245P-AC/BbP [240V],N,95,Y'
'Jiangyin Hareon Power HR-250-AC/Cb [208V],N,95,Y'
'Jiangyin Hareon Power HR-250-AC/Cb [240V],N,95,Y'
'Jiangyin Hareon Power HR-250P-AC/Bb [208V],N,95,Y'
'Jiangyin Hareon Power HR-250P-AC/Bb [240V],N,95,Y'
'Jiangyin Hareon Power HR-250P-AC/BbP [208V],N,95,Y'
'Jiangyin Hareon Power HR-250P-AC/BbP [240V],N,95,Y'
'Jiangyin Hareon Power HR-255-AC/Cb [208V],N,95,Y'
#REF!
#REF!
#REF!
#REF!
#REF!
#REF!
#REF!
#REF!
#REF!
#REF!
#REF!
#REF!
#REF!
#REF!
#REF!
#REF!
#REF!
#REF!
#REF!
#REF!
#REF!
#REF!
#REF!
#REF!
#REF!
#REF!
#REF!
#REF!
'Jiangyin Hareon Power HR-255-AC/Cb [240V],N,95,Y'
'Jiangyin Hareon Power HR-255P-AC/Bb [208V],N,95,Y'
'Jiangyin Hareon Power HR-255P-AC/Bb [240V],N,95,Y'
'Jiangyin Hareon Power HR-255P-AC/BbP [208V],N,95,Y'
'Jiangyin Hareon Power HR-255P-AC/BbP [240V],N,95,Y'
'Jiangyin Hareon Power HR-260-AC/Cb [208V],N,95,Y'
'Jiangyin Hareon Power HR-260-AC/Cb [240V],N,95,Y'
'Jiangyin Hareon Power HR-260P-AC/Bb [208V],N,95,Y'
'Jiangyin Hareon Power HR-260P-AC/Bb [240V],N,95,Y'
'Jiangyin Hareon Power HR-260P-AC/BbP [208V],N,95,Y'
'Jiangyin Hareon Power HR-260P-AC/BbP [240V],N,95,Y'
'Jiangyin Hareon Power HR-265-AC/Cb [208V],N,95,Y'
'Jiangyin Hareon Power HR-265-AC/Cb [240V],N,95,Y'
'Jiangyin Hareon Power HR-270-AC/Cb [208V],N,95,Y'
'Jiangyin Hareon Power HR-270-AC/Cb [240V],N,95,Y'
'Jinko Solar Co., Ltd. JKMS300M-60BL-EP [208V],N,97,Y'
'Jinko Solar Co., Ltd. JKMS300M-60BL-EP [240V],N,97,Y'
'Jinko Solar Co., Ltd. JKMS305M-60BL-EP [208V],N,97,Y'
'Jinko Solar Co., Ltd. JKMS305M-60BL-EP [240V],N,97,Y'
'Jinko Solar Co., Ltd. JKMS305M-60L-EP [208V],N,97,Y'
'Jinko Solar Co., Ltd. JKMS305M-60L-EP [240V],N,97,Y'
'Jinko Solar Co., Ltd. JKMS310M-60BL-EP [208V],N,97,Y'
'Jinko Solar Co., Ltd. JKMS310M-60BL-EP [240V],N,97,Y'
'Jinko Solar Co., Ltd. JKMS310M-60L-EP [208V],N,97,Y'
'Jinko Solar Co., Ltd. JKMS310M-60L-EP [240V],N,97,Y'
'Jinko Solar Co., Ltd. JKMS315M-60BL-EP [208V],N,97,Y'
'Jinko Solar Co., Ltd. JKMS315M-60BL-EP [240V],N,97,Y'
'Jinko Solar Co., Ltd. JKMS315M-60L-EP [208V],N,97,Y'
'Jinko Solar Co., Ltd. JKMS315M-60L-EP [240V],N,97,Y'
'Jinko Solar Co., Ltd. JKMS320M-60BL-EP [208V],N,97,Y'
'Jinko Solar Co., Ltd. JKMS320M-60BL-EP [240V],N,97,Y'
'Jinko Solar Co., Ltd. JKMS320M-60L-EP [208V],N,97,Y'
'Jinko Solar Co., Ltd. JKMS320M-60L-EP [240V],N,97,Y'
'Jinko Solar Co., Ltd. JKMS325M-60BL-EP [208V],N,97,Y'
'Jinko Solar Co., Ltd. JKMS325M-60BL-EP [240V],N,97,Y'
'Jinko Solar Co., Ltd. JKMS325M-60L-EP [208V],N,97,Y'
'Jinko Solar Co., Ltd. JKMS325M-60L-EP [240V],N,97,Y'
'Jinko Solar Co., Ltd. JKMS330M-60L-EP [208V],N,97,Y'
'Jinko Solar Co., Ltd. JKMS330M-60L-EP [240V],N,97,Y'
'KACO blueplanet Ultraverter 250,N,97.5,Y'
'KACO blueplanet 1501xi [240V],Y,95,N'
'KACO blueplanet 1502x [208V],Y,95.5,N'
'KACO blueplanet 1502xi [208V],Y,95.5,N'
'KACO blueplanet 1502x [240V],Y,94,N'
'KACO blueplanet 1502xi [240V],Y,94,N'
'KACO blueplanet 2.0 TL1 M1 WM OD US3x [208V],Y,96,N'
'KACO blueplanet 2.0 TL1 M1 WM OD US3x [240V],Y,96.5,N'
'KACO blueplanet 2502x [208V],Y,95,N'
'KACO blueplanet 2502x [240V],Y,95.5,N'
'KACO blueplanet 2502xi [208V],Y,95,N'
'KACO blueplanet 2502xi [240V],Y,95.5,N'
'KACO blueplanet 2901xi [240V],Y,94,N'
'KACO blueplanet 3.0 TL1 M1 WM OD US3x [208V],Y,96,N'
'KACO blueplanet 3.0 TL1 M1 WM OD US3x [240V],Y,96.5,N'
'KACO blueplanet 3502x [208V],Y,95.5,N'
'KACO blueplanet 3502x [240V],Y,95.5,N'
'KACO blueplanet 3502xi [208V],Y,95.5,N'
'KACO blueplanet 3502xi [240V],Y,95.5,N'
'KACO blueplanet 3601xi [240V],Y,93.5,N'
'KACO blueplanet 4.0 TL1 M1 WM OD US3x [208V],Y,96.5,N'
'KACO blueplanet 4.0 TL1 M1 WM OD US3x [240V],Y,96.5,N'
'KACO blueplanet 5.0 TL1 M1 WM OD US3x [208V],Y,96.5,N'
'KACO blueplanet 5002x [208V],Y,95,N'
'KACO blueplanet 5002x [240V],Y,95.5,N'
'KACO blueplanet 5002xi [208V],Y,95,N'
'KACO blueplanet 5002xi [240V],Y,95.5,N'
'KACO blueplanet 5.0 TL1 M1 WM OD US3x [240V],Y,96.5,N'
'KACO blueplanet 6400M [208V],Y,96.5,N'
#REF!
'KACO blueplanet 6400M [240V],Y,96.5,N'
'KACO blueplanet 6400x [208V],Y,96.5,N'
'KACO blueplanet 6400x [240V],Y,96.5,N'
'KACO blueplanet 6400xi [208V],Y,96.5,N'
'KACO blueplanet 6400xi [240V],Y,96.5,N'
'KACO blueplanet 7600M [208V],Y,96.5,N'
'KACO blueplanet 7600M [240V],Y,96.5,N'
'KACO blueplanet 7600x [208V],Y,96.5,N'
'KACO blueplanet 7600x [240V],Y,96.5,N'
'KACO blueplanet 7600xi [208V],Y,96.5,N'
'KACO blueplanet 7600xi [240V],Y,96.5,N'
'KACO blueplanet 10.0 TL3 [480V],Y,97,N'
'KACO XP10U-H4 (-PSD) [480V],Y,97,N'
'KACO blueplanet 32.0 TL3 M1 [480V],Y,97,N'
'KACO blueplanet 32.0 TL3 M3 [480V],Y,97,N'
'KACO blueplanet 40.0 TL3 M1 [480V],Y,97.5,N'
'KACO blueplanet 40.0 TL3 M3 [480V],Y,97.5,N'
'KACO XP42U-H2 [208V],Y,95.5,N'
'KACO blueplanet 50.0 TL3 M1 [480V],Y,97.5,N'
'KACO blueplanet 50.0 TL3 M3 [480V],Y,97.5,N'
'KACO XP50U-H4 [480V],Y,96,N'
'KACO XP100U-H2 [480V],Y,95.5,N'
'KACO XP100U-H4 [480V],Y,96,N'
'KACO XP500U-TL,Y,98,N'
'KACO XP550U-TL,Y,98,N'
'KACO KACO blueplanet 750 TL3 750 TL3 M1 GM OD USX0,Y,98,N'
'KACO KACO blueplanet 875 TL3 875 TL3 M1 GM OD USX0,Y,98,N'
'KACO KACO blueplanet 1000 TL3 1000 TL3 M1 GM OD USX0,Y,98,N'
#REF!
#REF!
#REF!
#REF!
#REF!
#REF!
#REF!
#REF!
#REF!
#REF!
#REF!
#REF!
#REF!
#REF!
#REF!
'KACO KACO blueplanet 1500 TL3 M1 GM OD USX0,Y,98,N'
'KACO KACO blueplanet 2200 TL3 M1 GM OD USX0,Y,98,N'
'Kostal Solar Electric Piko 5.3 US,Y,94,N'
'LeadSolar Energy Co., Ltd LS560 [240V],N,95.5,Y'
'LeadSolar Energy Co., Ltd LS600 [240V],N,95.5,Y'
'LeadSolar Energy Co., Ltd LS600T [208V],N,95,Y'
'LeadSolar Energy Co., Ltd LS600ES [277V],N,96,Y'
#REF!
'LeadSolar Energy Co., Ltd LS700TS-208 [208V],N,95.5,Y'
#REF!
'LeadSolar Energy Co., Ltd LS650S [277V],N,96,Y'
#REF!
'LeadSolar Energy Co., Ltd LS700S [277V],N,96,Y'
#REF!
'LeadSolar Energy Co., Ltd LS700TS-240 [240V],N,95.5,Y'
#REF!
'LeadSolar Energy Co., Ltd LS1400-240V [240V],N,95,Y'
#REF!
'Leatec Fine Ceramics CM21-0113 [240V],N,96,Y'
#REF!
'LG Electronics Inc. LG315E1K-A5 [208V],N,97,Y'
#REF!
'LG Electronics Inc. LG315E1K-A5 [240V],N,97,Y'
#REF!
'LG Electronics Inc. LG320E1K-A5 [208V],N,97,Y'
#REF!
'LG Electronics Inc. LG320E1K-A5 [240V],N,97,Y'
#REF!
'LG Electronics Inc. LG325E1C-A5 [208V],N,97,Y'
#REF!
'LG Electronics Inc. LG325E1C-A5 [240V],N,97,Y'
'LG Electronics Inc. LG325E1K-A5 [208V],N,97,Y'
'LG Electronics Inc. LG325E1K-A5 [240V],N,97,Y'
'LG Electronics Inc. LG330E1C-A5 [208V],N,97,Y'
'LG Electronics Inc. LG330E1C-A5 [240V],N,97,Y'
'LG Electronics Inc. LG335E1C-A5 [208V],N,97,Y'
'LG Electronics Inc. LG335E1C-A5 [240V],N,97,Y'
'LG Electronics Inc. LG295A1C-B3 [208V],N,96,Y'
'LG Electronics Inc. LG295A1W-B3 [208V],N,96,Y'
'LG Electronics Inc. LG300A1C-B3 [208V],N,96,Y'
'LG Electronics Inc. LG300A1W-B3 [208V],N,96,Y'
'LG Electronics Inc. LG305A1C-B3 [208V],N,96,Y'
'LG Electronics Inc. LG305A1W-B3 [208V],N,96,Y'
'LG Electronics Inc. LM305UE-G1 [208V],N,96,Y'
'LG Electronics Inc. LG295A1C-B3 [240V],N,96.5,Y'
'LG Electronics Inc. LG295A1W-B3 [240V],N,96.5,Y'
'LG Electronics Inc. LG300A1C-B3 [240V],N,96.5,Y'
'LG Electronics Inc. LG300A1W-B3 [240V],N,96.5,Y'
'LG Electronics Inc. LG305A1C-B3 [240V],N,96.5,Y'
'LG Electronics Inc. LG305A1W-B3 [240V],N,96.5,Y'
'LG Electronics Inc. LM305UE-G1 [240V],N,96.5,Y'
'Lixma Tech LSI4000 [240V],Y,95,N'
'Mage Solar POWERTEC Plus 240 / 6 PL-US AC [240V],N,95,Y'
'Mage Solar POWERTEC Plus 245 / 6 PL US AC [240V],N,95,Y'
'Mage Solar USA POWERTEC Plus 250 / 6 PL US AC [208V],N,95,Y'
'Mage Solar USA POWERTEC Plus 250 / 6 PL US AC [240V],N,95,Y'
'Ming Shen Energy Technology EnerBridge Emi_301RD [240V],N,96,Y'
'Mohr Power MPS1100EVR [120V],Y,90.5,N'
'Mohr Power MPS2000EVR [240V],Y,92,N'
'Mohr Power MPS2500 [240V],Y,94.5,N'
'Mohr Power MPS3000 [240V],Y,93.5,N'
'Mohr Power MPS3500 [240V],Y,95.5,N'
'Mohr Power MPS4600 [208V],Y,95.5,N'
'Mohr Power MPS4800 [240V],Y,96,N'
'Mohr Power MPS5200 [240V],Y,96,N'
'Motech Industries PVMate 2900U [208V],Y,95.5,N'
'Motech Industries PVMate 2900U-POS [208V],Y,95.5,N'
'Motech Industries PVMate 3000U [208V],Y,95.5,N'
'Motech Industries PVMate 3000U-PG [208V],Y,95.5,N'
'Motech Industries PVMate 2900U [240V],Y,96,N'
'Motech Industries PVMate 2900U-POS [240V],Y,96,N'
'Motech Industries PVMate 3000U [240V],Y,96,N'
'Motech Industries PVMate 3000U-PG [240V],Y,96,N'
'Motech Industries PVMate 3840U [208V],Y,95.5,N'
'Motech Industries PVMate 3840U-POS [208V],Y,95.5,N'
'Motech Industries PVMate 3900U [208V],Y,95.5,N'
'Motech Industries PVMate 3900U-POS [208V],Y,95.5,N'
'Motech Industries PVMate 4000U [208V],Y,95.5,N'
'Motech Industries PVMate 4000U-PG [208V],Y,95.5,N'
'Motech Industries PVMate 3840U [240V],Y,96,N'
'Motech Industries PVMate 3840U-POS [240V],Y,96,N'
'Motech Industries PVMate 3900U [240V],Y,96,N'
'Motech Industries PVMate 3900U-POS [240V],Y,96,N'
'Motech Industries PVMate 4000U [240V],Y,96,N'
'Motech Industries PVMate 4000U-PG [240V],Y,96,N'
'Motech Industries PVMate 4900U [208V],Y,96,N'
'Motech Industries PVMate 4900U-POS [208V],Y,96,N'
'Motech Industries PVMate 5000U [208V],Y,96,N'
'Motech Industries PVMate 5000U-PG [208V],Y,96,N'
'Motech Industries PVMate 5300U [208V],Y,95.5,N'
'Motech Industries PVMate 5300U-POS [208V],Y,95.5,N'
'Motech Industries PVMate 4900U [240V],Y,96,N'
'Motech Industries PVMate 4900U-POS [240V],Y,96,N'
'Motech Industries PVMate 5000U [240V],Y,96,N'
'Motech Industries PVMate 5000U-PG [240V],Y,96,N'
'Motech Industries PVMate 5300U [240V],Y,96,N'
'Motech Industries PVMate 5300U-POS [240V],Y,96,N'
'Motech Industries PVMate 6500U [208V],Y,95.5,N'
'Motech Industries PVMate 6500U [240V],Y,96,N'
'Motech Industries PVMate 6500U [277V],Y,96,N'
'Motech Industries PVMate 7500U [208V],Y,95.5,N'
'Motech Industries PVMate 7500U [240V],Y,96,N'
'Motech Industries PVMate 7500U [277V],Y,96,N'
'NeoVolta Inc. NV7600 [208V],N,96.5,N'
'NeoVolta Inc. NV7600 [240V],N,96.5,N'
'Nextronex Energy Systems Ray-Max 150,N,96,N'
'Nidec ASI PV800A60UNO04LNU0NN [600V],N,98,N'
'Ningbo Ginlong Technologies Co.,Ltd. GCI-1K-2G-H-US [208V],Y,96,N'
'Ningbo Ginlong Technologies Co.,Ltd. GCI-1K-2G-H-US [240V],Y,96,N'
'Ningbo Ginlong Technologies Co.,Ltd. GCI-1K-2G-W-US [208V],Y,96,N'
'Ningbo Ginlong Technologies Co.,Ltd. GCI-1K-2G-W-US [240V],Y,96,N'
'Ningbo Ginlong Technologies Co.,Ltd. Solis-1K-2G-US [208V],Y,96,N'
'Ningbo Ginlong Technologies Co.,Ltd. Solis-1K-2G-US [240V],Y,96,N'
'Ningbo Ginlong Technologies Co.,Ltd. GCI-1.5K-2G-H-US [208V],Y,96,N'
'Ningbo Ginlong Technologies Co.,Ltd. GCI-1.5K-2G-H-US [240V],Y,96,N'
'Ningbo Ginlong Technologies Co.,Ltd. GCI-1.5K-2G-W-US [208V],Y,96,N'
'Ningbo Ginlong Technologies Co.,Ltd. GCI-1.5K-2G-W-US [240V],Y,96,N'
'Ningbo Ginlong Technologies Co.,Ltd. Solis-1.5K-2G-US [208V],Y,96,N'
'Ningbo Ginlong Technologies Co.,Ltd. Solis-1.5K-2G-US [240V],Y,96,N'
'Ningbo Ginlong Technologies Co.,Ltd. GCI-2K-2G-H-US [208V],Y,96.5,N'
'Ningbo Ginlong Technologies Co.,Ltd. GCI-2K-2G-H-US [240V],Y,96.5,N'
'Ningbo Ginlong Technologies Co.,Ltd. GCI-2K-2G-W-US [208V],Y,96.5,N'
'Ningbo Ginlong Technologies Co.,Ltd. GCI-2K-2G-W-US [240V],Y,96.5,N'
'Ningbo Ginlong Technologies Co.,Ltd. Solis-2K-2G-US [208V],Y,96.5,N'
'Ningbo Ginlong Technologies Co.,Ltd. Solis-2K-2G-US [240V],Y,96.5,N'
'Ningbo Ginlong Technologies Co.,Ltd. GCI-2K [240V],Y,94,N'
'Ningbo Ginlong Technologies Co.,Ltd. GCI-2.5K-2G-H-US [208V],Y,96.5,N'
'Ningbo Ginlong Technologies Co.,Ltd. GCI-2.5K-2G-H-US [240V],Y,96.5,N'
'Ningbo Ginlong Technologies Co.,Ltd. GCI-2.5K-2G-W-US [208V],Y,96.5,N'
#REF!
'Ningbo Ginlong Technologies Co.,Ltd. GCI-2.5K-2G-W-US [240V],Y,96.5,N'
'Ningbo Ginlong Technologies Co.,Ltd. Solis-2.5K-2G-US [208V],Y,96.5,N'
#REF!
#REF!
#REF!
#REF!
#REF!
#REF!
'Ningbo Ginlong Technologies Co.,Ltd. Solis-2.5K-2G-US [240V],Y,96.5,N'
#REF!
'Ningbo Ginlong Technologies Co.,Ltd. Solis-1P2.5K-4G-US [240V],N,97,N'
'Ningbo Ginlong Technologies Co.,Ltd. GCI-3K-2G-H-US [208V],Y,96.5,N'
'Ningbo Ginlong Technologies Co.,Ltd. GCI-3K-2G-H-US [240V],Y,97,N'
#REF!
#REF!
#REF!
#REF!
'Ningbo Ginlong Technologies Co.,Ltd. GCI-3K-2G-W-US [240V],Y,97,N'
#REF!
'Ningbo Ginlong Technologies Co.,Ltd. Solis-3K-2G-US [208V],Y,96.5,N'
'Ningbo Ginlong Technologies Co.,Ltd. Solis-3K-2G-US [240V],Y,97,N'
#REF!
#REF!
'Ningbo Ginlong Technologies Co.,Ltd. Solis-1P3K-4G-US [240V],N,97,N'
'Ningbo Ginlong Technologies Co.,Ltd. GCI-3.6K-2G-H-US [208V],Y,96.5,N'
'Ningbo Ginlong Technologies Co.,Ltd. GCI-3.6K-2G-H-US [240V],Y,96.5,N'
'Ningbo Ginlong Technologies Co.,Ltd. GCI-3.6K-2G-W-US [208V],Y,96.5,N'
'Ningbo Ginlong Technologies Co.,Ltd. GCI-3.6K-2G-W-US [240V],Y,96.5,N'
'Ningbo Ginlong Technologies Co.,Ltd. Solis-3.6K-2G-US [208V],Y,96.5,N'
'Ningbo Ginlong Technologies Co.,Ltd. Solis-3.6K-2G-US [240V],Y,96.5,N'
#REF!
#REF!
'Ningbo Ginlong Technologies Co.,Ltd. Solis-1P3.6K-4G-US [240V],N,97,N'
'Ningbo Ginlong Technologies Co.,Ltd. GCI-4K-2G-H-US [208V],Y,97,N'
#REF!
#REF!
#REF!
'Ningbo Ginlong Technologies Co.,Ltd. GCI-4K-2G-H-US [240V],Y,97,N'
#REF!
#REF!
'Ningbo Ginlong Technologies Co.,Ltd. GCI-4K-2G-W-US [208V],Y,97,N'
#REF!
'Ningbo Ginlong Technologies Co.,Ltd. GCI-4K-2G-W-US [240V],Y,97,N'
'Ningbo Ginlong Technologies Co.,Ltd. Solis-4K-2G-US [208V],Y,97,N'
'Ningbo Ginlong Technologies Co.,Ltd. Solis-4K-2G-US [240V],Y,97,N'
'Ningbo Ginlong Technologies Co.,Ltd. Solis-1P4K-4G-US [240V],N,97,N'
#REF!
'Ningbo Ginlong Technologies Co.,Ltd. GCI-4.6K-2G-H-US [208V],Y,97,N'
'Ningbo Ginlong Technologies Co.,Ltd. GCI-4.6K-2G-H-US [240V],Y,97,N'
#REF!
'Ningbo Ginlong Technologies Co.,Ltd. GCI-4.6K-2G-W-US [208V],Y,97,N'
'Ningbo Ginlong Technologies Co.,Ltd. GCI-4.6K-2G-W-US [240V],Y,97,N'
'Ningbo Ginlong Technologies Co.,Ltd. Solis-4.6K-2G-US [208V],Y,97,N'
'Ningbo Ginlong Technologies Co.,Ltd. Solis-4.6K-2G-US [240V],Y,97,N'
'Ningbo Ginlong Technologies Co.,Ltd. Solis-1P4.6K-4G-US [240V],N,97,N'
'Ningbo Ginlong Technologies Co.,Ltd. GCI-5K-2G-H-US [208V],Y,97,N'
'Ningbo Ginlong Technologies Co.,Ltd. GCI-5K-2G-H-US [240V],Y,97,N'
#REF!
'Ningbo Ginlong Technologies Co.,Ltd. GCI-5K-2G-W-US [208V],Y,97,N'
#REF!
'Ningbo Ginlong Technologies Co.,Ltd. GCI-5K-2G-W-US [240V],Y,97,N'
'Ningbo Ginlong Technologies Co.,Ltd. Solis-5K-2G-US [208V],Y,97,N'
'Ningbo Ginlong Technologies Co.,Ltd. Solis-5K-2G-US [240V],Y,97,N'
'Ningbo Ginlong Technologies Co.,Ltd. GCI-5K-DB [240V],Y,95.5,N'
#REF!
'Ningbo Ginlong Technologies Co.,Ltd. GCI-5K-W [240V],Y,95.5,N'
'Ningbo Ginlong Technologies Co.,Ltd. Solis 5000-DB [240V],Y,95.5,N'
'Ningbo Ginlong Technologies Co.,Ltd. Solis-1P5K-4G-US [240V],N,97,N'
'Ningbo Ginlong Technologies Co.,Ltd. Solis-1P6K2-4G-US [240V],N,97,N'
#REF!
'Ningbo Ginlong Technologies Co.,Ltd. Solis-1P6K-4G-US,Y,97.5,N'
'Ningbo Ginlong Technologies Co.,Ltd. Solis-6K-US 480 Vac [480V],Y,97,N'
'Ningbo Ginlong Technologies Co.,Ltd. Solis-1P7K-4G-US [240V],Y,97.5,N'
#REF!
'Ningbo Ginlong Technologies Co.,Ltd. Solis-1P7.6K-4G-US,Y,97.5,N'
'Ningbo Ginlong Technologies Co.,Ltd. Solis-1P8K-4G-US,Y,97.5,N'
#REF!
#REF!
'Ningbo Ginlong Technologies Co.,Ltd. Solis-1P9K-4G-US,Y,97.5,N'
#REF!
#REF!
#REF!
'Ningbo Ginlong Technologies Co.,Ltd. Solis-10K-US [480V],Y,97.5,N'
'Ningbo Ginlong Technologies Co.,Ltd. Solis-1P10K-4G-US,Y,97.5,N'
#REF!
#REF!
'Ningbo Ginlong Technologies Co.,Ltd. Solis-15K-US [480V],Y,97.5,N'
'Ningbo Ginlong Technologies Co.,Ltd. Solis-20K-US [480V],Y,97.5,N'
#REF!
'Ningbo Ginlong Technologies Co.,Ltd. Solis-25K-US [480V],N,98,N'
'Ningbo Ginlong Technologies Co.,Ltd. Solis-30K-US [480V],N,98,N'
'Ningbo Ginlong Technologies Co.,Ltd. Solis-36K-US [480V],N,98,N'
'Ningbo Ginlong Technologies Co.,Ltd. Solis-40K-US-F [480V],N,98.5,N'
#REF!
'Ningbo Ginlong Technologies Co.,Ltd. Solis-40K-US [480V],N,98.5,N'
'Ningbo Ginlong Technologies Co.,Ltd. Solis-50K-US [480V],N,98.5,N'
#REF!
'Ningbo Ginlong Technologies Co.,Ltd. Solis-50K-US-F [480V],N,98.5,N'
'Ningbo Ginlong Technologies Co.,Ltd. Solis-60K-US-F [480V],N,98.5,N'
'Ningbo Ginlong Technologies Co.,Ltd. Solis-66K-US-F [480V],N,98.5,N'
'Northern Electric BDM-300X2-208A [208V],N,95.5,Y'
'Northern Electric BDM-300X2-240A [240V],N,95.5,Y'
'Northern Electric & Power BDM-250-208A [208V],N,95,Y'
'Northern Electric & Power BDM-250-240A [240V],N,95,Y'
'Northern Electric & Power Co., Ltd BDM-300-208A [208V],N,95.5,Y'
'Northern Electric & Power Co., Ltd BDM-300-240A [240V],N,95.5,Y'
'Open Energy Solar Save 1100 [240V],Y,90.5,N'
'Open Energy Solar Save 2000 [240V],Y,92,N'
'Open Energy Solar Save 2500 [240V],Y,94.5,N'
'Open Energy Solar Save 3500 [240V],Y,95.5,N'
'Open Energy Solar Save 4600 [208V],Y,95.5,N'
'Open Energy Solar Save 4800 [240V],Y,96,N'
'Open Energy Solar Save 5200 [240V],Y,96,N'
'OPTI International GT 1500 [208V],Y,94.5,N'
'OPTI International GT 1500 [240V],Y,94.5,N'
'OPTI International GT 2000 [208V],Y,95.5,N'
'OPTI International GT 2000 [240V],Y,95,N'
'OPTI International GT 3000 [208V],Y,95.5,N'
'OPTI International GT 3000 [240V],Y,95.5,N'
'OPTI-Solar GT-4000 [208V],Y,95.5,N'
'OPTI-Solar GT-4000 [240V],Y,96,N'
'OutBack Power Technologies, Inc. FXR3048A,Y,91,N'
'OutBack Power Technologies, Inc. GTFX3048,N,91,N'
'OutBack Power Technologies, Inc. GVFX3524,Y,90.5,N'
'OutBack Power Technologies, Inc. VFXR3524A,Y,90.5,N'
'OutBack Power Technologies, Inc. GVFX3648,N,91,N'
'OutBack Power Technologies, Inc. VFXR3648A,Y,91,N'
'OutBack Power Technologies, Inc. GS4048A,Y,92.5,N'
'OutBack Power Technologies, Inc. SBX5048-120/240 [240V],Y,94,N'
'OutBack Power Technologies, Inc. GS8048A,Y,92.5,N'
'OutBack Power Technologies, Inc. GS8048,N,90,N'
#REF!
'OutBack Power Technologies, Inc. PHXL480-10k [480V],N,97.5,N'
'Perfect Galaxy AE-30-60-PV-A [480V],Y,93,N'
'Perfect Galaxy AE-30-60-PV-D [208V],Y,92.5,N'
'Perfect Galaxy AE-30-60-PV-E [240V],Y,93,N'
'Perfect Galaxy AE-30-60-PV-F [240V],Y,94.5,N'
'Perfect Galaxy PVS-30 [208V],Y,95,N'
'Perfect Galaxy PVS-30 [240V],Y,95,N'
'Perfect Galaxy PVS-30 [480V],Y,95,N'
'Perfect Galaxy AE-50-60-PV-D [208V],Y,94.5,N'
'Perfect Galaxy AE-50-60-PV-F [240V],Y,93,N'
'Perfect Galaxy PVS-50 [208V],Y,95.5,N'
'Perfect Galaxy PVS-50 [240V],Y,95.5,N'
'Perfect Galaxy PVS-50 [480V],Y,95.5,N'
'Perfect Galaxy PVS-50-S-MT [208V],Y,95.5,N'
'Perfect Galaxy PVS-50-S-MT [240V],Y,95.5,N'
'Perfect Galaxy PVS-50-S-MT [480V],Y,95.5,N'
'Perfect Galaxy AE-50-60-PV-A [480V],Y,93,N'
'Perfect Galaxy AE-75-60-PV-A [480V],Y,95.5,N'
'Perfect Galaxy AE-75-60-PV-D [208V],Y,95.5,N'
'Perfect Galaxy PVS-75 [208V],Y,96,N'
'Perfect Galaxy PVS-75 [240V],Y,96,N'
'Perfect Galaxy PVS-75 [480V],Y,96,N'
'Perfect Galaxy AE-100-60-PV-A [480V],Y,94.5,N'
'Perfect Galaxy AE-100-60-PV-A-HE [480V],Y,95.5,N'
'Perfect Galaxy AE-100-60-PV-D [208V],Y,94.5,N'
'Perfect Galaxy AE-100-60-PV-F [240V],Y,95,N'
'Perfect Galaxy PVS-100 [208V],Y,96,N'
'Perfect Galaxy PVS-100 [240V],Y,96,N'
'Perfect Galaxy PVS-100 [480V],Y,96,N'
'Perfect Galaxy SDMS0100208LNIU [208V],Y,95,N'
'Perfect Galaxy SDMS0100240LNIU [240V],Y,95,N'
'Perfect Galaxy SDMS0100480LNIU [480V],Y,95,N'
'Perfect Galaxy PVS-110-S-MT [208V],Y,95,N'
'Perfect Galaxy PVS-110-S-MT [240V],Y,95.5,N'
'Perfect Galaxy PVS-110-S-MT [480V],Y,95.5,N'
'Perfect Galaxy AE-135-60-PV-A [480V],Y,95.5,N'
'Perfect Galaxy AE-135-60-PV-D [208V],Y,95,N'
'Perfect Galaxy PVS-135 [208V],Y,96,N'
'Perfect Galaxy PVS-135 [240V],Y,96,N'
'Perfect Galaxy PVS-135 [480V],Y,96,N'
'Perfect Galaxy PVS-210-S [208V],Y,95.5,N'
'Perfect Galaxy PVS-210-S [240V],Y,95.5,N'
'Perfect Galaxy PVS-210-S [480V],Y,95.5,N'
'Perfect Galaxy AE-225-60-PV-A [480V],Y,94.5,N'
'Perfect Galaxy AE-225-60-PV-D [208V],Y,95.5,N'
'Perfect Galaxy EQX0250UV480TN (P),Y,96.5,N'
'Perfect Galaxy PVS-250,Y,95.5,N'
'Perfect Galaxy PVS-250 [208V],Y,96,N'
'Perfect Galaxy PVS-250 [240V],Y,96,N'
'Perfect Galaxy PVS-250 [480V],Y,96,N'
'Perfect Galaxy PVS-375 [480V],Y,95.5,N'
'Perfect Galaxy AE-500-60-PV-A [480V],Y,95,N'
'Perfect Galaxy EQX0500US200X-N,Y,96,N'
'Perfect Galaxy EQX0500US200X-P,Y,96,N'
'Perfect Galaxy EQX0500US480T-N,Y,96,N'
'Perfect Galaxy EQX0500US480T-P,Y,96,N'
#REF!
'Perfect Galaxy EQX0500UV320XP(N),Y,97,N'
'Perfect Galaxy PVS-500,Y,95.5,N'
'Perfect Galaxy PVS-500 [480V],Y,96,N'
'Perfect Galaxy SDMS0500UL320XN,Y,95.5,N'
'Perfect Galaxy SDMS0500UL320XP,Y,95.5,N'
'Perfect Galaxy SDMS0500UL480TN,Y,96,N'
'Perfect Galaxy SDMS0500UL480TP,Y,96,N'
'Perfect Galaxy PV-625-XRLS-VV-RVG,Y,96.5,N'
'Perfect Galaxy PV-625-XRLS-VV-STG,Y,96.5,N'
'Perfect Galaxy EQX0630UV360XP(N),Y,97,N'
'Perfect Galaxy PV-680-XRLS-VV-RVG,Y,96.5,N'
'Perfect Galaxy PV-680-XRLS-VV-STG,Y,96.5,N'
'Perfect Galaxy EQX0750UV320XP(N),Y,97,N'
'Perfect Galaxy EPP-1000-0600-32060-200X-U-N,Y,96.5,N'
'Perfect Galaxy EPP-1000-0600-32060-200X-U-P,Y,96.5,N'
'Perfect Galaxy EQX1000UV400XP(N),Y,97.5,N'
'Perfect Galaxy PVS-1000,Y,96,N'
'Perfect Galaxy EPP-1250-1000-52085-320X-U-N,Y,97,N'
'Perfect Galaxy EPP-1250-1000-52085-320X-U-P,Y,97,N'
'Perfect Galaxy International Ltd EQMX0500UV320XN [320V],N,97.5,N'
'Perfect Galaxy International Ltd EQMX0500UV320XP [320V],N,97.5,N'
'Perfect Galaxy International Ltd EQMX0630UV400XN [400V],N,97.5,N'
'Perfect Galaxy International Ltd EQMX0630UV400XP [400V],N,97.5,N'
'Perfect Galaxy International Ltd. EQX0500UV320XP(N),Y,97,N'
'Petra Solar 103.10866.500x [120V],N,93,Y'
'Petra Systems 103.10400.0002 [240V],N,96,Y'
'Petra Systems 103.10400.0001 [120V],N,96,Y'
'Phoenixtec Power PS240US3R [208V],Y,95.5,N'
'Phoenixtec Power PS240US3R [240V],Y,95.5,N'
'Phono Solar Technology PS240M-20/U-AC,N,94.5,Y'
'Phono Solar Technology PS240P-20/U-AC,N,94.5,Y'
'Phono Solar Technology PS245M-20/U-AC,N,94.5,Y'
'Phono Solar Technology PS245P-20/U-AC,N,94.5,Y'
#REF!
'Phono Solar Technology PS250M-20/U-AC,N,94.5,Y'
'Phono Solar Technology PS250P-20/U-AC,N,94.5,Y'
#REF!
'Phono Solar Technology PS255M-20/U-AC,N,94.5,Y'
'Phono Solar Technology PS255P-20/U-AC,N,94.5,Y'
#REF!
'Phono Solar Technology PS260M-20/U-AC,N,94.5,Y'
'Phono Solar Technology PS260P-20/U-AC,N,94.5,Y'
#REF!
'Pika Energy X3001-NA,Y,96,N'
#REF!
'Pika Energy X7603 [240V],N,96.5,N'
'Pika Energy X7601 [240V],Y,96.5,N'
'Pika Energy X7602 [240V],Y,96.5,N'
#REF!
'Pika Energy X11403 [208V],N,97.5,N'
#REF!
'Pika Energy X11402 [208V],Y,97.5,N'
#REF!
'Power Electronics FS0300CU,Y,96.5,N'
#REF!
'Power Electronics FS0300PU,Y,96.5,N'
#REF!
'Power Electronics FS0450CU,Y,97,N'
'Power Electronics FS0450PU,Y,97,N'
'Power Electronics FS0501CU,Y,96.5,N'
'Power Electronics FS0560CU,Y,96,N'
'Power Electronics FS0560PU,Y,96,N'
'Power Electronics FS0600PU,Y,97,N'
'Power Electronics FS0640CU,Y,96,N'
'Power Electronics FS0640PU,Y,96,N'
'Power Electronics FS0600CU,Y,97,N'
'Power Electronics FS0750CU,Y,96.5,N'
'Power Electronics FS0751PU,Y,97,N'
'Power Electronics FS0701CU [360V],Y,97,N'
'Power Electronics FS0830PU,Y,97,N'
'Power Electronics FS0751CU,N,97,N'
'Power Electronics FS0900PU,Y,97,N'
'Power Electronics FS0830CU,Y,97,N'
'Power Electronics FS0970CU,Y,97,N'
'Power Electronics FS0970PU,Y,97,N'
'Power Electronics FS0901CU,N,97,N'
'Power Electronics FS1001CU,Y,97,N'
'Power Electronics FS1004CU,N,97,N'
'Power Electronics FS0900CU,Y,97.5,N'
'Power Electronics FS0940CU,N,97,N'
'Power Electronics FS1050PU,Y,97,N'
'Power Electronics FS1051CU,N,97,N'
'Power Electronics FS1003CU,Y,97,N'
'Power Electronics FS01110PU,Y,97,N'
'Power Electronics FS1000CU [440V],N,97,N'
'Power Electronics FS1112CU [440V],N,97,N'
'Power Electronics FS1050CU15 [565V],N,97,N'
'Power Electronics FS1100CU15O3 [600V],N,98,N'
'Power Electronics FS1050CU,Y,97,N'
#REF!
'Power Electronics FS1080CU [400V],N,97,N'
#REF!
'Power Electronics FS1200CU,Y,97,N'
'Power Electronics FS1200PU,Y,97,N'
'Power Electronics FS1201CU [400V],N,98,N'
'Power Electronics FS1100CU15 [600V],N,97,N'
'Power Electronics FS01110CU,Y,97,N'
'Power Electronics FS1250PU,Y,97,N'
#REF!
'Power Electronics FS1140CU [420V],N,97,N'
'Power Electronics FS1271CU [420V],N,98,N'
'Power Electronics FS1290CU [330V],Y,97,N'
'Power Electronics FS1200CU15 [645V],N,97.5,N'
'Power Electronics FS1190CU [440V],N,97,N'
'Power Electronics FS1331CU [440V],N,97,N'
#REF!
'Power Electronics FS1250CU,Y,97.5,N'
'Power Electronics FS1275CU15 [690V],N,97,N'
'Power Electronics FS1260CU [400V],N,97,N'
'Power Electronics FS1401CU [400V],Y,97,N'
#REF!
'Power Electronics FS1430CU [330V],Y,97,N'
'Power Electronics FS1330CU [420V],N,97,N'
'Power Electronics FS1480CU [420V],N,97,N'
'Power Electronics FS1400CU15 [565V],N,97.5,N'
'Power Electronics FS1530CU [390V],Y,97,N'
'Power Electronics FS1390CU [440V],N,97,N'
#REF!
'Power Electronics FS1550CU [440V],Y,97,N'
'Power Electronics FS1500CU15O3 [600V],N,98,N'
'Power Electronics FS1440CU [400V],N,97,N'
'Power Electronics FS1600CU [400V],N,97,N'
#REF!
'Power Electronics FS1475CU15 [600V],N,97.5,N'
'Power Electronics FS1590CU [440V],N,97,N'
'Power Electronics FS1520CU [420V],N,97,N'
#REF!
'Power Electronics FS1690CU [420V],N,97,N'
'Power Electronics FS1700CU [390V],Y,97,N'
'Power Electronics FS1600CU15 [645V],N,97.5,N'
'Power Electronics FS1770CU [440V],N,97,N'
'Power Electronics FS1620CU [400V],N,97,N'
#REF!
'Power Electronics FS1801CU [400V],N,97,N'
'Power Electronics FS1700CU15 [690V],N,98,N'
'Power Electronics FS1750CU15 [565V],N,97.5,N'
'Power Electronics FS1710CU [420V],N,97,N'
#REF!
'Power Electronics FS1901CU [420V],N,97,N'
#REF!
'Power Electronics FS1850CU15O3 [600V],N,98,N'
'Power Electronics FS1790CU [440V],N,97,N'
'Power Electronics FS1991CU [440V],N,97,N'
#REF!
'Power Electronics FS1800CU [400V],N,97,N'
'Power Electronics FS2000CU [400V],N,97,N'
'Power Electronics FS1850CU15 [600V],N,97.5,N'
'Power Electronics FS2000K [600V],N,98,N'
'Power Electronics FS1900CU [420V],N,97,N'
#REF!
'Power Electronics FS2110CU [420V],N,97,N'
'Power Electronics FS2000CU15 [645V],N,98,N'
'Power Electronics FS2000M [34000V],N,97,N'
#REF!
'Power Electronics FS1980CU [440V],N,97,N'
'Power Electronics FS2200CU [440V],N,97,N'
'Power Electronics FS2100CU15 [565V],N,97.5,N'
#REF!
'Power Electronics FS2125CU15 [690V],N,98,N'
#REF!
'Power Electronics FS2225CU15 [600V],N,97.5,N'
#REF!
'Power Electronics FS2250CU15O3 [600V],N,98,N'
#REF!
'Power Electronics FS2150CU15 [645V],N,98,N'
#REF!
'Power Electronics FS2400CU15 [645V],N,98,N'
#REF!
'Power Electronics FS2450CU15 [565V],N,97.5,N'
#REF!
'Power Electronics FS2550CU15 [690V],N,98,N'
#REF!
'Power Electronics FS2300CU15 [690V],N,98,N'
#REF!
'Power Electronics FS2600CU15O3 [600V],N,98,N'
#REF!
'Power Electronics FS2600CU15 [600V],N,98,N'
#REF!
'Power Electronics FS2840M [34000V],N,97.5,N'
#REF!
'Power Electronics FS3001M [34000V],N,97.5,N'
#REF!
'Power Electronics FS2800CU15 [645V],N,98,N'
'Power Electronics FS3000M [34000V],N,97.5,N'
'Power Electronics FS3000CU15 [690V],N,98,N'
'Power Electronics FS3150M [34000V],N,97.5,N'
'Power Electronics FS3225M [34000V],N,97.5,N'
'Powercom SLK-1500 [208V],Y,94.5,N'
'Powercom SLK-1500 [240V],Y,94.5,N'
'Powercom SLK-2000 [208V],Y,95.5,N'
'Powercom SLK-2000 [240V],Y,95,N'
'Powercom SLK-3000 [208V],Y,95.5,N'
'Powercom SLK-3000 [240V],Y,95.5,N'
'Powercom SLK-4000 [208V],Y,95.5,N'
'Powercom SLK-4000 [240V],Y,96,N'
'Powercom SLK-4000 [277V],Y,95.5,N'
'Power-One MICRO-0.25-I-OUTD-US-208 [208V],N,96,Y'
'Power-One MICRO-0.25-I-OUTD-US-240 [240V],N,96,Y'
'Power-One MICRO-0.3HV-I-OUTD-US-208 [208V],N,96,Y'
'Power-One MICRO-0.3HV-I-OUTD-US-240 [240V],N,96,Y'
'Power-One MICRO-0.3-I-OUTD-US-208 [208V],N,96,Y'
'Power-One MICRO-0.3-I-OUTD-US-240 [240V],N,96,Y'
'Power-One UNO-2.0-I-OUTD-S-US [208V],Y,95.5,N'
'Power-One UNO-2.0-I-OUTD-S-US [240V],Y,95.5,N'
'Power-One UNO-2.0-I-OUTD-S-US [277V],Y,95.5,N'
'Power-One UNO-2.5-I-OUTD-S-US [208V],Y,95.5,N'
'Power-One UNO-2.5-I-OUTD-S-US [240V],Y,96,N'
'Power-One UNO-2.5-I-OUTD-S-US [277V],Y,96,N'
'Power-One PVI-3000-I-OUTD-US [208V],Y,90.5,N'
'Power-One PVI-3000-I-OUTD-US-F [208V],Y,90.5,N'
'Power-One PVI-3.0-OUTD-S-US [208V],Y,96,N'
'Power-One PVI-3.0-OUTD-S-US [240V],Y,96,N'
'Power-One PVI-3.0-OUTD-S-US [277V],Y,96,N'
'Power-One PVI-3.0-OUTD-S-US-A [208V],Y,96,N'
'Power-One PVI-3.0-OUTD-S-US-A [240V],Y,96,N'
'Power-One PVI-3.0-OUTD-S-US-A [277V],Y,96,N'
'Power-One PVI-3.0-OUTD-S-US-Z [208V],Y,96,N'
'Power-One PVI-3.0-OUTD-S-US-Z [240V],Y,96,N'
'Power-One PVI-3.0-OUTD-S-US-Z [277V],Y,96,N'
'Power-One PVI-3.0-OUTD-S-US-Z-A [208V],Y,96,N'
'Power-One PVI-3.0-OUTD-S-US-Z-A [240V],Y,96,N'
'Power-One PVI-3.0-OUTD-S-US-Z-A [277V],Y,96,N'
'Power-One PVI-3.0-OUTD-US [208V],Y,96,N'
'Power-One PVI-3.0-OUTD-US [240V],Y,96,N'
'Power-One PVI-3.0-OUTD-US [277V],Y,96,N'
'Power-One PVI-3000-I-OUTD-US [240V],Y,92,N'
'Power-One PVI-3000-I-OUTD-US-F [240V],Y,91,N'
'Power-One PVI-3.8-1-OUTD-x-US-y [208V],Y,96,N'
'Power-One PVI-3600-OUTD-US-F [208V],Y,94.5,N'
'Power-One PVI-3600-US [208V],Y,94,N'
'Power-One PVI-3.6-OUTD-S-US [208V],Y,96,N'
'Power-One PVI-3.6-OUTD-S-US [240V],Y,96,N'
'Power-One PVI-3.6-OUTD-S-US [277V],Y,96,N'
'Power-One PVI-3.6-OUTD-S-US-A [208V],Y,96,N'
'Power-One PVI-3.6-OUTD-S-US-A [240V],Y,96,N'
'Power-One PVI-3.6-OUTD-S-US-A [277V],Y,96,N'
'Power-One PVI-3.6-OUTD-S-US-Z [208V],Y,96,N'
'Power-One PVI-3.6-OUTD-S-US-Z [240V],Y,96,N'
'Power-One PVI-3.6-OUTD-S-US-Z [277V],Y,96,N'
'Power-One PVI-3.6-OUTD-S-US-Z-A [208V],Y,96,N'
'Power-One PVI-3.6-OUTD-S-US-Z-A [240V],Y,96,N'
'Power-One PVI-3.6-OUTD-S-US-Z-A [277V],Y,96,N'
'Power-One PVI-3.6-OUTD-US [208V],Y,96,N'
'Power-One PVI-3.6-OUTD-US [240V],Y,96,N'
'Power-One PVI-3.6-OUTD-US [277V],Y,96,N'
'Power-One PVI-3600-OUTD-US-F [240V],Y,95,N'
'Power-One PVI-3600-US [240V],Y,94.5,N'
'Power-One PVI-3.8-1-OUTD-x-US-y [240V],Y,96.5,N'
'Power-One PVI-3.8-1-OUTD-x-US-y [277V],Y,96.5,N'
'Power-One PVI-3.8-OUTD-S-US [208V],Y,95.5,N'
'Power-One PVI-3.8-OUTD-S-US [240V],Y,96,N'
'Power-One PVI-3.8-OUTD-S-US [277V],Y,96,N'
'Power-One PVI-3.8-OUTD-S-US-A [208V],Y,95.5,N'
'Power-One PVI-3.8-OUTD-S-US-A [240V],Y,96,N'
'Power-One PVI-3.8-OUTD-S-US-A [277V],Y,96,N'
'Power-One PVI-3.8-OUTD-S-US-Z [208V],Y,95.5,N'
'Power-One PVI-3.8-OUTD-S-US-Z [240V],Y,96,N'
'Power-One PVI-3.8-OUTD-S-US-Z [277V],Y,96,N'
'Power-One PVI-3.8-OUTD-S-US-Z-A [208V],Y,95.5,N'
'Power-One PVI-3.8-OUTD-S-US-Z-A [240V],Y,96,N'
'Power-One PVI-3.8-OUTD-S-US-Z-A [277V],Y,96,N'
'Power-One PVI-3.8-OUTD-US [208V],Y,95.5,N'
'Power-One PVI-3.8-OUTD-US [240V],Y,96,N'
'Power-One PVI-3.8-OUTD-US [277V],Y,96,N'
'Power-One PVI-4.2-OUTD-S-US [208V],Y,96,N'
'Power-One PVI-4.2-OUTD-S-US [240V],Y,96,N'
'Power-One PVI-4.2-OUTD-S-US [277V],Y,96,N'
'Power-One PVI-4.2-OUTD-S-US-A [208V],Y,96,N'
'Power-One PVI-4.2-OUTD-S-US-A [240V],Y,96,N'
'Power-One PVI-4.2-OUTD-S-US-A [277V],Y,96,N'
'Power-One PVI-4.2-OUTD-S-US-Z [208V],Y,96,N'
'Power-One PVI-4.2-OUTD-S-US-Z [240V],Y,96,N'
'Power-One PVI-4.2-OUTD-S-US-Z [277V],Y,96,N'
'Power-One PVI-4.2-OUTD-S-US-Z-A [208V],Y,96,N'
'Power-One PVI-4.2-OUTD-S-US-Z-A [240V],Y,96,N'
'Power-One PVI-4.2-OUTD-S-US-Z-A [277V],Y,96,N'
'Power-One PVI-4.2-OUTD-US [208V],Y,96,N'
'Power-One PVI-4.2-OUTD-US [240V],Y,96,N'
'Power-One PVI-4.2-OUTD-US [277V],Y,96,N'
'Power-One PVI-4.6-1-OUTD-x-US-y [208V],Y,96,N'
'Power-One PVI-4.6-1-OUTD-x-US-y [240V],Y,96.5,N'
'Power-One PVI-4.6-1-OUTD-x-US-y [277V],Y,96.5,N'
'Power-One PVI-5000-OUTD-S-US-Z [208V],Y,96,N'
'Power-One PVI-5000-OUTD-S-US-Z [240V],Y,96.5,N'
'Power-One PVI-5000-OUTD-S-US-Z [277V],Y,96.5,N'
'Power-One PVI-5000-OUTD-S-US-Z-A [208V],Y,96,N'
'Power-One PVI-5000-OUTD-S-US-Z-A [240V],Y,96.5,N'
'Power-One PVI-5000-OUTD-S-US-Z-A [277V],Y,96.5,N'
'Power-One PVI-5000-OUTD-US [208V],Y,96,N'
'Power-One PVI-5000-OUTD-US [240V],Y,96.5,N'
'Power-One PVI-5000-OUTD-US [277V],Y,96.5,N'
'Power-One PVI-5000-OUTD-US-A [208V],Y,96,N'
'Power-One PVI-5000-OUTD-US-A [240V],Y,96.5,N'
'Power-One PVI-5000-OUTD-US-A [277V],Y,96.5,N'
'Power-One PVI-5000-OUTD-US-Z [208V],Y,96,N'
'Power-One PVI-5000-OUTD-US-Z [240V],Y,96.5,N'
#REF!
#REF!
'Power-One PVI-5000-OUTD-US-Z [277V],Y,96.5,N'
'Power-One PVI-5000-OUTD-US-Z-A [208V],Y,96,N'
'Power-One PVI-5000-OUTD-US-Z-A [240V],Y,96.5,N'
'Power-One PVI-5000-OUTD-US-Z-A [277V],Y,96.5,N'
'Power-One PVI-6000-OUTD-S-US-A [208V],Y,96,N'
'Power-One PVI-6000-OUTD-S-US-A [240V],Y,96.5,N'
'Power-One PVI-6000-OUTD-S-US-A [277V],Y,96.5,N'
'Power-One PVI-6000-OUTD-S-US-Z [208V],Y,96,N'
'Power-One PVI-6000-OUTD-S-US-Z [240V],Y,96.5,N'
'Power-One PVI-6000-OUTD-S-US-Z [277V],Y,96.5,N'
'Power-One PVI-6000-OUTD-S-US-Z-A [208V],Y,96,N'
'Power-One PVI-6000-OUTD-S-US-Z-A [240V],Y,96.5,N'
'Power-One PVI-6000-OUTD-S-US-Z-A [277V],Y,96.5,N'
'Power-One PVI-6000-OUTD-US [208V],Y,96,N'
'Power-One PVI-6000-OUTD-US [240V],Y,96.5,N'
'Power-One PVI-6000-OUTD-US [277V],Y,96.5,N'
'Power-One PVI-6000-OUTD-US-A [208V],Y,96,N'
'Power-One PVI-6000-OUTD-US-A [240V],Y,96.5,N'
'Power-One PVI-6000-OUTD-US-A [277V],Y,96.5,N'
'Power-One PVI-6000-OUTD-US-Z [208V],Y,96,N'
'Power-One PVI-6000-OUTD-US-Z [240V],Y,96.5,N'
'Power-One PVI-6000-OUTD-US-Z [277V],Y,96.5,N'
'Power-One PVI-6000-OUTD-US-Z-A [208V],Y,96,N'
'Power-One PVI-6000-OUTD-US-Z-A [240V],Y,96.5,N'
'Power-One PVI-6000-OUTD-US-Z-A [277V],Y,96.5,N'
'Power-One UNO-7.6-TL-OUTD-S-US-A [208V],Y,96.5,N'
'Power-One UNO-7.6-TL-OUTD-S-US-A [240V],Y,96.5,N'
'Power-One UNO-7.6-TL-OUTD-S-US-A [277V],Y,96.5,N'
'Power-One UNO-7.6-TL-OUTD-S-US-Z-A [208V],Y,96.5,N'
'Power-One UNO-7.6-TL-OUTD-S-US-Z-A [240V],Y,96.5,N'
'Power-One UNO-7.6-TL-OUTD-S-US-Z-A [277V],Y,96.5,N'
'Power-One UNO-8.6-TL-OUTD-S-US-A [240V],Y,96.5,N'
'Power-One UNO-8.6-TL-OUTD-S-US-A [277V],Y,96.5,N'
'Power-One UNO-8.6-TL-OUTD-S-US-Z-A [240V],Y,96.5,N'
'Power-One UNO-8.6-TL-OUTD-S-US-Z-A [277V],Y,96.5,N'
'Power-One PVI-10.0-I-OUTD-x-US-208-y [208V],Y,96,N'
'Power-One PVI-10.0-I-OUTD-x-US-480-y-z [480V],Y,97,N'
'Power-One PVI-12.0-I-OUTD-x-US-480-y [480V],Y,97,N'
'Power-One TRIO-20.0-TL-OUTD-S1-480-A [480V],Y,97.5,N'
'Power-One TRIO-20.0-TL-OUTD-S1A-480-A [480V],Y,97.5,N'
'Power-One TRIO-20.0-TL-OUTD-S1A-US-480 [480V],Y,97.5,N'
'Power-One TRIO-20.0-TL-OUTD-S1B-480-A [480V],Y,97.5,N'
'Power-One TRIO-20.0-TL-OUTD-S1B-US-480 [480V],Y,97.5,N'
'Power-One TRIO-20.0-TL-OUTD-S1-US-480 [480V],Y,97.5,N'
'Power-One TRIO-20.0-TL-OUTD-S-480-A [480V],Y,97.5,N'
'Power-One TRIO-20.0-TL-OUTD-S-US-480 [480V],Y,97.5,N'
'Power-One TRIO-27.6-TL-OUTD-S1-480-A [480V],Y,97.5,N'
'Power-One TRIO-27.6-TL-OUTD-S1A-480-A [480V],Y,97.5,N'
'Power-One TRIO-27.6-TL-OUTD-S1A-US-480 [480V],Y,97.5,N'
'Power-One TRIO-27.6-TL-OUTD-S1B-480-A [480V],Y,97.5,N'
'Power-One TRIO-27.6-TL-OUTD-S1B-US-480 [480V],Y,97.5,N'
'Power-One TRIO-27.6-TL-OUTD-S1-US-480 [480V],Y,97.5,N'
'Power-One TRIO-27.6-TL-OUTD-S-480-A [480V],Y,97.5,N'
'Power-One TRIO-27.6-TL-OUTD-S-US-480 [480V],Y,97.5,N'
'Power-One PVI-CENTRAL-50-US [208V],Y,95,N'
'Power-One PVI-CENTRAL-50-US [480V],Y,95,N'
'Power-One PVI-CENTRAL-100-US [208V],Y,95,N'
'Power-One PVI-CENTRAL-100-US [480V],Y,95,N'
'Power-One PVI-CENTRAL-250-US [480V],Y,97,N'
'Power-One PVI-CENTRAL-300-US [480V],Y,97,N'
'Power-One ULTRA-750-TL-OUTD-2-US-690-x-y-z [690V],Y,96.5,N'
'Power-One ULTRA-750-TL-OUTD-4-US-690-x-y-z [690V],Y,96.5,N'
'Power-One ULTRA-750-TL-OUTD-1-US-690-x-y-z [690V],Y,96.5,N'
'Power-One ULTRA-750-TL-OUTD-3-US-690-x-y-z [690V],Y,96.5,N'
'Power-One ULTRA-1100-TL-OUTD-2-US-690-x-y-z [690V],Y,96.5,N'
'Power-One ULTRA-1100-TL-OUTD-4-US-690-x-y-z [690V],Y,97,N'
'Power-One ULTRA-1100-TL-OUTD-1-US-690-x-y-z [690V],Y,96.5,N'
'Power-One ULTRA-1100-TL-OUTD-3-US-690-x-y-z [690V],Y,97,N'
'Power-One ULTRA-1500-TL-OUTD-2-US-690-x-y-z [690V],Y,96.5,N'
'Power-One ULTRA-1500-TL-OUTD-4-US-690-x-y-z [690V],Y,97,N'
'Power-One ULTRA-1500-TL-OUTD-1-US-690-x-y-z [690V],Y,96.5,N'
'Power-One ULTRA-1500-TL-OUTD-3-US-690-x-y-z [690V],Y,97,N'
'Princeton Power Systems, Inc. GTIB-480-30-WZZZZZZ-G1.3 [480V],N,93.5,N'
'Princeton Power Systems, Inc. GTIB-480-30-ZZZZZZ-G1.3 [480V],N,97,N'
'Princeton Power Systems, Inc. GTIB-208-30WYYYYYY [208V],N,93,N'
'Princeton Power Systems, Inc. GTIB30-480BGNSC [480V],Y,92.5,N'
'Princeton Power Systems, Inc. GTIB-480-30-WZZZZZZ [480V],N,92.5,N'
'Princeton Power Systems, Inc. GTIB-480-30-ZZZZZZZ [480V],N,95.5,N'
'Princeton Power Systems, Inc. GTIB-480-100-xxxx [480V] [480Vdc],N,94.5,N'
'Princeton Power Systems, Inc. GTIB-480-100-xxxx [480V] [600Vdc],N,95,N'
'Princeton Power Systems, Inc. GTIB-480-100X-YYYYYYYY-Z-G1.2 [480V],Y,94.5,N'
'Princeton Power Systems, Inc. GTIB-480-125XXXXXX-G1.5 [480V],N,96,N'
'Princeton Power Systems, Inc. GTIB-480-125XXXXXX-W-G1.5 [480V],N,94.5,N'
'Princeton Power Systems, Inc. GTIB-480-125-XXXXXX-W-G1.3 [480V],N,94,N'
'Princeton Power Systems, Inc. GTIB-480-125-XXXXXX-Y-G1.3 [480V],N,96,N'
'Princeton Power Systems, Inc. BIGI-250-X48GNMNR [480V],Y,94.5,N'
'Princeton Power Systems, Inc. BIGI-250-X48GNNR [480V],N,94.5,N'
'PV Powered PVP1100,Y,91.5,N'
'PV Powered PVP1100EVR [120V],Y,90.5,N'
'PV Powered PVP2000 [120V],Y,92.5,N'
'PV Powered PVP2000EVR [240V],Y,92,N'
'PV Powered PVP2500 [240V],Y,94.5,N'
'PV Powered PVP2800-208 [208V],Y,92,N'
'PV Powered PVP3000 [240V],Y,93.5,N'
'PV Powered PVP3500 [240V],Y,95.5,N'
'PV Powered PVP4600 [240V],Y,95.5,N'
'PV Powered PVP4800 [240V],Y,96,N'
'PV Powered PVP5200 [240V],Y,96,N'
'PV Powered PVP30KW-208 [208V],Y,94,N'
'PV Powered PVP30KW-480 [480V],Y,94,N'
'PV Powered PVP30KW-LV-208 [208V],Y,93,N'
'PV Powered PVP30KW-LV-480 [480V],Y,93.5,N'
'PV Powered PVP35 kW-208 [208V],Y,95.5,N'
'PV Powered PVP35 kW-480 [480V],Y,96,N'
'PV Powered PVP35 kW-600 [600V],Y,95.5,N'
'PV Powered PVP50KW-208 [208V],Y,96,N'
'PV Powered PVP50KW-480 [480V],Y,96,N'
'PV Powered PVP50KW-600 [600V],Y,96,N'
'PV Powered PVP75KW-208 [208V],Y,95.5,N'
'PV Powered PVP75KW-480 [480V],Y,95.5,N'
'PV Powered PVP75KW-600 [600V],Y,96,N'
'PV Powered PVP100 kW-208 [208V],Y,95.5,N'
'PV Powered PVP100 kW-480 [480V],Y,96,N'
'PV Powered PVP100KW-600 [600V],Y,96,N'
'PV Powered PVP250KW-480 [480V],Y,96.5,N'
'PV Powered PVP250KW-600 [600V],Y,96.5,N'
'PV Powered PVP260KW [480V],Y,97,N'
'PV Powered PVP260KW-LV [480V],Y,96.5,N'
'REFU Elektronik REFUsol 24K-UL [480V],N,98,N'
'REFU Elektronik REFUsol 24K-UL-AFCI [480V],N,98,N'
'REFU Elektronik REFUsol 48K-UL [480V],N,98,N'
'REFU Elektronik REFUsol 48K-UL-AFCI [480V],N,98,N'
'Refusol 804R012 [480V],Y,97.5,N'
'Refusol 804R016 [480V],Y,97.5,N'
'Refusol 804R020 [480V],Y,97.5,N'
'Refusol 804R024 [480V],Y,98,N'
'Renergy RS-1500 [208V],Y,94.5,N'
'Renergy RS-1500 [240V],Y,94.5,N'
'Renergy RS-2000 [208V],Y,95.5,N'
'Renergy RS-2000 [240V],Y,95,N'
'Renergy RS-3000 [208V],Y,95.5,N'
'Renergy RS-3000 [240V],Y,95.5,N'
'Renergy RS-4000 [208V],Y,95.5,N'
'Renergy RS-4000 [240V],Y,96,N'
'Renergy RS-5000 [240V],Y,95.5,N'
'Renesola Zhejiang Replus-250A [240V],N,95,Y'
'Renesola Zhejiang Replus-250B [208V],N,95,Y'
'Renesola Zhejiang Replus-300-208A,N,95.5,Y'
'Renesola Zhejiang Replus-300-240A,N,95.5,Y'
'Renesola Zhejiang MU300SAP3 [240V],N,96,Y'
'Renesola Zhejiang Replus 3600MTLB-US [208V],Y,97,N'
'Renesola Zhejiang Replus 3600MTLB-US [240V],Y,97,N'
'Renesola Zhejiang Replus 3600MTLB-US [277V],Y,97,N'
'Renesola Zhejiang Replus 4200MTLB-US [208V],Y,97,N'
'Renesola Zhejiang Replus 4200MTLB-US [240V],Y,97,N'
'Renesola Zhejiang Replus 4200MTLB-US [277V],Y,97,N'
'Renesola Zhejiang Replus 5000MTLB-US [208V],Y,97,N'
'Renesola Zhejiang Replus 5000MTLB-US [240V],Y,97,N'
'Renesola Zhejiang Replus 5000MTLB-US [277V],Y,97,N'
'Renesola Zhejiang Replus 8000TLB-US [208V],Y,96.5,N'
'Renesola Zhejiang Replus 8000TLB-US [240V],Y,97,N'
'Renesola Zhejiang Replus 9000TLB-US [208V],Y,96.5,N'
'Renesola Zhejiang Replus 9000TLB-US [240V],Y,96.5,N'
'Renesola Zhejiang Replus 10000TLB-US [208V],Y,96.5,N'
'Renesola Zhejiang Replus 10000TLB-US [240V],Y,97,N'
'Renesola Zhejiang Replus 10000TL3B-US [277V],Y,95.5,N'
'Renesola Zhejiang Replus 12000TL3B-US [277V],Y,95.5,N'
'Renesola Zhejiang Replus 11000TLB-US [240V],Y,97,N'
'Renesola Zhejiang Replus 18000TL3B-US [277V],Y,96,N'
'Renesola Zhejiang Replus 20000TL3B-US [277V],Y,96.5,N'
'Renovo Power Systems RN3000US,Y,96.5,N'
'Renovo Power Systems RN5000US,Y,94.5,N'
#REF!
'Resonix EVSK1750WG [208V],Y,94.5,N'
#REF!
'Resonix EVSK1750WG [240V],Y,94.5,N'
'Resonix EVSK2340WG [208V],Y,95.5,N'
'Resonix EVSK2340WG [240V],Y,95,N'
'Resonix EVSK3510WG [208V],Y,95.5,N'
'Resonix EVSK3510WG [240V],Y,95.5,N'
'Resonix EVSK4700WG [208V],Y,95.5,N'
'Resonix EVSK4700WG [240V],Y,96,N'
'Rhombus Energy Solutions BESI-50kW-480 [480V],N,94,N'
'Rhombus Energy Solutions BESS-50kW-480 [480V],N,94,N'
'Ritek RTMU300SAP2 [240V],N,96,Y'
'Sainty Solar SSI-2K2U [240V],Y,94.5,N'
'Sainty Solar SSI-3K3U [240V],Y,95,N'
'Sainty Solar SSI-4K4U [240V],Y,95.5,N'
'Sainty Solar SSI-5K5U [240V],Y,95.5,N'
'Samil Power SolarPond 240HF-US [208V],N,95.5,Y'
'Samil Power SolarPond 240HF-US [240V],N,95,Y'
'Samil Power SolarRiver3000TL-US [208V],Y,96.5,N'
'Samil Power SolarRiver3000TL-US [240V],Y,97,N'
'Samil Power SolarRiver4000TL-US [208V],Y,97,N'
'Samil Power SolarRiver4000TL-US [240V],Y,97,N'
'Samil Power SolarRiver5000TL-US [208V],Y,97,N'
'Samil Power SolarRiver5000TL-US [240V],Y,97,N'
'Samil Power SolarRiver6000TL-US [208V],Y,97,N'
'Samil Power SolarRiver6000TL-US [240V],Y,97,N'
'Samil Power SolarRiver6000TL-US [277V],Y,97,N'
'Samil Power SolarRiver7000TL-US [208V],Y,97,N'
'Samil Power SolarRiver7000TL-US [240V],Y,97.5,N'
'Samil Power SolarRiver7000TL-US [277V],Y,97,N'
'Samil Power SolarRiver8000TL-US [208V],Y,97,N'
'Samil Power SolarRiver8000TL-US [240V],Y,97.5,N'
'Samil Power SolarRiver8000TL-US [277V],Y,97,N'
'Samil Power SolarRiver9000TL-US [208V],Y,97,N'
'Samil Power SolarRiver9000TL-US [240V],Y,97.5,N'
'Samil Power SolarRiver9000TL-US [277V],Y,97.5,N'
'Samil Power SolarRiver10000TL-US [208V],Y,97,N'
'Samil Power SolarRiver10000TL-US [240V],Y,97.5,N'
'Samil Power SolarRiver10000TL-US [277V],Y,97.5,N'
'SanRex PV-100K-48T-13,Y,94.5,N'
'SanRex PV-250K-48T-13,Y,95,N'
'SanRex PV-500K-48T-13,N,95.5,N'
'SANYO ELECTRIC CO LTD OF PANASONIC GROUP VBHN325SA17E [240V],N,97.5,Y'
'SANYO ELECTRIC CO LTD OF PANASONIC GROUP VBHN330SA17E [240V],N,97.5,Y'
'Satcon Technology AE-30-60-PV-A [480V],Y,93,N'
'Satcon Technology AE-30-60-PV-D [208V],Y,92.5,N'
'Satcon Technology AE-30-60-PV-E [240V],Y,93,N'
'Satcon Technology AE-30-60-PV-F [240V],Y,94.5,N'
'Satcon Technology PVS-30 [208V],Y,95,N'
'Satcon Technology PVS-30 [240V],Y,95,N'
'Satcon Technology PVS-30 [480V],Y,95,N'
'Satcon Technology AE-50-60-PV-D [208V],Y,94.5,N'
'Satcon Technology AE-50-60-PV-F [240V],Y,93,N'
'Satcon Technology PVS-50 [208V],Y,95.5,N'
'Satcon Technology PVS-50 [240V],Y,95.5,N'
'Satcon Technology PVS-50 [480V],Y,95.5,N'
'Satcon Technology PVS-50-S-MT [208V],Y,95.5,N'
'Satcon Technology PVS-50-S-MT [240V],Y,95.5,N'
'Satcon Technology PVS-50-S-MT [480V],Y,95.5,N'
'Satcon Technology AE-50-60-PV-A [480V],Y,93,N'
'Satcon Technology AE-75-60-PV-A [480V],Y,95.5,N'
'Satcon Technology AE-75-60-PV-D [208V],Y,95.5,N'
'Satcon Technology PVS-75 [208V],Y,96,N'
'Satcon Technology PVS-75 [240V],Y,96,N'
'Satcon Technology PVS-75 [480V],Y,96,N'
'Satcon Technology AE-100-60-PV-A [480V],Y,94.5,N'
'Satcon Technology AE-100-60-PV-A-HE [480V],Y,95.5,N'
'Satcon Technology AE-100-60-PV-D [208V],Y,94.5,N'
'Satcon Technology AE-100-60-PV-F [240V],Y,95,N'
'Satcon Technology PVS-100 [208V],Y,96,N'
'Satcon Technology PVS-100 [240V],Y,96,N'
'Satcon Technology PVS-100 [480V],Y,96,N'
'Satcon Technology SDMS0100208LNIU [208V],Y,95,N'
'Satcon Technology SDMS0100240LNIU [240V],Y,95,N'
'Satcon Technology SDMS0100480LNIU [480V],Y,95,N'
'Satcon Technology PVS-110-S-MT [208V],Y,95,N'
'Satcon Technology PVS-110-S-MT [240V],Y,95.5,N'
'Satcon Technology PVS-110-S-MT [480V],Y,95.5,N'
'Satcon Technology AE-135-60-PV-A [480V],Y,95.5,N'
#REF!
'Satcon Technology AE-135-60-PV-D [208V],Y,95,N'
#REF!
#REF!
'Satcon Technology PVS-135 [208V],Y,96,N'
'Satcon Technology PVS-135 [240V],Y,96,N'
'Satcon Technology PVS-135 [480V],Y,96,N'
'Satcon Technology PVS-210-S [208V],Y,95.5,N'
'Satcon Technology PVS-210-S [240V],Y,95.5,N'
'Satcon Technology PVS-210-S [480V],Y,95.5,N'
'Satcon Technology AE-225-60-PV-A [480V],Y,94.5,N'
'Satcon Technology AE-225-60-PV-D [208V],Y,95.5,N'
'Satcon Technology PVS-250,Y,95.5,N'
#REF!
'Satcon Technology PVS-250 [208V],Y,96,N'
'Satcon Technology PVS-250 [240V],Y,96,N'
'Satcon Technology PVS-250 [480V],Y,96,N'
'Satcon Technology PVS-375 [480V],Y,95.5,N'
'Satcon Technology AE-500-60-PV-A [480V],Y,95,N'
'Satcon Technology EQX0500US200X-N,Y,96,N'
'Satcon Technology EQX0500US200X-P,Y,96,N'
'Satcon Technology EQX0500US480T-N,Y,96,N'
'Satcon Technology PVS-500,Y,95.5,N'
'Satcon Technology PVS-500 [480V],Y,96,N'
'Satcon Technology SDMS0500UL320XN [320V],Y,95.5,N'
'Satcon Technology SDMS0500UL320XP [320V],Y,95.5,N'
'Satcon Technology SDMS0500UL480TN [480V],Y,96,N'
'Satcon Technology SDMS0500UL480TP [480V],Y,96,N'
'Satcon Technology EPP-1000-0600-32060-200X-U-N,Y,96.5,N'
'Satcon Technology EPP-1000-0600-32060-200X-U-P,Y,96.5,N'
'Satcon Technology PVS-1000,Y,96,N'
'Satcon Technology EPP-1250-1000-52085-320X-U-N,Y,97,N'
'Satcon Technology EPP-1250-1000-52085-320X-U-P,Y,97,N'
'Schneider Electric Solar Inverters USA, Inc. Conext TX 2800 NA [208V],Y,94.5,N'
#REF!
'Schneider Electric Solar Inverters USA, Inc. Conext TX 2800 NA [240V],Y,94.5,N'
'Schneider Electric Solar Inverters USA, Inc. Conext TX 3300 NA [208V],Y,94.5,N'
'Schneider Electric Solar Inverters USA, Inc. Conext TX 3300 NA [240V],Y,95,N'
'Schneider Electric Solar Inverters USA, Inc. Conext TX 3800 NA [208V],Y,95.5,N'
'Schneider Electric Solar Inverters USA, Inc. Conext TX 3800 NA [240V],Y,95.5,N'
'Schneider Electric Solar Inverters USA, Inc. XW4024-120/240-60 [120V],Y,91.5,N'
'Schneider Electric Solar Inverters USA, Inc. XW4024-120/240-60,Y,91,N'
'Schneider Electric Solar Inverters USA, Inc. XW4548-120/240-60,Y,93,N'
'Schneider Electric Solar Inverters USA, Inc. Conext TX 5000 NA [208V],Y,95.5,N'
'Schneider Electric Solar Inverters USA, Inc. XW+5548-NA,Y,93.5,N'
'Schneider Electric Solar Inverters USA, Inc. XW+5548-NA [120V],Y,93,N'
'Schneider Electric Solar Inverters USA, Inc. Conext TX 5000 NA [240V],Y,96,N'
'Schneider Electric Solar Inverters USA, Inc. XW6048-120-60 [120V],Y,92.5,N'
'Schneider Electric Solar Inverters USA, Inc. XW+6848-NA,Y,92.5,N'
'Schneider Electric Solar Inverters USA, Inc. XW+6848-NA [120V],Y,92.5,N'
'Schneider Electric Solar Inverters USA, Inc. XW6048-120/240,Y,92.5,N'
'Schneider Electric Solar Inverters USA, Inc. Conext CL 18000NA,Y,97,N'
'Schneider Electric Solar Inverters USA, Inc. Conext CL 25000NA,Y,98,N'
'Schneider Electric Solar Inverters USA, Inc. GT30-208 [208V],Y,96,N'
'Schneider Electric Solar Inverters USA, Inc. Conext CL-60A,Y,98,N'
'Schneider Electric Solar Inverters USA, Inc. GT100-208 [208V],Y,95,N'
'Schneider Electric Solar Inverters USA, Inc. GT100-208-PG [208V],Y,95,N'
'Schneider Electric Solar Inverters USA, Inc. GT100-480 [480V],Y,96,N'
'Schneider Electric Solar Inverters USA, Inc. GT100-480-PG [480V],Y,96,N'
#REF!
'Schneider Electric Solar Inverters USA, Inc. GT250-480 [480V],Y,96,N'
#REF!
'Schneider Electric Solar Inverters USA, Inc. GT250-480-PG [480V],Y,96,N'
#REF!
'Schneider Electric Solar Inverters USA, Inc. GT500-480 [480V],Y,96,N'
#REF!
'Schneider Electric Solar Inverters USA, Inc. GT500-480-PG [480V],Y,96,N'
#REF!
'Schneider Electric Solar Inverters USA, Inc. GT500-MVX,Y,95.5,N'
#REF!
'Schneider Electric Solar Inverters USA, Inc. GT500-MVX-PG,Y,95.5,N'
'Schneider Electric Solar Inverters USA, Inc. Conext Core XC540-NA,N,97,N'
'Schneider Electric Solar Inverters USA, Inc. Conext Core XC630-NA,N,97.5,N'
'Schneider Electric Solar Inverters USA, Inc. Conext Core XC680-NA,N,97.5,N'
'Schneider Electric Solar Inverters USA, Inc. Conext Core XC733-NA,N,97.5,N'
'Schneider Electric Solar Inverters USA, Inc. CS1666-1-NA [575V],N,98,N'
'Schneider Electric Solar Inverters USA, Inc. CS1666-2-NA [575V],N,98,N'
'Schneider Electric Solar Inverters USA, Inc. CS1666-3-NA [575V],N,98,N'
'Schneider Electric Solar Inverters USA, Inc. CS1800-NA [575V],N,98,N'
'Schneider Electric Solar Inverters USA, Inc. CS2000-NA [575V],N,97.5,N'
'Schneider Electric Solar Inverters USA, Inc. CS2200-NA [600V],N,98,N'
#REF!
'Schneider Electric Solar Inverters USA, Inc. CS2400-NA [600V],N,98,N'
#REF!
'Schuco USA SB700U [120V],Y,91.5,N'
#REF!
'Schuco USA SB700U-SBD [120V],Y,91.5,N'
'Schuco USA SWR1800U [120V],Y,91.5,N'
'Schuco USA SWR1800U-SBD [120V],Y,91.5,N'
'Schuco USA SWR2100U [240V],Y,93,N'
#REF!
'Schuco USA SWR2500U [208V],Y,92.5,N'
'Schuco USA SWR2500U-SBD [208V],Y,92.5,N'
'Schuco USA SWR2500U [240V],Y,93,N'
'Schuco USA SWR2500U-SBD [240V],Y,93,N'
#REF!
'Schuco USA SB3000US [208V],Y,95,N'
#REF!
'Schuco USA SB3000US [240V],Y,95.5,N'
#REF!
' ,,(%),'